## DISCLAIMER
DISCLAIMER
ENTSO-E assums no liability in the case of any direct, indirect or subsequent damages which occur in any way in connection with the use of the information and the data contained in the TYNDP. Use of information and data is to be understood in the broad sense and would include, for example, transmission, display, reuse, reproduction, publication or creation of any derivative work. Irrespective of the above, any use of information and data contained in the TYNDP should enunciate the source of the data an information.

## TYNDP 2012 report
5 July 2012
TYDNP 2012 package - Table of projects TYNDP report
Project identification |  |  |  |  | Project assessment
Project number | Investment number | Substation 1 | Substation 2 | Brief technical description | Grid Transfer Capability Increase [MW] | Socio-economic Welfare | RES integration | Improved Security of Supply | Losses variation | CO2 mitigation | Technical resilience | Flexibility | Social and environmental Impact | Project costs | Present status | Expected date of commissioning | Evolution compared to the TYNDP 2010 situation | Investment comment | Project comment
1 | 1. 1 | Frades B (PT) | Pedralva 1&2 (PT) | Creation of a new 400kV station in Frades B connected to Pedralva by means of two new 400kV, 40km lines. The realization of this two connections can take advantage of some already existing 150kV single lines, which will be reconstructed as double circuit lines 400+150kV line and partially sharing towers with those 400kV circuits. | 3800 | 4 | 1 | Tras -so Montes and the Alto Duore area | [5 empty] | 2 | design & permitting | 2014 | Adjustment resulting from the new date of the hydro power plant. |  | This project integrates new amounts of Hydro Power Plants in the Northern region of Portugal (3200 MW of which 2700 MW with pumping) creates better conditions to evacuate Wind Power already existent and new with authorization for connection. These new amounts of power will increase the flows in the region, and it is estimated that the flows could reach 3800 MW, which must be evacuated to the littoral strip and south Portugal through three new independent routes. Part of these flows will interfere and accumulate with the already existent flows entering in Portugal through the international interconnections with Spain on the North, the Alto Lindoso-Riba de Ave-Recarei and Lagoaça-Aldeadávila axis, which induces additional needs for reinforcement of this axis in a coordinated way.
1 | 1. 2 | Pedralva (PT) | Alfena (PT) | New 50km double circuit Pedralva (PT) - Alfena (PT) 400kV OHL, (only one circuit installed in a first step). This line is going to use partially a corridor of a existing single 150 OHL. | [10 empty] | planned | 2017 | Adjustment resulting from the new date of the hydro power plant. |  | 1
1 | 1. 3 | Pedralva (PT) | Vila Fria (PT) | New 55km double circuit Pedralva - Vila Fria 400kV OHL (one circuit installed), with needed extension of existing Vila Fria substation to include 400kV facilities. | [10 empty] | design & permitting | 2014/2015 | Delays due to authorization process. |  | 1
1 | 1. 4 | Frades B - Ribeira de Pena - Feira (PT) |  | New 160km double-circuit 400kV OHL Frades B (PT) -Ribeira de Pena (PT) - Feira (PT) (one circuit operated at 220kV between R. Pena and Feira) with a new 400/60kV substation in Rib. Pena. In a first step, only the 130km section Rib. de Pena (PT) - Feira (PT) will be constructed and operated at 220kV as Vila Pouca Aguiar (PT) - Carrapatelo (PT) - Estarreja (PT) (see project 1.6). In a second step, one circuit of this line will be operated at 400kV. | [10 empty] | design & permitting | 2015/2016 | Progresses as planned |  | 1
1 | 1. 5 | Macedo de Cavaleiros (PT) | Vila Pouca de Aguiar (PT) | New 75km double circuit 400+220kV OHL Macedo de Cavaleiros (PT) -Valpaços (PT) - Vila Pouca de Aguiar (PT). | [10 empty] | partly under construction, design & permitting | 2011/2012 | Delays due to authorization process. A section of the line Macedo de Cavaleiro-Vila Pouca de Aguiar between Macedo de Cavaleiros and Valpaços (53 km) was commissioned at the end of 2011. | This investment allows the connection of RES (mainly wind) and increases the transmission capacity in the Douro area. | 1
1 | 1. 6 | V. P. Aguiar - Carrapatelo - Estarreja (PT) |  | New 400+220kV double circuit OHL (initially only used at 220kV) Vila Pouca Aguiar - (Rib. Pena) - Carrapatelo - Estarreja . Total length of line: 2x(90+49)km. | [10 empty] | design & permitting | 2013 | Delays due to authorization process. | This investment allows the connection of the RES (mainly wind) and new load in the area. | 1
1 | 1. A1 | Ribeira de Pena - Guarda (PT) |  | New 192km double/single-circuit 400kV OHL Ribeira de Pena (PT) - Guarda (PT). In a first step, only the 75 km section Ribeira de Pena - Guarda will be constructed and operated at 220 kV between Vila Pouca de Aguiar and Macedo de Cavaleiros (see project 5), in a second step one circuit of this line will be operated at 400 kV. Between Macedo de Cavaleiros zone and Pocinho zone a single line will be constructed, between Pocinho zone and Chafariz zone a double circuit 400 kV OHL will be constructed (only one circuit installed in a first step), this last line will use one circuit of the line V. Chã B - Guarda (see project 2. A2) to establish the line Ribeira de Pena (PT) - Guarda (PT). | [10 empty] | planned | 2022 | New investment in TYNDP. This investment the supports the integration of new hydro and wind power plant in Northern Portugal |  | 1
2 | 2. 8 | V. Chã B - Arg./Góis - Penela - Paraimo / Batalha (PT) |  | New single circuit 400kV OHL Vila Chã B-Arganil/Gois-Penela (90km) plus new double circuit 400kV OHL (15km) to connect Penela substation to Paraimo - Batalha line. Two new 400/60kV substations at Vila Chã B and Arg./Góis are needed, as well as the expansion of the existing Penela substation to include 400kV facilities. | 1800 | 4 | 1 | [6 empty] | 2 | design & permitting | 2015/2016 | Progresses as planned |  | This project integrates new hydro power plants (590 MW with pumping) and evacuates the existent and new wind generation in the inner central region of Portugal (it is expected to connect more 800 MW of new wind, but the wind target in this region overcomes surmounts of more than 2000 MW). The existing network of 220 kV and 150kV is no more adequate to integrate these new amounts of power, and a new 400kV axis should be launched in this region in a two major routes: one to the littoral strip (Penela/Paraimo/Batalha) and another by the interior, establishing a connection to Falagueira substation, where there is an interconnection with Spain (Falagueira-Cedillo).
2 | 2. 9 | Guarda - Ferro B - (C. Branco) - Falagueira (PT) |  | New double circuit 400+220kV OHL Guarda (PT) -Ferro B (PT) -'Castelo Branco zone' (PT) (between Guarda and Ferro B only the 400kV circuit will be installed) plus new double circuit 400+150kV OHL 'Castelo Branco zone' (PT) -Falagueira (PT). New 400/60kV substations in Guarda and Ferro B. Total length of line: 135km. | [10 empty] | design & permitting | 2015/2016 | Adjustment resulting from the new date of the renewables project. |  | 2
2 | 2. 10 | Falagueira (PT) | Pego (PT) | New 40km double circuit 400+150kV OHL substituting for an existing 150kV line. | [10 empty] | design & permitting | 2014 | Progresses as planned |  | 2
2 | 2. A2 | V. Chã B - Guarda (PT) |  | New double circuit 400kV OHL Vila Chã B-Guarda (55km) | [10 empty] | planned | 2020 | New investment in TYNDP This investment supports the integration of new hydro and wind power plant in Northern Portugal |  | 2
3 | 3. 12 | Rio Maior - Alm. Bispo - Fanhões (PT) |  | New 71km double circuit 400kV OHL feeding Lisbon area from north with creation of a 400/220/60kV substation in Almargem do Bispo. A section of this reinforcement (between Rio Maior and Carvoeira zone) will be finished earlier included on a 400/220kV double circuit line linking Rio Maior and Carregado substations. | 1880 | 2 | 5 | Lisboa and Setúbal Peninsula | [5 empty] | 1 | planned | 2016/2019 | Progresses as planned |  | This project reinforceS the security of supply of Lisbon and Setubal region (north and south Tagus river) by creating a strong semi-ring of 400 kV, with two new 400kV substations that can guarantee the load growth in the region in a safe, secure and quality way. Currently there are only 3 400/VHV substations (Alto de Mira, Fanhões and Palmela), and two of them are quite far from the main load. This new project will create two new 400 kV substations near the main loads.
3 | 3. 13 | Palmela - F. Ferro -Ribatejo (PT) |  | Expansion of Fernão Ferro substation to include 400kV facilities and connection to the existent Palmela (PT) - Ribatejo (PT) single circuit line by a new 25km double-circuit 400kV OHL. | [10 empty] | under construction | 2012 | Progresses as planned Line Palmela-F.Ferro-Ribatejo was commisined at the end of 2011. The expansion of Fernão Ferro substation to include the 400 kV will be concluded only in 2012. |  | 3
3 | 3. 14 | Marateca - Pegões - Fanhões (PT) |  | New 400/60kV substations in Pegoes. New 90km double-circuit 400kV OHL . This new line will be connected to already existing line Palmela (PT) - Sines 2 (PT) , so making a direct link Sines-Pegões (PT) -Fanhões (PT) substations. | [10 empty] | under construction | 2012 | Progresses as planned |  | 3
4 | 4. 16 | Aldeadávila (ES) | Lagoaça (PT) - Armamar (PT) - Recarei (PT) | New Duero Interconnection 400kV New 400kV OHL interconnection line Aldeadávila (ES) - Lagoaça (PT) , including new Lagoaça substation (PT). Also associated, the lines Lagoaça-Armamar-Recarei 400kV in PT and the Armamar (PT) 400/220kV substation. On a first phase (2009) a new 400/220kV substation (Lagoaça - PT) will be created with only 220kV level installed, and there will be some rearrangements and reinforcements on the local 220kV network structure. On river crossing a new 220kV double line with separated circuits, firstly Aldeadavila (ES) - Lagoaça (PT) 1 & 2 and changing later to Aldeadavila (ES) - Pocinho (PT) 1 & 2, will substitute the existing two 220kV lines Aldeadavila (ES) – Bemposta (PT) and Aldeadavila (ES)-Pocinho (PT). Total length: 1km (ES)+105km (PT). | P>E 1700 - E>P 1400 | 3 | 2 | [6 empty] | 2 | partly commissioned, design & permitting | Aldeadavila-Lagoaça 400kV (cros border ), Aldeadavila (ES) - Pocinho (PT) 1 & 2 220 kV, Lagoaça 400/220 kV Substation, Armamar (PT)-Lagoaça (PT) 400 kV commissioned in 2010. Armamar (PT)-Recarei (PT) expected in 2012. | Aldeadavila-Lagoaça 400kV (cross-border), Aldeadavila (ES) - Pocinho (PT) 1 & 2 220 kV, Lagoaça 400/220 kV Substation, Armamar (PT)-Lagoaça (PT) 400 kV completed. Portuguese section Armamar (PT)-Recarei (PT) delayed in autorization process. |  | This project increases the capacity between PT and ES. Larger and more volatile flows are expected between both countries due to the huge increase of volatile sources and the market interchanges. The project includes two interconnection routes, besides the internal reinforcements required, one in the North and other in the South, due to the important loop flows between the two countries and, consequently, only both interconnections allow to reach a reasonable import/export capacities that will reach the "3.2 GW" .
4 | 4. 17 | Guillena (ES)-Puebla de Guzman (ES) | Tavira (PT)-Portimao (PT) | New Southern Interconnection New 400kV OHL double-circuit line between Guillena (ES)-Puebla de Guzman (ES) - Tavira (PT) - Portimão (PT), including new Tavira (PT) and P.Guzman (ES) 400kV substations. On the interconnection section P.Guzmán (ES) –Tavira (PT), initially only one circuit will be placed. Total length: 25km (ES)+110km(PT). | P>E 1700 - E>P 1400 | [9 empty] | partly under construction, design & permitting | 2013 | Portuguese section commissioned.P. Guzman -Guillena (ES) built and operating at 220kV. Difficulties in the authorization process in the Spanish section P. Guzman - border and connection to Guillena 400 Kv. |  | 4
4 | 4. 18 | Boboras (ES)-O Covelo (ES) | Vila Fría (PT)- Vila Conde (PT) - Recarei (PT) | New northern interconnection. New double circuit 400kV OHL between O Boboras (ES) -O Covelo (ES) - Vila Fria (PT) - Vila do Conde (PT) - Recarei (PT), including new 400kV substations O Covelo (ES), Boboras (ES), Vila Fria (PT) and Vila do Conde (PT). On the section O Covelo (ES) – Vila do Conde (PT), only one circuit will be placed. Total length: 50km (ES)+112km (PT). | P>E 1700 - E>P 1400 | [9 empty] | design & permitting | 2014 | Progresses as planned. Changes in route and connecting point in Spain due to environmental constraints |  | 4
4 | 4. 21 | Aldeadavila (ES) JM Oriol (ES) | Villarino (ES) Caceres (ES) | Uprating the existing Aldeadávila-Villarino 400kV OHL in order to increase its capacity from 1350MVA to 1690MVA. Uprating the existing line JM Oriol-Caceres 220 kV | [10 empty] | under construction | 2013 | Progress ans planned, although there are difficulties to find a suitable period for a planned outage to carry on the project. |  | 4
4 | 4. 21 | JM Oriol (ES) | Arenales -Caceres (ES) | New 220kV JM Oriol-Arenales, and new Arenales substation. | P>E 1700 - E>P 1400 | [9 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 4
5 | 5. 19 | Vic (ES) | Pierola (ES) | Upgrading (uprating) the existing 75km single circuit Vic-Pierola 400kV line in order to increase its capacity from 1360 MVA to 1710 MVA. | 1200-1400 in both directions | 1 | 2 | Perpignan, Gerona | [5 empty] | 2 | under construction | 2012 | Delays due to authorization process. |  | Mid-term interconnection project between France and Spain ("2.8 GW") . It includes cross border lines and internal lines required to assure NTC.
5 | 5. 20 | Arkale (ES) | Hernani (ES) | Upgrading the existing single circuit Arkale-Hernani n°2 220kV OHL in order to increase its capacity up to 640 MVA. | [10 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 5
5 | 5. 36 | Sta.Llogaia (ES) | Baixas (FR) | New HVDC (VSC) bipolar interconnection in the Eastern part of the border, via 320kV DC underground cable using existing infrastructures corridors and converters in both ending points. | [10 empty] | partly under construction, design & permitting | 2014 | Progresses as planned. |  | 5
5 | 5. 37 | Santa Llogaia (ES) | Bescanó (ES) | New double circuit Sta.Llogaia-Ramis-Bescano-Vic/ Senmenat 400kV OHL (single circuit in some sections) New 400kV substations in Bescano, Ramis and Sta.Llogaia, with 400/220kV transformers in Ramis and Bescano. | [10 empty] | under construction | 2011-2013 | Bescano-Vic/Senmenat 400 KV commissioned. Difficulties in the authorization process of the section Bescano-Sta Llogaia 400kV |  | 5
5 | 5. 46 | Baixas (FR) | Gaudière (FR) | Reconductoring of existing 70km double circuit 400kV OHL to increase its capacity. | [10 empty] | design & permitting | end 2013 | Progresses as planned |  | 5
6 | 6. 22 | Boimente (ES) | Grado (ES) | North axis Project between Galicia and the Basque Country. Part of the project is considered as the Asturias Ring. New double circuit Boimente-Pesoz-El Palo-Salas Grado 400kV OHL. Change of voltage level of the existing Soto-Tabiella single circuit from 220kV to 400kV, and connection as input/output in Grado. New single circuit Soto-Penagos 400kV OHL. New double circuit Aguayo/Penagos-Udalla-Abanto 400kV OHL New double circuit Zierbena-Abanto-Gueñes 400kV OHL. New double circuit Gueñes-Ichaso OHL. New double circuit Gozón-Reboria--Sama-Lada 400kV OHL. New double circuit Sama-Velilla 400kV OHL. Uprating the single circuit Lada-Robla 400kV OHL in order to increase its capacity by around 300 MVA. It includes new 400kV substations Pesoz, El Palo,Salas, Grado, Gozón, Sama, Reboria , Costa Verde, Penagos, Solorzano, Udalla, Abanto and several transformers to 220kV. | 2000- 4200 | 5 | 2 | [6 empty] | 2 | partly commissioned, design & permitting | 2012-2014 | Section Pesoz-Salas commissioned. El Palo connection is in progress. Difficulties in the authorization process of the section Boimente-Pesoz and Salas-Grado |  | Larger and more volatile West East power flows from Galicia to the Basque Country, triggered especially by the development of new generation sources in the North and North Western part of the country (mainly wind, a new pumping hydro power plant, and some CCGT that will replace former coal power plants) and the need to feed the high industrial and demanding regions of the North and Northeastern part of Spain.
6 | 6. 22 | Soto -Grado- Gozon-Reboria (ES) | Costaverde-Sama (ES) | [11 empty] | design & permitting | 2015 | Changes in the definition of the investment: Subestation Valle del Nalón 400kV is not required as the link can not take advantage of existing 132kV due to technical and environmental problems, connection Gozón-Carrio 400kV can not use existing corridor of lower voltage lines and requires therefore a new substation Reboria 400kV. |  | 6
6 | 6. 22 | Soto (ES) | Penagos (ES) | [11 empty] | commissioned | commissioned | Commissioned |  | 6
6 | 6. 22 | Sama (ES) | Velilla (ES) | [11 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 6
6 | 6. 22 | Lada (ES) | Robla (ES | [11 empty] | commissioned | commissioned | Commissioned |  | 6
6 | 6. 22 | Penagos/Aguayo (ES) | Abanto (ES) | [11 empty] | partly commissioned, design & permitting | 2012 | From Penagos/Aguayo to udalla commissioned. The connection from udalla to Abanto has delays in authorization process |  | 6
6 | 6. 22 | Zierbena (ES) | Abanto (ES) | [11 empty] | commissioned | commissioned | Commissioned |  | 6
6 | 6. 22 | Abanto/Gueñes (ES) | Ichaso (ES) | [11 empty] | design & permitting | 2016 | Delays due to authorization process. |  | 6
7 | 7. 23 | Ichaso (ES) | Castejón (ES) | Northern part of the new Cantabric-Mediterranean axis. New double circuit Castejón-Muruarte-Dicastillo-Ichaso 400kV OHL, with new 400kV substations in Muruarte and Dicastillo with 400/220kV transformers. Section Castejón-Muruarte 400kV already in service | 1320--4280 | 1 | 1 | [6 empty] | 2 | partly commissioned, design & permitting | 2017 | Castejón-Muruarte section have been commissioned. Muruarte-Dicastillo-Ichaso has difficulties in the authorization process which led to change the route and connection (Ichaso substitutes Vitoria) |  | Larger and more volatile Cantabric-Mediterranean power flows in Spain, triggered by the development of local RES but also influenced by transits flows caused by the generation/demand situations in the North and Levante areas.
7 | 7. 23 | La Serna (ES) | Magallón (ES) | New double circuit La Serna-Magallón 400kV OHL. | [10 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 7
7 | 7. A4 | Tudela (ES) | Magallón (ES) | New CCRS (Combination of Reactors step by step) in Magalló 220 kV | [10 empty] | design & permitting | 2013 | New investment in the TYNDP, as it is required to ensure the GTC increase for the entire project |  | 7
7 | 7. A5 | Dicastillo (ES) | Moncayo (ES) | New double circuit Dicastillo-El Sequero-Santa Engracia-Magaña-Moncayo 220kV OHL. | [10 empty] | design & permitting | 2013-2017 | New investment in the TYNDP. Ensures the GTC increase of the project while helping to evacuate the generation in Soria and Aragón. |  | 7
7 | 7. 23 | Aragón (ES) Tudela (ES) La Serna (ES) | Peñaflor (ES) Magallón (ES) Ichaso (ES) | Uprating the existing Aragón-Peñaflor 400kV OHL , Tudela-Magallón 220kV and La Serna-Ichaso 220 kV. | [10 empty] | design & permitting | 2013-2014 | New investment in the TYNDP. Difficulties in the authorization process |  | 7
7 | 7. 24 | Fuendetodos /Mudejar (ES) | Eliana/ Godelleta(ES) | Southern part of the new Cantabric-Mediterranean axis. New double circuit Fuendetodos-Muniesa-Mezquita-Platea-Godelleta 400kV OHL. New double circuit Teruel-Mudejar-Morella-la Plana/Godelleta 400kV-OHL. the new TGodelleta substation will be equipped with a 400/220kV transformer and connected to the existing 400kV lines Cofrentes-La Eliana, and Catadau-Requena 400kV lines. New 400kV substations Mezquita, Platea, Muniesa, Mudejar and Godelleta with 400/220kV transformer units | [10 empty] | design & permitting | 2012-2015 | Turis substation is substituted by Godelleta due to environmental reasons. Uprate Eliana-La Plana and new circuit is rejected due to environmental reason. As alternative a double circuit connection morella-Godelleta/La plan. These issues delay the project up to 2015 |  | 7
8 | 8. 25 | Aragón (ES) | Isona (ES) | New double circuit Aragón/Peñalba-Arnero-Isona 400kV OHL with new 400kV substations Arnero and Isona, and a 400/220kV transformer in Arnero. | 3870 | 1 | 3 | [6 empty] | 1 | design & permitting | 2014 | Delays due to authorization process.. In addition, Monzón substation is substituted by Arnero |  | Larger and more volatile South- NorthEastern power flows from Aragón to Catalunya, triggered especially by the development of new RES in the south of Catalunya and Aragón, that joined to the existing generation sources (RES and conventional) in this area and further in the south causes higher flows, that would naturally flow to the large consumption areas in Catalunya.
8 | 8. 25 | Escatron (ES) | La Secuita (ES) | New single circuit Escatrón-Els Aubals-La Secuita 400kV OHL with new 400kV substation in Els Aubals and La Secuita with 400/220kV transformer. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 8
8 | 8. A6 | Torres del Segre(ES) | Mequinenza (ES) | New SSSC (Static Synchronous Series Compensator) in Torres del Segre-Mequinenza 220kV. | [10 empty] | design & permitting | 2013 | New investment in the TYNDP. Ensures the GTC increase of the project while alleviating present and the future congestion in the parallel 220kV axis |  | 8
8 | 8. A7 | Mangraners (ES) | Begues (ES) | New Double circuit Mangraners-Espluga-Begues and Mangraners-Juneda-Secuita-Perafort-Begues 220 kV | [10 empty] | design & permitting | 2013 | New investment in the TYNDP. Ensures the GTC increase of the project while alleviating present and the future congestion in the parallel 220kV axis |  | 8
8 | 8. A8 | Espluga (ES) | Penedes (ES) | Uprate 116km single circuit 220kV OHL | [10 empty] | design & permitting | 2011-2013 | New investment in the TYNDP. Ensures the GTC increase of the project while alleviating present and the future congestion in the parallel 220kV axis |  | 8
8 | 8. A9 | Garraf (ES) | Vandellos (ES) | Uprate 108km single circuit 400kV OHL | [10 empty] | design & permitting | 2015 | New investment in the TYNDP. Ensures the GTC increase of the project while alleviating present and the future congestion in the parallel 220kV axis |  | 8
8 | 8. A10 | Isona (ES) | Calders (ES) | uprate 79km single circuit 400kV OHL | [10 empty] | design & permitting | 2015 | New investment in the TYNDP. Ensures the GTC increase of the project while alleviating present and the future congestion in the parallel 220kV axis |  | 8
9 | 9. 26 | Catadau (ES) | Benajama (ES) | New double-circuit Catadau-Jijona-Benejama 400kV OHL .A new 400kV substation will be created at Jijona and transformers installed in Jijona and Catadau. | 1840 | 2 | 5 | Costablanca area | [5 empty] | 1 | design & permitting | 2017 | Delays due to authorization process. |  | Security of supply of the Costablanca area in Levante Mediterranean coast
9 | 9. 26 | Catadau (ES) | Jijona (ES) | 220 kV lines from Catadau to Jijona in the coast of Costablanca using partially the 132KV lines | [10 empty] | design & permitting | 2016-2019 | New investment in the TYNDP complementing the previous one to alleviate congestion in the 132kV lines that supplies Casabanca area. 132 kV lines will be upgraded to 220KV. |  | 9
10 | 10. 28 | Cofrentes (ES) | Ayora (ES) | New single circuit Cofrentes-Ayora 400kV OHL. | 3380-4270 | 4 | 1 | [6 empty] | 1 | design & permitting | 2015 | Delays due to authorization process. forcing to reschedule the investment |  | Larger and more volatile East-West flows triggered mainly due to new RES generation development in Valencia, Albacete and Ciudad Real .
10 | 10. 28 | Ayora (ES) | Pinilla (ES) | New single circuit Cofrentes-Ayora-Campanario-Pinilla 400kV OHL. This project also includes a new 400kV substation in Campanario. | [10 empty] | design & permitting | 2012-2013 | Progresses globally as planned |  | 10
10 | 10. 33 | Romica (ES) | Manzanares (ES) | Transmanchega project New double circuit line Romica-Manzanares 400kV OHL. New substation Manzanares with a 400/220kV transformer unit. | [10 empty] | design & permitting | 2016 | Postponed in new national Master Plan as need is not imminent |  | 10
10 | 10. 33 | Manzanares (ES) | Brazatortas (ES) | Transmanchega project New double circuit line Manzanares-Brazatortas 400kV OHL. The new 400kV substation Brazatortas will be connected to the existing line Guadame-Valdecaballeros. | [10 empty] | design & permitting | 2013 | Progresses as planned |  | 10
11 | 11. 29 | Cartuja (ES) | Guadame (ES) | New double circuit Cartuja-Arcos de la Frontera-La Roda-Cabra-Cordoba-Guadame 400kV OHL (partly already commissioned) . It includes new 400kV substations Cartuja and Cordoba, with 400/220kV transformers. | 1270 | 4 | 1 | [6 empty] | 1 | partly commissioned, design & permitting | 2011/2014 | Arcos-Cabra-Guadame section commissioned. Cordoba connection postponed in new National Master Plan as need for demand is not imminent. Cartuja-Arcos faces difficulties in the authorization process. |  | Larger and more volatile South-North power flows, triggered especially by the development of new RES in Cadiz, that joined to the existing generation sources (RES and conventional) in the area causes higher flows, that would naturally flow to the large consumption areas in the North.
11 | 11. A11 | Cartuja-Pto Sta Maria (ES) | Facinas (ES) | New 52km single circuit 220 kV OHL Puerto Sta Maria-Pto.Real-Parralejo-Facinas | [10 empty] | design & permitting | 2012/2013 | New investment in the TYNDP, contributing also to evacuate the generation in the coast of Cadiz |  | 15
12 | 12. 30 | Don Rodrigo (ES) | Aznalcollar (ES) | New double circuit 400kV OHL: Aznalcollar-Guadaira-Don Rodrigo. Aznalcollar substation will also have a new input/output in Guillena-Palos 400kV. This project also includes new 400kV substations in Aznalcollar and Guadaira with 400/220kV transformers. | 2150-1600 | 3 | 4 | [6 empty] | 2 | design & permitting | 2017 | Delays due to authorization process. which led that Guillena-Guadaira connection is substituted by Aznalcollar-Guadaira with a new topology. |  | Larger and more volatile Southwestern-Northwestern power flows, triggered especially by the development of new generation sources in Sevilla and Huelva (mainly wind and solar), but also in Extremadura, that joined to the existing generation sources in the area causes higher flows, that would naturally flow to the large consumption areas in the South (Sevilla) or in the North (towards Madrid), depending on the demand/generation situation.
12 | 12. 30 | Guillena (ES) | Almaraz (ES) | New double circuit 400kV OHL Guillena-Brovales-Arroyo S.Servan-Carmonita- Almaraz. This project also includes new 400kV substations in Arroyo S.Servan, Carmonita with 400/220kV transformers. | [10 empty] | design & permitting | 2012 | Alcuescar substation substituted by Carmonita. Progresses as planned otherwise |  | 12
13 | 13. 31 | Caparacena (ES) | La Ribina (ES) | New double circuit Caparacena-Baza-La Ribina 400kV OHL, with two new 400kV substations in Baza and La Ribina (these substations will be also connected to Carril-Litoral 400kV line ). | 1950-3400 | 4 | 1 | [6 empty] | 1 | design & permitting | 2016 | Delays due to authorization process. |  | The project aims at ensuring the connection to the transmission network of new RES (wind, solar and pumping hydro) and ensuring the possibility of more volatile power flows between the Almeria and Granada.
13 | 13. 31 | Caparacena (ES) | Litoral (ES) | The existing single circuit Litoral-Tabernas-Hueneja-Caparacena 400kV line will be uprated in order to increase its capacity . | [10 empty] | under construction | 2012 | Final phase of permitting.. Progress as planned although there are difficulties to find a suitable period for a planned outages to carry out the work |  | 13
14 | 14. 34 | Trives (ES) | Tordesillas (ES) | New line Trives-Aparecida-Arbillera-Tordesillas 400kV OHL and Trives-Conso-Valparaiso-Tordesillas 220kV OHL. New 400kV substations in Aparecida, | 600+3000 | 1 | 2 | [6 empty] | 2 | under construction | 2011-2012 | Progress as planned. Trives-Tordesillas 400kV axis shares towers with the Trives-Tordesilla 220kV line. Final phase of permitting. |  | Larger and more volatile Northwestern- Centre power flows , triggered especially by the development of new RES in Galicia and Castilla-León, that joined to the existing generation sources (RES and conventional) in the area and further in the north causes higher flows, that would naturally flow to the large consumption areas in the center of Spain, mainly Madrid.
14 | 14. 34 | Tordesillas (ES) | La Cereal /Moraleja (ES) | New double circuit Tordesillas-Segovia- Galapagar 400kV OHL. | [10 empty] | under construction | 2012-2013 | Partly commissioned. Progresses as planned |  | 14
14 | 14. 34 | Segovia (ES)-PST Galapagar | Moraleja (ES) | New input/output of Moraleja in Segovia-Galapagar 400kV OHL and new PST in the 400kV line Galapagar-Moraleja. | [10 empty] | design & permitting | 2013-2015 | Delays due to authorization process. |  | 14
14 | 14. 34 | Loeches (ES) | SSReyes (ES) | Upgrade of the existing 21km single circuit Loeches-SS Reyes 220kV OHL to 400kV in order to increase its capacity. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 14
14 | 14. 34 | Fuencarral (ES) | Galapagar (ES) | Uprate Galapagar-Fuencarral 400kV. | [10 empty] | design & permitting | 2014 | New investment in TYNDP |  | 14
14 | 14. 34 | Mudarra (ES) | Tordesillas (ES) | New double circuit 400kV Mudarra-Tordesillas OHL and upgrade of the existing single-circuit Mudarra-Tordesillas 400kV line in order to increase its capacity. | [10 empty] | partly under construction, design & permitting | 2018 | Uprate fostered because of necessity. New line postponed in new Master Plan. |  | 14
15 | 15. A12 | Olmedilla (ES) | Valdemingomez (ES) | New double circuit Olmedilla-Villares-Morata-Valdemingomez 400kV OHL, and New substation Villares and Valdemingomez 400kV, with 400/220 kV transformers in T.Velasco | 8700 | 5 | 1 | [6 empty] | 1 | design & permitting | 2016/2017 | New investment in TYNDP |  | Larger and more volatile South- Centre power flows , triggered especially by the development of new RES in Cuenca, that would naturally flow to the large consumption area of Madrid but also influenced by transits flows caused by higher flows coming from the south of Spain.
15 | 15. 32 | (Castilla) (ES) | (Madrid) (ES) | Uprate Cofrentes-Minglanilla-Belinchon-Morata 400kV,double circuit Trillo-Villanueva Escuderos-Olmedilla-Belinchon 400kV, double circuit Valdecaballeros-Arañuelo 400 kV, double circuit Morata-Villamiel-Almaraz 400 kV, double circuit Villaviciosa- Almaraz 400 kV, double circuit Aldeadavila-Arañuelo and Aldeadavila- Hinojosa-Almaraz 400kV, Picon-Aceca-Los Pradillos-Torrejon de Velasco and Añover-Torrejón de Velasco-Pinto Ayuden-El Hornillo-Villaverde 220 kV | [10 empty] | partly under construction, design & permitting | 2011/2018 | Some of the investments progressed as planned. Other have problems either in permitting process or finding a suitable period for a planned outage to carry out the works. |  | 15
16 | 16. 38 | Gatica (ES) | Aquitaine (FR) | New HVDC interconnection in the western part of the border via DC subsea cable in the Biscay Gulf. | Fr->Es 1200 ; Es ->Fr 2000 | 1 | 2 | Biarritz, Basque country | [5 empty] | 3 | under consideration | ca. 2020 | New investment in TYNDP, defined since last release, aiming 4 GW capacity between France and Spain. |  | Long-term interconnection project between France and Spain ("4 GW") . It includes cross border lines and internal lines required to assure NTC.
16 | 16. A14 | Amorebieta (ES) Garraf (ES) Adrall (ES) Orcoyen (ES) | Gueñes (ES) Secuita (ES) La Pobla (ES) Elgea (ES) | Uprates required in basque country and Catalonia in order to use fully the benefit of the longterm ES-FR interconnection. | [10 empty] | under consideration | 2016 | New investment in TYNDP meant to solve congestion in this area. |  | 16
16 | 16. A17 | Arkale (ES) |  | New PST on Arkale-Argia 220 kV interconnection line | [10 empty] | design & permitting | 2016 | New investment enabling to take full advantage of the transfer capacity of the new subsea interconnection. |  | 16
17 | 17. 42 | Lonny (FR) | Vesle (FR) | Reconstruction of the existing 70km single circuit 400kV OHL as double circuit OHL. | 9000 | 1 | 2 | Reims, Paris area | [5 empty] | 3 | design & permitting | 2016 | Progresses as planned |  | Project needed to cope with larger and more volatile North South power flows from Normandy to Champagne, triggered especially by the development of new generation sources (along the Channel coasts, from Picardie to Champagne and further North abroad) that would naturally flow to large consumption areas: Paris area, but also more broadly from Brittany to Reims.
17 | 17. 44 | Havre (FR) | Rougemontier (FR) | Reconductoring of existing 54km double circuit 400kV OHL to increase its capacity. | [10 empty] | under construction | 2018 | As the pace of generation installation is lower than expected, the investment has been postponed. | This investment is needed for integrating new generation in Le Havre area. As the pace of generation installation is lower than assumed earlier, the investment has been postponed from 2015 to 2018 | 17
17 | 17. A18 | tbd (FR) | tbd (FR) | New network reinforcement between Haute Normandy and the south of Paris area. Length about 160 km. | [10 empty] | under consideration | long term | New investment in TYNDP, defined since last release | Either existing assets uprate or new HVDC, actual needs still being evaluated, depending on uncertainties on generation location | 17
17 | 17. 45 | Taute (FR) | Oudon (FR) | "Cotentin-Maine "Project : new 163km double circuit 400kV OHL connected to existing network via two new substations in Cotentin and Maine regions. | [10 empty] | under construction | 2013 | Delays due to authorization process. |  | 17
17 | 17. A144 | Cergy (FR) | Terrier (FR) | MORP project : new single circuit 400-kV line between existing 400-kV substations | [10 empty] | planned | 2018 | New investment in TYNDP, defined since last release, triggered by larger and more volatile power flows between generation developing North of Paris and Paris area. |  | 17
18 | 18. 48 | Gaudière (FR) | Rueyres (FR) | Reconductoring with ACCS limiting section (10km) of existing single circuit 400kV OHL. | >1000 | 3 | 5 | Provence area | [5 empty] | 3 | under construction | end 2012 | Progresses as planned |  | Larger and more volatile North South power flows in South-Western France, triggered by the development of local RES generation but also influenced by transits flows with neighboring countries.
18 | 18. A19 | tbd (FR) | tbd (FR) | Restructuration of whole EHV grid in Massif Central area | [10 empty] | under consideration | long term | New investment in TYNDP, defined since last release, triggered by larger and more volatile power flows in South West France. |  | 18
18 | 18. 20. A20 | (Provence) (FR) | (Midi) (FR) | New subsea HVDC link between Marseille area and Languedoc | [10 empty] | design & permitting | 2018 | New investment in TYNDP, defined since last release, triggered by larger and more volatile power flows in South West France. |  | 18
19 | 19. 51 | Boutre (FR) | La Bocca (FR) | PACA "Filet de sécurité" project: construction of 3 new AC 220kV underground cables (Boutre - Trans [65 km], Biançon - Fréjus [26 km] & Biançon - La Bocca [17 km]) and installation of reactive power compensation devices in 220 kV Boutre and Trans substations | 500 | 2 | 5 | French riviera | [5 empty] | 1 | design & permitting | 2015 | Progresses as planned |  | Security of supply of the French riviera
20 | 20. 53 | Coulange (FR) | Le Chaffard (FR) | Reconductoring (with ACCS / ACCR) of two existing double circuit 400kV OHL (Coulange - Pivoz-Cordier - Le Chaffard and Coulange - Beaumont-Monteux - Le Chaffard). Total length of both lines: 275km | 2400 | 1 | 5 | South East France | [5 empty] | 2 | under construction | 2016 | Progresses as planned | Construction over 4 years because the works are only possible during limited periods every years on this strategic corridor | The project aims at ensuring the reliable grid operation to cope with new generation development along the Rhone Valley and more volatile power flows between the Alps and South Western France.
20 | 20. 18. A20 | [15 empty] | 0 | The investment contributes both to project 18 and project 20. For the technical description see project 18 | 20
21 | 21. 54 | Cornier (FR) | Piossasco (IT) | Replacement of conductors (by ACCS) on Albertville (FR) - Montagny (FR) - Cornier (FR) and Albertville (FR) - La Coche (FR) - La Praz (FR) - Villarodin (FR) - Venaus (IT) - Piossasco (IT) single circuit 400kV OHLs. In addition, change of conductors and operation at 400kV of an existing single circuit OHL between Grande Ile and Albertville (FR) currently operated at lower voltage, and associated works in Albertville (FR) 400kV substation. (Total length of lines : 257 km) | 1800 from FR to IT, (600 in the MT) | 1 | 5 | [6 empty] | 3 | under construction | 2012/2013 | Mainly progresses as planned although the works on existing lines take slightly longer than initially thought |  | Planned France-Italy interconnection development
21 | 21. 55 | Grande Ile (FR) | Piossasco (IT) | "Savoie - Piémont" Project : New 190km HVDC (VSC) interconnection FR-IT via underground cable and converter stations at both ends (two poles, each of them with 600MW capacity). The cables will be laid in the security gallery of the Frejus motorway tunnel and possibly also along the existing motorways' right-of-way. | [10 empty] | design & permitting | 2017/2018 | Progresses as planned |  | 21
21 | 21. 81 | Trino (IT) | Lacchiarella (IT) | A new 380kV double circuit OHL between the existing 380kV substations of Trino and Lacchiarella in North West Italy area. Total line length: 95km, Voltage upgrade of the existing Magenta 220/132kV substation up to 380kV. | [10 empty] | under construction | 2013 | Authorization process ended, construction phase on going |  | 21
21 | 21. 84 | Casanova (IT) | Vignole (IT) | Voltage upgrade of the existing 100km Casanova-Vignole 220kV OHL to 400kV and new 400/220/150kV substation in Asti area. | [10 empty] | design & permitting | long term | Delays due to authorization process. |  | 21
21 | 21. 101 | Turin (IT) |  | Restructuring of the 220kV network in the urban area of Turin. Some new 220kV cables, some new 220/132kV substations and some reinforcements of existing assets are planned. Total length: 63km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 21
22 | 22. 57 | under consideration (FR) | under consideration (CH) | Reinforcement of the interconnection in the area of Geneva's lake. | < 1000 from FR to CH and < 1500 from CH to FR | 3 | 2 | [6 empty] | 1 | under consideration | long term | Progresses as planned. Several technical options (route, technologies) have been designed and are being investigated. | The very uncertain environment, regarding commissioning and decommissioning of generation in particular makes the assessment complex. | France-Switzerland interconnection development under consideration.
23 | 23. 60 | under consideration (FR) | under consideration (BE) | To be determined. | 1800-3000 | 3 | 2 | Lille, Ruien area | [5 empty] | 2 | under consideration | 2018-2020 | Project entered a feasibility study phase. Expected date of commissioning is now 2018. |  | France-Belgium interconnection development: internal French grid reinforcements, that are prerequisite to maintain the present NTC and further interconnection development under consideration. This project enhances security of supply in Belgium and allows intra and inter countries RES integration.
23 | 23. A21 | Avelin (FR) | Mastaing (FR) | Operation at 400 kV of existing line currently operated at 220 kV | [10 empty] | design & permitting | 2017 | New investment in the TYNDP | Upgrade of all grid assets in Northern France at the same standard | 23
23 | 23. A22 | Avelin (FR) | Gavrelle (FR) | Substitution of a new double-circuit 400kV OHL to an existing 400-kV single circuit OHL | [10 empty] | design & permitting | 2017 | New investment in the TYNDP |  | 23
24 | 24. 60a | Lillo (BE) | Mercator (BE) | Brabo Project : Doubling of the axis Zandvliet-Mercator via Lillo. First part : erecting a new 22km double circuit 380kV OHL with 1500 MVA capacity Lillo and Mercator. | 1500 | 2 | 2 | Antwerp area | [5 empty] | 2 | design & permitting | 2017 | New date of operation advanced to 2017 due to new generation projects. | Brabo Project | The project aims at ensuring the reliable grid operation to cope with new generation development in the northern part of Belgium and more volatile north south flows. It also enhances the security of supply in Antwerp harbor.
24 | 24. 445 | Zandvliet (BE) | Lillo (BE) | Brabo Project : Doubling of the axis Zandvliet-Mercator via Lillo. Second part : erecting a new 22km double circuit 380kV OHL with 1500 MVA capacity Lillo and Zandvliet and a new 400 kV substation in Lillo. | [10 empty] | design & permitting | 2017 | Permits cancelled by national authority . New permitting procedure has started | Brabo Project | 24
24 | 24. 445a | Gramme (BE) | Van Eyck (BE) | Doubling of 108km 380kV axis Gramme-Van Eyck + high performance conductors + new 380 kV substation (Van Eyck) | [10 empty] | design & permitting | 2014 | Permitting phase has started |  | 24
24 | 24. A26 | Horta (BE) | Doel/Mercator (BE) | Upgrade with high performance conductors. | [10 empty] | design & permitting | 2016-2020 | New investment in the TYNDP (The grid simulations performed by Regional Group North Sea showed higher North-South physical flows on northern Belgian boundary. This project avoid a NTC reduction due to higher loop flows.) |  | 24
24 | 24. A27 | Zandvliet (BE) |  | New PST in Zandvliet substation | [10 empty] | planned | 2016-2020 | New investment in the TYNDP (The grid simulations performed by Regional Group North Sea showed higher North-South physical flows on northern Belgian boundary. This project avoid a NTC reduction due to higher loop flows) | 4th PST on the Belgian north border. | 24
25 | 25. 62 | Under Consideration (FR) | Under Consideration (GB) | IFA2:New subsea HVDC link between the UK and France. Capacity is still to be determined. (Possibly 1000MW) | 1000 | 1 | 5 | [6 empty] | 2 | under consideration | 2020 | Further investigations during the feasibility phase have led to reassess the expected commissioning date for "IFA2" |  | France-UK interconnection development under consideration
26 | 26. 63 | Lienz (AT) | Veneto region (IT) | The project foresees the reconstruction of the existing 220kV-interconnection line as 380kV-line on an optimized route to minimize the environmental impact. Total length should be in the range of 100-150km. | 750 | 3 | 2 | [6 empty] | 3 | planned | long term | Progresses as planned |  | Reinforcement of the interconnection between Italy and Austria. Also the support the interaction between the RES in mainly Italy with the pump storage in the Austrian Alps.
26 | 26. 47. 220 | Lienz (AT) |  | Erection of a new 220/220kV- PST in the substation Lienz (AT). | [10 empty] | under construction | 2012 | Project is in errecion and expected to be commissioned 2012 according to the schedule | The investment contributes also to project 47. | 26
26 | 26. 47. 216 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 26
26 | 26. 64 | Bressanone (IT) | New substation near Innsbruck (AT) | New double circuit 400kV interconnection through the pilot tunnel of the planned Brenner Base Tunnel. Total line length: 65km. | [10 empty] | under consideration | >2022 | Progresses as planned |  | 26
26 | 26. 66 | Prati di Vizze (IT) | Steinach (AT) | Upgrade of the existing 44km Prati di Vizze (IT) – Steinach (AT) single circuit 110/132kV OHL, currently operated at medium voltage and installing a 110kV/132kV PST. | [10 empty] | design & permitting | mid term | Investment delayed with 2 years due to the permitting process |  | 26
26 | 26. 83 | Volpago (IT) | North Venezia (IT) | Realization of a new 380kV line between the existing substation of North Venezia and the future 380kV substation of Volpago, connected in and out to the 380kV "Sandrigo - Cordignano” . Total line length: 31km. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 26
26 | 26. 93 | Dolo (IT) | Camin (IT) | New 15km double circuit 400kV OHL between existing Dolo and Camin 400kV substations, to be built in parallel with the existing line. | [10 empty] | under construction | 2014 | Authorization process ended, construction phase on going |  | 26
26 | 26. 97 | Polpet (IT) |  | Voltage upgrade of the existing Polpet 150kV/medium voltage substation up to 220kV, complying with 400kV standards. The substation will be connected by two shorts links to the existing Soverzene-Lienz 220kV line. | [10 empty] | design & permitting | 2015 | Authorization process started, project phase on going |  | 26
26 | 26. 47. 218 | Obersielach (AT) | Lienz (AT) | New 190km 380kV OHL connecting the substations Lienz (AT) and Obersielach (AT) to close the Austrian 380kV-Ring in the southern grid area. Line length: 190km. | [10 empty] | under consideration | long term | Progresses as planned | The investment contributes also to project 47. | 26
26 | 26. A102 | New interconnection between Italy and Austria |  | New possible interconnection line between Italy and Austria | [10 empty] | under consideration | long term | This investment replaces investment n°65 mentioned on TYNDP 2010. The previous investment evolved so much that it is substituted by a new project. Feasibility studies ongoing including internal reinforcements. |  | 26
27 | 27. 68 | Okroglo (SI) | Udine (IT) | New 120km double circuit 400kV OHL with installation of a PST in Okroglo. The thermal rating will be 1870 MVA per circuit. | >1800 | 1 | 3 | [6 empty] | 2 | planned | long term | Progresses as planned |  | This project increases the capacity between Slovenia - Italy and Slovenia - Hungary. Project will remove congestion and strengthen connection on North-South and East-West axis.
27 | 27. 92 | West Udine (IT) | Redipuglia (IT) | New 40km double circuit 400kV OHL between the existing substations of West Udine and Redipuglia, providing in and out connection to the future 400kV substation of South Udine. | [10 empty] | design & permitting | 2015 | The investment is delayed due to longer than expected authorization procedures. |  | 27
27 | 27. A96 | New interconnection between Italy and Slovenia |  | New interconnection between Italy and Slovenia | [10 empty] | under consideration | long term | Feasibility studies ongoing including the internal reinforcements. | Need for strengthening the connection between Slovenia and Italy and increasing of power exchange capability | 27
27 | 27. 223 | Cirkovce (SI) | Heviz (HU) Zerjavenec (HR) | The existing substation of Cirkovce (SI) will be connected to one circuit of the existing Heviz (HU) -Zerjavinec (HR) double circuit 400kV OHL by erecting a new 80km double circuit 400kV OHL in Slovenia. The project will result in two new cross-border circuits: Heviz (HU) - Cirkovce (SI) and Cirkovce (SI) - Žerjavenec (HR). | [10 empty] | design & permitting | 2016 | Presently in the authorization process. This investment was delayed due to permitting process. |  | 27
27 | 27. 224 | Krsko (SI) | Bericevo (SI) | New 400kV double circuit OHL. This project will strengthen connection between East and Central part of Slovenia and connect an internal loop. Line length: 80km. | [10 empty] | under construction | 2015 | Authorization process ended, construction phase is on going. This investment was delayed due to permitting process. |  | 27
27 | 27. 225 | Divaca (SI) | Cirkovce (SI) | Upgrading 220kV lines to 400kV in corridor Divaca-Klece-Bericevo-Podlog-Cirkovce. Line length: 193km. | [10 empty] | planned | long term | Progresses as planned |  | 27
27 | 27. A105 | Lika(HR) | Brinje(HR) | New 55km single circuit 400 kV OHL replacing aging 220 kV overhead line | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. A106 | Lika(HR) | Velebit(HR) | New 60km single circuit 400 kV OHL replacing aging 220 kV overhead line | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. A107 | Lika (HR) |  | New 400/110 kV substation, 2x300 MVA | [10 empty] | planned | 2017 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. A108 | Brinje (HR) |  | New 400/220 kV substation, 1x400 MVA | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. 229 | Plomin (HR) | Melina(HR) | New 90 km double circuit OHL, with two connecting substations and transformer 400/220 kV, 400 MVA | [10 empty] | design & permitting | >2016 | Project moved to long term, due to postponed commissioning date of thermal power plant Plomin |  | 27
27 | 27. 227 | Banja Luka (BA) | Lika (HR) | New 400kV interconnection line between BA and HR | [10 empty] | under consideration | 2020 | End points of OHL and commissioning date defined after bilateral HR-BA agreement |  | 27
28 | 28. 70 | Villanova (IT) | Lastva (ME) | New 1000MW HVDC interconnection line between Italy and Montenegro via 375km 500kV DC subsea cable and converter stations at both ending points. | 1000 | 1 | 2 | [6 empty] | 3 | under construction | 2015 | Authorization process ended, construction phase on going. The substations on the ME side has been changed. |  | It contributes significantly to the increase of GTC between the West Balkans and IT such contributing to market integration; complements the ME - IT cable
28 | 28. 86 | Foggia (IT) | Villanova (IT) | New 178km double circuit 400kV OHL between existing Foggia and Villanova 400kV substations, also connected in and out to the Larino and Gissi substations. A PST will be installed on the new 400kV line. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 28
28 | 28. 89 | Fano (IT) | Teramo (IT) | New 200km single circuit 400kV OHL between the existing 400kV substations of Fano and Teramo, providing the connection in and out to the future substation to be built in Macerata area. | [10 empty] | design & permitting | long term | The investment is delayed due to longer than expected authorization procedures. |  | 28
28 | 28. 232 | Visegrad (BA) | Pljevlja (ME) | New 70km single circuit 400kV OHL between Visegrad and Pljevlja | [10 empty] | planned | 2015 | Feasibility study for 400kV interconnections RS-ME-BA proposed under Infrastructure Projects Facility for Western Balkans |  | 28
28 | 28. 233a | Lastva (ME) |  | A new substation will be connected to the existing line 400kV Podgorica 2(ME)-Trebinje(BA), with two transformers 2X300MVA 400/110kV, and convertor station for the DC cable Lastva(Tivat)-Villanova (see 70). | [10 empty] | design & permitting | 2015 | Feasibility study covering the aspects of route planning, substation location, environmental and social issues and equipment selection is due to end in second half of 2011 |  | 28
28 | 28. 233b | Lastva (ME) | Pljevlja (ME) | New 160 km double circuit 400kV OHL existing substation Pljevlja and new substation Tivat. | [10 empty] | design & permitting | 2016 | Feasibility study covering the aspects of route planning, substation location, environmental and social issues and equipment selection is due to end in second half of 2011 |  | 28
28 | 28. A109 | Bajina Basta (RS) | Visegrad (BA) | New 400kV interconnection OHL between Serbia and BiH, and reconstruction of existing two OHL 220 kV between BiH and Serbia. | [10 empty] | planned | >2016 | New investment in TYNDP | New 400 kV overhead line between Serbia and BIH. It will eliminate constraints in the region for electric energy transits and exchange. | 28
28 | 28. A110 | Bajina Basta (RS) | TPP Obrenovac (RS) | New double circuit 400 kV OHL between new substation Bajina Basta (see infra), and substation Obrenovac | [10 empty] | design & permitting | >2016 | New investment in TYNDP | Obrenovac is the "strongest" 400 kV node in Serbia, thus providing significant upgrade for evacuation and energy transfer from north to south, and further down in Montenegro, through the new line between Bajina Basta and Pljevlja (ME) | 28
28 | 28. A111 | Bajina Basta (RS) | Pljevlja (ME) | New 86 km single circuit 400kV OHL connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS). | [10 empty] | planned | >2016 | New investment in TYNDP |  | 28
28 | 28. A112 | Bajina Basta (RS) |  | New 400/110 kV substation in Bajina Basta, upgrading an existing 220/110 kV substation. | [10 empty] | planned | >2016 | New investment in TYNDP |  | 28
28 | 28. A113 | Bistrica (RS) |  | New 220/110 kV substation | [10 empty] | design & permitting | 2015 | New investment in TYNDP | After a topology change in the area, the investment will eliminate firm connection in "Vardiste" (secure and stable operation in Serbian network and systems of Bosnia and Herzegovina and Montenegro), to eliminate constraints in the region for electric energy transits and exchange. | 28
28 | 28. A114 | Konjsko(HR) | Velebit(HR) | New 100km single circuit 400 kV OHL replacing ageing 220 kV overhead line | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 28
28 | 28. 231 | Konjsko(HR) |  | Installation of a 150MVAr reactive power device | [10 empty] | design & permitting | 2014 | Investment postponed 1 year due to permitting process |  | 28
28 | 28. A115 | Plat (HR) |  | New 220/110 kV substation | [10 empty] | under construction | 2013 | New investment in TYNDP, contributing to mesh the network surrounding HVDC link IT-ME and to increase the reliability of the EHV system |  | 28
28 | 28. 228 | Trebinhe(BA) | Plat(HR) | Re-establishment of two previously existing 220kV single circuit interconnection Trebinje(BA)-Plat(HR); Total length 10km. | [10 empty] | planned | 2014 | Progresses as planned |  | 28
29 | 29. 73 | El Aouaria (TU) | Partanna (IT) | New 350km 1000 MW HVDC line between Tunisia and Italy via Sicily with 400kV DC subsea cable and converters stations at both ends. | 1500 | 3 | 5 | [6 empty] | 2 | design & permitting | long term | The investment is delayed due to longer than expected authorization procedures. | This project will be realized in 2 steps. In the previous TYNDP just the first part of the investment was mentioned (500MW). | Interconnection between Italy and North Africa. Other interconnection projects between North Africa and Italy are still under investigation and under study
29 | 29. 76 | Partanna (IT) | Ciminna (IT) | New 65km single circuit 400kV OHL in Sicily between existing Partanna and Ciminna substations. | [10 empty] | planned | long term | Progresses as planned |  | 29
29 | 29. A97 | unknown (IT) | unknown (AL) | New interconnection between Italy and Algeria -new DC submarine cable | [10 empty] | under consideration | long term | New investment in TYNDP | Need for a new interconnection between Algeria and Italy and increasing of power exchange capability with North Africa frontier. feasibility study on going | 29
30 | 30. 74 | Chiaramonte Gulfi (IT) | Sorgente (IT) | Realization of 380kV ring grid, trough the construction of 3 new 380kV line: "Chiaramonte Gulfi - Ciminna", "Sorgente - Ciminna" and "Paternò - Priolo". It will be realized a new 380/150kV substation in Caltanissetta area and the voltage upgrade of the existing Ciminna substation up to 380kV. Total line length: 365km. New 380/150 kV substation in Sorgente area will be temporally connected in and out to the existing 400 line kV "Paterno - Sorgente" and to the local 220 kV and 150 kV network. | 1000 | 4 | 1 | Palermo, Catania, Agrigento and Messina area | [5 empty] | 3 | planned | 2016/long term | Feasibility studies carried out have led to adapt the schedule. |  | Sicilian 400kV transmission ring.
30 | 30. 75 | Sorgente (IT) | Rizziconi (IT) | New 90km double circuit 400kV line, partly via subsea cable and partly via OHL. This line is part of a larger project that foresees the creation of the future 400kV ring grid of Sicily. | [10 empty] | under construction | 2014 | Delays on construction phase |  | 30
30 | 30. 77 | Partinico (IT) | Fulgatore (IT) | New 45km single circuit 400kV OHL between Partinico and Fulgatore in Western Sicily. | [10 empty] | planned | 2016 | Feasibility studies carried out have led to adapt the schedule. |  | 30
30 | 30. 87 | Feroleto (IT) | Maida (IT) | New 400kV OHL across Calabria between the existing substation of Feroleto and the future substation of Maida, while restructuring the existing grid in North Calabria. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 30
30 | 30. A98 | Mineo (IT) |  | New 380/150 kV substation in Mineo area connected in and out to the existing 400 line kV "Chiaramonte Gulfi - Paterno" and to the local HV network. | [10 empty] | planned | long term | New investment in TYNDP | needed to overcome the expected congestions on the central-east HV network of Sicily affected by the flows of consistent production from renewable plants | 30
31 | 31. 85 | Pavia area (IT) | Piacenza area (IT) | New 45km double circuit 400kV OHL between 2 substations in the Pavia area and Piacenza. | >1000 | 3 | [7 empty] | 2 | planned | long term | Initial design partially changed, with new reinforcements and rearrangements activities on the neighboring areas resulting from further studies |  | Increase interconnection capability between IT and CH.
31 | 31. 95 | Mese (IT) |  | Voltage upgrade of the existing 220/132kV Mese substation up to 400kV. | [10 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 31
31 | 31. 99 | Avise (IT) | Chatillon (IT) | Voltage upgrade of the existing 40km Avise-Villeneuve-Chatillon single circuit 220kV OHL up to 400kV. | [10 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 31
31 | 31. 100 | Milan (IT) |  | Restructuring of the 220kV network in the urban area of Milan. Some new 220kV cables (33km), a new 220kV substation (Musocco) and some reinforcements of existing assets (35km) are planned. | [10 empty] | design & permitting | mid term | The cables in the Milan area are in operation, the appropriate substations are under construction and the reinforcements are under design and permitting. |  | 31
31 | 31. 103 | Brescia (IT) |  | New 400/132kV substation in South East area of Brescia, connected in and out to the existing Flero-Nave 400kVOHL, while restructuring the 132kV network. | [10 empty] | planned | mid term | Progresses as planned |  | 31
31 | 31. 112 | Tirano (IT) | Verderio(IT) | New 140km single circuit 400kV OHL between Tirano and Verderio substations connecting also the new 400kV substation Grosio/Piateda. | [10 empty] | planned | long term | Progresses as planned |  | 31
31 | 31. 124 | Mettlen (CH) | Airolo (CH) | Upgrade of existing 225kV OHL into 400kV. Line length: 90km. | [10 empty] | under consideration | 2020 | Progresses as planned |  | 31
31 | 31. A101 | New interconnections between Italy and Switzerland |  | Up to 4 interconnection projects are under discussion, one or two probably will be implemented | [10 empty] | under consideration | long term | This investment replaces investment n° 120 mentioned on TYNDP 2010. The previous investment evolved so much that it is substituted by a new project. Feasibility studies ongoing including the internal reinforcements. |  | 31
32 | 32. 88 | Montecorvino (IT) | Benevento (IT) | New 70km double circuit 400kV OHL between the existing 400kV substations of Montecorvino and Benevento II, providing in and out connection to the future substation to be build in Avellino North area, which will be also connected to the existing "Matera-S. Sofia" 400kV line. | 1900 | 4 | 1 | Naple urban area, Sorrento Penninsul, minor Campania islands and Tirrenic South coast Italy | [5 empty] | 3 | design & permitting | mid term | The Avelino substation is under construction, the line is in delay due to authorization process. |  | Reinforcement between South and Central-South of Italy to accommodate increasing market flows.
32 | 32. 91 | Foggia (IT) | Benevento II (IT) | Upgrade of the existing 85km Foggia-Benevento II 400kV OHL and installation of a PST on this line. | [10 empty] | under construction | 2013-2014 | Authorization process ended, construction phase on going |  | 32
32 | 32. 96 | Deliceto (IT) | Bisaccia (IT) | New 30km single circuit 400kV OHL between the future substations of Deliceto and Bisaccia, in the Candela area. | [10 empty] | design & permitting | mid term | The 2 substations are in operation from 2011. The connecting line is still in design and permitting. This delay is due to authorization process. |  | 32
32 | 32. 96a | Several new 38 kV substations in Central / South of Italy for RES (IT) |  | It will be realized few new 380/150kV substations. The new substations will be connected to the wind power plants in order to avoid the congestions on the 150kV network and to dispatch the renewable energy produced. | [10 empty] | under construction | mid term | The realization of the substations is delayed. These investments are highly sensitive to the construction of the wind/solar plants that are meant to connect. |  | 32
32 | 32. 102 | Naples (IT) |  | Restructuring of the 220kV network in the urban area of Naples. Some new 220kV cables and some reinforcements of existing assets are planned. Total length: 36km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 32
32 | 32. 110a | Aliano (IT) | Montecorvino (IT) | New connection OHL 400 kV between north Basilicata and Campania region. | [10 empty] | planned | long term | Progresses as planned |  | 32
32 | 32. A99 | Restructuring of North Calabria (IT) |  | New 400kV OHL between the existing substations of Laino and Altomonte in Calabria and a new 380/150 kV substation in Aliano connected in and out to the existing 400 line kV "Matera - Laino" and to the local HV network. Related to this project will be acted a great restructuring of the local HV network, downgrading the existing 220 kV lines to 150 kV level and the demolition of great part of existing 150 kV lines inside the Pollino Park. | [10 empty] | partly under construction, design & permitting | 2012/mid term | New investment in TYNDP (initial design partially changed, evolution including new reinforcements and rearrangements activities on the neighboring areas resulting from further studies) |  | 32
33 | 33. 90 | Calenzano (IT) | Colunga (IT) | Voltage upgrade of the existing 80km Calenzano-Colunga 220kV OHL to 400kV, providing in and out connection to the existing 220/150kV substation of S. Benedetto del Querceto (which already complies with 400kV standards). | 500 | 2 | 5 | central part of Italy | [5 empty] | 2 | design & permitting | mid term | Delays due to authorization process. |  | Reinforcement between Northern and Central part of Italy to accommodate increasing market flows.
33 | 33. 94 | Mantova area (IT) | Modena area (IT) | New 35km 400kV OHL between the 2 substations in Modena and Mantova area. | [10 empty] | planned | long term | During the preliminary consultation process the substations have became uncertain. |  | 33
33 | 33. 104 | Rome (IT) |  | Restructuring of the network in the Rome area. The work consists of : a new 380/150kV substation in south-West area of Rome, connected in and out to the existing 380kV line "Rome West-Rome South", a voltage upgrade of the existing Flaminia substation up to 380kV to be connected in and out to the foreseen 380kV line "Rome West - Rome North" and a restructuring of the 150kV network. | [10 empty] | design & permitting | 2013/long term | Progresses as planned |  | 33
33 | 33. 109 | North Bologna (IT) |  | New 400/132kV substation in North Bologna area connected in and out to the existing Sermide–Martignone 400kV line. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 33
33 | 33. 111 | Lucca (IT) |  | New 380/132kV substation in Lucca area connected in and out to the existing 380kV line “La Spezia-Acciaiolo”. | [10 empty] | planned | long term | Progresses as planned |  | 33
33 | 33. 113 | Monte S. Savino (IT) |  | New 400/220/132kV substation in Monte S. Savino area connected to the existing S. Barbara 400kV substation by upgrading an existing 220kV line. | [10 empty] | design & permitting | 2015/long term | Delays due to authorization process. |  | 33
34 | 34. A100 | Codrongianos (IT) | Suvereto (IT) | Repowering of existing HVDC interconnection between Sardinia, Corse and mainland Italy via 220kV DC subsea cable (358km). The first connection is in operation since 1970. Total capacity of the bipolar link: 500MW. | 500 | 4 | 1 | [6 empty] | 2 | planned | long term | New investment in TYNDP. |  | Reinforcement between Sardinia Corso and mainland Italy.
35 | 35. 137 | Vitkov (CZ) | Mechlenreuth (DE) | New 400kV single circuit tie-line between new (CZ) substation and existing (DE) substation. Length: 70km. | 500 | 5 | 4 | [6 empty] | 3 | under consideration | long term | Progresses as planned |  | This project is required to enable power flows between West and East, enhance the transfer capability between CZ and DE and supports the future generation evacuation.
35 | 35. 138 | tbd (CZ) | tbd (DE) - South-Eastern part of 5 Hertz Transmission control area (Röhrsdorf) | Possible increase of interconnection capacity between CEPS and 50Hertz Transmission is under consideration: either a new 400kV tie-line (OHL on new route) or a reinforcement of the existing 400kV tie-line Hradec (CEPS) – Röhrsdorf (50Hertz Transmission). | [10 empty] | under consideration | long term | Progresses as planned |  | 35
35 | 35. 306 | Vitkov (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA. | [10 empty] | planned | 2017/2018 | It is closely dependent on construction of line investment n°308 |  | 35
35 | 35. 307 | Vernerov (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA. | [10 empty] | planned | 2013/2016 | Commissioning date has been divided into two phases (1. phase - temporary connection of wind plant 180MW, 2. phase finalization of substation construction including connection to the distribution grid (consumption) |  | 35
35 | 35. 308 | Vernerov (CZ) | Vitkov (CZ) | New 400kV double circuit OHL, 1385 MVA. | [10 empty] | planned | long term | Permitting procedure complications are foreseen (line crosses protected area) |  | 35
35 | 35. 309 | Vitkov (CZ) | Prestice (CZ) | New 400kV double circuit OHL, 1385 MVA. | [10 empty] | under consideration | long term | Permitting procedure complications are foreseen (line crosses protected area) |  | 35
35 | 35. 311 | Kocin (CZ) |  | Upgrade of the existing substation 400/110kV; upgrade transformers 2x350MVA. | [10 empty] | design & permitting | long term | Schedule harmonization with market participants |  | 35
35 | 35. 312 | Mirovka (CZ) |  | Upgrade of the existing substation 400/110kV with two transformers 2x250MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 313 | Kocin (CZ) | Mirovka (CZ) | Connection of 2 existing 400kV substations with double circuit OHL having 120.5km length: and a capacity of 2X1385 MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 314 | Mirovka (CZ) | V413 (CZ) | New double circuit OHL with a capacity of 2x1385 MVA and 26.5km length. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 315 | Kocin (CZ) | Prestice (CZ) | Adding second circuit to existing single circuit line OHL upgrade in length of 115.8km. Target capacity 2x1385 MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 316 | Mirovka (CZ) | Cebin (CZ) | Adding second circuit to existing single circuit line (88.5km, 2x1385 MVA). | [10 empty] | under consideration | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 317 | Hradec (CZ) | Reporyje (CZ) | Upgrade of existing 400kV single circuit OHL with length of 116.9km. Target capacity 1385 MVA. | [10 empty] | commissioned | commissioned | Commissioned |  | 35
36 | 36. 141 | Ishøj/Bjæverskov (DK) | Bentwisch/Güstrow (DE) | The Kriegers Flak Combined Grid Solution is the new offshore multiterminal connection between Denmark and Germany used for both grid connection of offshore wind farms Kriegers Flak and interconnection. Technical features still have to be determined. | 600 | 5 | 3 | [6 empty] | 1 | planned | long term | Permission for Danish Wind Farm KF 3 is in pending. Connection to Sweden is withdrawn at present, but can come on a later stage. |  | The Kriegers Flak Combined Grid Solution is the new offshore multiterminal connection between Denmark and Germany used for both grid connection of offshore wind farms Kriegers Flak and interconnection.
37 | 37. 142 | Tonstad (NO) | Wilster (DE) | Nord.Link/NorGer: a new HVDC connection between Southern Norway and Northern Germany. Estimated subsea cable length: 520 - 600km. Capacity: 1000 MW. | up to 1400 | 1 | 4 | [6 empty] | 3 | design & permitting | 2018/2021 | Revised capacity and progress postponed, due to more demanding system operations and time needed to obtain necessary government permits for reinforcing the national grid. |  | The purpose is: Market integration with the continent and facilitating RES integration in southern and western Norway. Will also improve security of supply in southern Norway.
| 37. 408 | Kristiansand, Feda (NO) |  | Reactive compensation due to HVDC links NorNed and Skagerak 4. Reactive power devices in 400kV substations. | [10 empty] | design & permitting | 2012/2014 | Feda is in the planning and permitting stage. Kristiansand is under construction(commissioned expected as planned 2012)
37 | 37. 406 | (Southern part of Norway) (NO) |  | Voltage uprating of existing 300 kV line Sauda/Saurdal - Lyse - Tonstad - Feda - 1&2, Feda - Kristiansand; Sauda-Samnanger in long term. Voltage upgrading of existing single circuit 400kV OHL Tonstad-Solhom-Arendal. Reactive power devices in 400kV substations. | [10 empty] | design & permitting | 2016 (2013-2018) | Revised progress. Due to more demanding system operations and time needed to obtain necessary government permits for reinforcing the national grid. The investment now embed former TYNDP 2010's investments 407 and 409 and the technical description has been updated accordingly. |  | 37
38 | 38. 425 | Feda (NO) | tbd (NL) | NorNed 2: a second HVDC connection between Norway and The Netherlands via 570km 450kV DC subsea cable with 700 - 1400MW capacity. | 700 | 5 | 2 | [6 empty] | 2 | under consideration | Long term | NorNed 2 is now not likely be realised during this planning period but is included in the TYNDP calculations and therefore on the project list. NorNed 2 is not included in the current Norwegian national grid development plan. |  | Additional interconnection between NO and NL under consideration
39 | 39. 428 | Kassø (DK) | Tjele (DK) | Rebuilding of a 400kV OHL of 173km from a single-circuit to a double-circuit . This increases the transfer capacity with approx. 1000 MW. | 1000-1550 | 1 | 2 | [6 empty] | 2 | design & permitting | 2012/2014 | Progresses as planned |  | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity.
39 | 39. 144 | Audorf (DE) | Kassö (DK) | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity. It consists of partially an upgrade of existing 400kV line and partially a new 400kV route in Denmark. In Germany new 400kV line mainly in the trace of a existing 220kV line. The total length of this OHL is 114km. | [10 empty] | under consideration | 2017 | Progresses as planned |  | 39
40 | 40. 446 | Bascharage (LU) | Aubange (BE) | As a first step(2016) a PST could be placed in the existing 225kV line between LU and BE. In a second stage, two solutions are currently investigated (4 TSOs - Elia, Amprion, CREOS, RTE are involved). Solutions 1 would be a new interconnection between Creos grid in LU and ELIA grid in BE via a 16km double circuit 225kV underground cable with a capacity of 1000 MVA. Solution 2 would be the interconnection between CREOS grid in LU and ELIA grid in BE via a new 380 kV double circuit. The current study will investigate the impact of this new interconnection on other boundaries (impact of loop flow) and on internal grids . The potential reinforcements of the other boundaries and the internal grids will also be taken into account in the evaluation. | 380-900 | 2 | 5 | Luxemburg area | [5 empty] | 2 | under consideration | 2016/2020 | The commissioning date and status changed as the study to determine the best investment is still ongoing. |  | Increase the transfer capability between LU,DE, BE and FR.
40 | 40. A29 | Bascharage (LU) | tbd (BE, DE, &/o FR) | New interconnection with neighbor(s) either 220kV or 400kV | [10 empty] | under consideration | 2020 | New investment in TYNDP | An ongoing network study (4 TSOs involved) investigates the robustness of the planned 220kV connection between LU and BE and the potentially need for an upgrading to a 400kV interconnector in the South. | 40
40 | 40. 447 | Heisdorf (LU) | Berchem (LU) | New 20km double-circuit mixed (underground cable+OHL) 225kV project with 1000 MVA capacity including substations for in feed in lower voltage levels. | [10 empty] | design & permitting | 2012/2017 | Progresses as planned |  | 40
40 | 40. A30 | Bascharage (LU) | Niederstedem (DE) or tbd (DE) | Upgrading and new construction of an interconnector to DE, in conjunction with the interconnector in the south of LU; Partial upgrading of existing 220kV lines and partial new construction of lines; With power transformer station in LU | [10 empty] | under consideration | 2020 | New investment in TYNDP |  | 40
41 | 41. 149 | Dollern (DE) | Stade (DE) | New 400kV double circuit OHL Dollern - Stade including new 400kV switchgear in Stade. Length:14km. | >3000 | 4 | 5 | [6 empty] | 1 | design & permitting | mid term | This investment depends on the commissioning of a conventional power plant in the area. The additional reason for delay is the long permitting procedure associated with this investment. |  | Evacuation of the new conventional generation in the 50Hz and TenneT area.
41 | 41. 150 | Conneforde (DE) | Maade (DE) | New 400kV double circuit ( underground cable+OHL) Conneforde - Maade including new 400kV switchgear Maade. Length: 37km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 41
41 | 41. A74 | North of Control Area 5 HzT (DE) |  | Construction of new substations/lines for integration of newly build power plants in northern part of 50HzT control area. | [10 empty] | planned | long term | New investment in TYNDP, because of additional need for generation evacuation. Some of the investments are to be commissioned by the mid term and the some by long term. | Support of conventional generation integration in North-Eastern Germany, maintaining of security of supply and support of market development. | 41
42 | 42. 152 | Dörpen/West (DE) |  | New substation for connection of offshore wind farms. | >8000 | 4 | 1 | [6 empty] | 3 | under construction | mid term | Progresses as planned | Commercially sensitive information about this new wind-farm connection cannot be displayed in the TYNDP report | Integration of the offshore wind parks and the onshore grid reinforcements in the Northern DE.
42 | 42. 159 | Cluster BorWin1 (DE) | Diele (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 205km. Line capacity: 400MW. | [10 empty] | under construction | mid term | The commission date of this wind farms connection should be in 2012. Energy transportation is however already enable | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 160 | Offshore- Wind park Nordergründe (DE) | Inhausen (DE) | New AC-cable connection with a total length of 35km. | [10 empty] | design & permitting | mid term | Progresses depend on development of the off shore wind farm |  | 42
42 | 42. 161 | Offshore- Wind park GEOFreE (DE) | Göhl (DE) | New AC-cable connection with a total length of 32km. | [10 empty] | design & permitting | mid term | Progresses depend on development of the off shore wind farm |  | 42
42 | 42. 163 | Cluster HelWin1 (DE) | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 145km. Line capacity: aprox. 690MW. This Project includes also a new substation Büttel and connection of this new substation with the existing OHL Brünsbüttel - Wilster. | [10 empty] | under construction | mid term | Progresses with delay. | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 164 | Cluster SylWin1 (DE) | Büttel (DE) | New line consisting of underground +subsea cable with a total length of 210km. Line capacity: aprox.864MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 165 | Cluster DolWin1 (DE) | Dörpen/West (DE) | New line consisting of underground +subsea cable with a total length of 155km. Line capacity: 800MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 166 | Offshore Wind park Riffgat (DE) | Emden /Borßum(DE) | New AC-cable connection with a total length of 80km. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 167 | Cluster BorWin2 (DE) | Diele (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 205km. Line capacity: 800MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A82 | Cluster DolWin2 (DE) | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 160 km. Line capacity: 900 MW | [10 empty] | under construction | mid term | New investment in TYNDP, for connection of new off-shore wind-farms | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A83 | Cluster DolWin3 (DE) | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 160 km. Line capacity: 900 MW | [10 empty] | design & permitting | mid term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A84 | Cluster BorWin3 | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 180 km. Line capacity: 900 MW | [10 empty] | design & permitting | mid term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A85 | Cluster HelWin2 | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 145km. Line capacity: 690 MW | [10 empty] | under construction | mid term | New investment in TYNDP, for connection of new off-shore wind-farms | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A86 | Cluster BorWin4 (DE) | Emden/Ost (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 185 km. Line capacity: 900 MW | [10 empty] | under consideration | long term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A87 | Cluster SylWin2 (DE) | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 210km. Line capacity: 800 MW | [10 empty] | under consideration | long term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. 211 | Further connections of more offshore wind farms (DE) |  | Further connections in the clusters BorWin, DolWin, SylWin and HelWin. | [10 empty] | under consideration | long term | Progresses depend on development of the off shore wind farm |  | 42
43 | 43. A81 | Osterath (DE) | Philippsburg (DE) | New HVDC-lines from Osterath to Philippsburg to integrate new wind generation especially from North/ Baltic Sea towards Central-South Germany for consumption and storage. | 10000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany |  | Combined DC and AC new infrastructure to accommodate the new RES generation, the associated flows from North to South and also secure the SOS in South Germany.
| 43. A152 | Emden (DE) | Osterath (DE) | New HVDC-lines from Endem to Osterath to integrate new wind generation especially from North/ Baltic Sea towards Central Germany for consumption and storage. | [10 empty] | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany
| 43. A153 | Wehrendorf (DE) | Urberach (DE) | New lines in HVDC technology from the region of Lower Saxony to North Baden-Württemberg to integrate new wind generation especially from North Sea towards Central-South Europe for consumption and storage. The investment is part of the transmission corridor Cloppenburg - North Baden-Württemberg. | [10 empty] | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany
| 43. A154 | Cloppenburg (DE) | Westerkappeln (DE) | New 400-kV double circuit OHL Cloppenburg-Westerkappel (75 km). The investment is part of the transmission corridor Cloppenburg - North Baden-Württemberg. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
43 | 43. A88 | Brunsbüttel (DE), Wilster (DE), Kaltenkirchen (DE) | Großgartach (DE), Goldshöfe (DE), Grafenrheinfeld (DE) | New DC-lines to integrate new wind generation from Northern Germany towards Southern Germany and Southern Europe for consumption and storage. | [10 empty] | under consideration | long term | New Investment. |  | 43
43 | 43. A75 | Lauchstadt (DE) | Meitingen (DE) | New DC- lines to integrate new wind generation from Baltic Sea towards Central/south Europe for consumption and storage. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits |  | 43
43 | 43. A89 | Area of Northern Lower Saxony (DE) |  | New lines for integration of on- and offshore Wind generation incl. 380-kV-lines Halbemond - Emden, Emden-Conneforde and Conneforde - Cloppenburg. Total length: 160 km | [10 empty] | under consideration | long term | New Investment. |  | 43
43 | 43. A90 | Area of Schleswig-Holstein (DE) |  | About 300 km new 380-kV-lines and around 24 new transformers for integration of onshore Wind in Schleswig-Holstein, incl. lines Brunsbüttel-Barlt-Heide-Husum-Niebüll-border of Denmark, Audorf-Kiel-Göhl-Siems-Lübeck-Kaltenkirchen and Kaltenkirchen-Itzehoe-Brunsbüttel | [10 empty] | under consideration | long term | New investment in TYNDP due to new wind generation projects. | The German West-coast line (Brunsbuettel – Niebuel) is planned to be connected to the Danish grid in the 400 kV substation Endrup. The distance from the German/Danish border is approx. 80 km. Bilateral technical/economical investigations are ongoing. Reinforcements in the Danish 400 kV grid are foreseen in order to facilitate the increased power exchange capacity on the Danish-German border. | 43
44 | 44. 147 | Dollern (DE) | Hamburg/Nord (DE) | New 400kV double circuit OHL Dollern - Hamburg/Nord including one new 400/230kV transformer in substation Hamburg/Nord and new 400kV switchgear Kummerfeld. Length:43km. | 5000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 | design & permitting | mid term | Delays due to authorization process. |  | This project helps accommodating the increasing flows coming mainly form RES in NW DE to SW DE and CH.
44 | 44. 148 | Audorf (DE) | Hamburg/Nord (DE) | New 400kV double circuit OHL Audorf - Hamburg/Nord including two new 400/230kV transformers in substation Audorf. Length: 65km. | [10 empty] | design & permitting | mid term | This investment was schedulted for 2015. Presently it is foreseen a delay of around 1 year due to permitting process. |  | 44
44 | 44. 151 | Wehrendorf (DE) | Ganderkesee (DE) | New line (length: ca. 95km), extension of existing and erection of substations, erection of 380/110kV-transformers. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 156 | Niederrhein (DE) | Dörpen/West (DE) | New 400kV double circuit OHL Dörpen - Niederrhein including extension of existing substations. Length: 167km. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 157 | Wahle (DE) | Mecklar (DE) | New 400kV double circuit OHL Wahle - Mecklar including two new substations. Length: 210km. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 90. 170 | Großgartach (DE) | Hüffenhardt (DE) | New 380kV OHL. Length: 23km. Included with the project : 1 new 380kV substation, 2 transformers. | [10 empty] | under construction | 2012 | Progresses as planned |  | 44
44 | 44. 171 | Hüffenhardt (DE) | Neurott (DE) | Upgrade of the line from 220kV to 380kV. Length: 11km. Included with the project : 1 new 380kV substation. | [10 empty] | planned | 2020 | Progresses as planned |  | 44
44 | 44. 90. 172 | Mühlhausen (DE) | Großgartach (DE) | Upgrading line from 220kV to 380kV. Length:-45km. | [10 empty] | design & permitting | 2014 | Progresses as planned |  | 44
44 | 44. 90. 173 | Hoheneck (DE) | Endersbach (DE) | Upgrading line from 220kV to 380kV. Length:20km. | [10 empty] | design & permitting | 2014 | Progresses as planned |  | 44
44 | 44. 174 | Bruchsal Kändelweg (DE) | Ubstadt (DE) | A new 380kV OHL. Length:6km. | [10 empty] | design & permitting | 2014 | Postponed from one year due to permitting procedures |  | 44
44 | 44.90. 176 | Daxlanden | Eichstetten | Upgrade of transmission capacity of existing 380 kV line (120 km) | [10 empty] | under consideration | 2020 | Progresses as planned |  | 44
44 | 44. 178 | Baden-Württemberg, Süden & Nordosten (DE) |  | Installation of 2x250 MVAr 380kV capacitance banks. | [10 empty] | under construction | 2014 | One more bank in addition. Two have already been installed. Projects realised earlier because the need for reactive power compensation became urgent. |  | 44
44 | 44. 179 | Rommerskirchen (DE) | Weißenthurm (DE) | New line, extension of existing and erection of substations, erection of 380/110kV-transformers. Total line length: 100km. | [10 empty] | under construction/design & permitting | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. 181 | Dauersberg (DE) | Limburg (DE) | New 380kV double circuit OHL, extension of existing of substations, Total line length: 20km. | [10 empty] | under construction/design & permitting | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. 182 | Kriftel (DE) | Obererlenbach (DE) | New 400 kV double circuit OHL Kriftel - Obererlebenbach in existing OHL corridor. Length: 11 km | [10 empty] | planned | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. A80 | Area of West Germany (DE) |  | Installation of several 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | under consideration | long term | New investment in TYNDP, because of additional needs for RES integration (combined with SoS) |  | 44
44 | 44. 183 | Wehrendorf (DE) |  | Installation of 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 184 | Bürstadt (DE) |  | Installation of 2 x 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 185 | Area of Muensterland and Westfalia (DE) |  | New lines and installation of additional circuits, extension of existing and erection of several 380/110kV-substations. Total length: ca. 110km. | [10 empty] | design & permitting | long term | Delays due to authorization process. |  | 44
44 | 44. 186 | Gütersloh (DE) | Bechterdissen (DE) | New lines and installation of additional circuits, extension of existing and erection of 380/110kV-substation. Total line length:27km. | [10 empty] | under construction | mid term | Delays due to authorization process. |  | 44
44 | 44. 187 | Area of West-Rhineland (DE) |  | New lines and installation of additional circuits, extension of existing and erection of several 380/110kV-substations. | [10 empty] | under construction | 2013 | Progresses as planned |  | 44
44 | 44. 188 | Kruckel (DE) | Dauersberg (DE) | New lines, extension of existing and erection of several 380/110kV-substations. Total line length: 130km. | [10 empty] | planned | long term | Progresses as planned |  | 44
44 | 44. A78 | Pkt. Metternich (DE) | Niederstedem (DE) | Construction of new 380kV double-circuit OHLs, decommissioning of existing old 220kV double-circuit OHLs, extension of existing and erection of several 380/110kV-substations. Length: 108km. | [10 empty] | planned | long term | New investment in TYNDP | RES integration/ Market integration especially east-west-direction | 44
44 | 44. A77 | Area of South-Wuerttemberg (DE) |  | Construction of new 380kV double-circuit OHLs, decommissioning of existing double-circuit OHLs, extension of existing 380-kV-substations. Length: ca. 60km. | [10 empty] | planned | long term | New investment in TYNDP | RES integration combined with pump storage in the alp region (market) / increasing of the NTC DE-CH/AT | 44
44 | 44. 190 | Saar-Pfalz-Region (DE) |  | New lines, extension of existing and erection of several 380/110kV-substations. Upgrade of an existing line from 220 to 380 kV | [10 empty] | planned | long term | Delays due to authorization process. | SoS (Neub. Frltg Fraulaut-Saarwellingen) combined with RES integration | 44
| 44. A155 | Conneforde (DE) | Unterweser (DE) | Upgrade of 230-kV-circuit Unterweser-Conneforde to 400kV , Line length: 32 km. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A156 | Dollern (DE) | Elsfleht/West (DE) | New 400 kV line in existing OHL corridor Dollern - Elsfleht/West Length:100 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A157 | Dollern (DE) | Landesbergen (DE) | New 400 kV line in existing OHL corridor Dollern-Sottrum-Wechold-Landesbergen (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A158 | Hamm/Uentrop (DE) | Kruckel (DE) | Extension of existing line to a 400 kV single circuit OHL Hamm/Uentrop - Kruckel. Length: 60 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A159 | Pkt. Blatzheim (DE) | Oberzier (DE) | New 400 kV double circuit OHL Pkt. Blatzheim - Oberzier including extension of existing substations. Length 16 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A160 | Urberach (DE) | Daxlanden (DE) | New line and extension of existing line to 400 kV double circuit OHL Urberach - Pfungstadt - Weinheim - Daxlanden including extension of existing substations. Length: 219 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A161 | Bürstadt (DE) | Daxlanden (DE) | New line and extension of existing line to 400 kV double circuit OHL Bürstadt - Lambshein - Daxlanden including extension of existing substastions. Length: 134 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A162 | Großgartach (DE) | Endersbach (DE) | Extension of existing 400-kV-line Großgartach - Endersbach. (Lenght: 32 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
44 | 44. 175 | Birkenfeld (DE) | Ötisheim (DE) | A new 380kV OHL. Length:11km. | [10 empty] | planned | 2020 | New investment in TYNDP |  | 44
44 | 44. 189 | Niederrhein (DE) | Utfort (DE) | New 400 kV double-circuit OHL Niederrhein-Utfort (24 km). | [10 empty] | under consideration | long term | New investment in TYNDP |  | 44
45 | 45. 90. 177 |  |  |  | 5000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 |  |  | 0 | The investment contributes both to project 45 and project 90. For the technical description see project 90. | This project helps accommodating the increasing flows coming mainly form RES in NE DE to South DE and to the Alps.
45 | 45. 191 | Neuenhagen (DE) | Vierraden (DE) | Project of new 380kV double-circuit OHL Neuenhagen-Vierraden-Bertikow with 125km length as prerequisite for the planned upgrading of the existing 220kV double-circuit interconnection Krajnik (PL) – Vierraden (DE Hertz Transmission). | [10 empty] | design & permitting | 2013/2015 | Project in permitting phase, strong local resistance |  | 45
45 | 45. 193 | Halle/Saale (DE) | Schweinfurt (DE) | New 380kV double-circuit OHL between the substations Vieselbach-Altenfeld-Redwitz with 215km length combined with upgrade between Redwitz and Grafenrheinfeld (see project 153). The Section Lauchstedt-Vieselbach has already been commissioned. Support of RES integration in Germany, annual redispatching cost reduction, maintaining of security of supply and support of the market development. The line crosses the former border between Eastern and Western Germany and is right downstream in the main load flow direction. The project will help to avoid loop flows through neighboring grids. | [10 empty] | design & permitting | mid term | Investment partly completed, strong local public resistance- delay due to permitting process |  | 45
45 | 45. 197 | Neuenhagen (DE) | Wustermark (DE) | Construction of new 380kV double-circuit OHL between the substations Wustermark-Neuenhagen with 75km length. Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | under construction | mid term | Investment partly under construction and partly in permitting phase. Expected date of commissioning was adjusted due to long permitting process and strong local public resistance. |  | 45
45 | 45. 199 | Western Pomerania (DE) | Uckermark North (DE) | Construction of new 380kV double-circuit OHLs in North-Eastern part of 50HzT control area and decommissioning of existing old 220kV double-circuit OHLs, incl. 380-kV-line Bertikow-Pasewalk (30 km). Length: 135km.Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015 | Progresses as planned |  | 45
45 | 45. 200 | Lubmin (DE) | Erfurt area (DE) | 380-kV-grid enhancement and structural change area Lubmin-Stralsund and area Magdeburg/Wolmirstedt, incl. 380-kV-line Güstrow-Wolmirsted (195 km) | [10 empty] | planned | long term | Progresses as planned |  | 45
45 | 45. 202 | Area upper Lausitz(DE) | Area Gera(DE) | Upgrading existing double-circuit 380kV OHL in the South-Eastern part of the control area of 50Hertz Transmission. Bärwalde-Schmölln length approx.. 50km. Support of RES and conventional generation integration in North-Eastern Germany, maintaining of security of supply and support of market development. | [10 empty] | design & permitting | 2017 | Progresses as planned |  | 45
45 | 45. 204 | Calbe (DE) |  | Construction of new 380kV double-circuit OHL in substation Calbe for double connection/loop into an existing line. | [10 empty] | planned | mid term / long term | The evolution of this investment depends on the development of the power plant in the area. The date mentioned in the TYNDP 2010 was a typing mistake. |  | 45
45 | 45. 205 | Fördertsedt (DE) | Area Magdeburg(DE) | Construction of new 380kV double-circuit OHL from the substation Förderstedt with 20 km length for double connection/loop in for Förderstedt; Reinforcement of existing switchgear, Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015/2020 | Progresses as planned |  | 45
45 | 45. 206 | Area Leipzig(DE) | Area Chemnitz(DE) | Construction of new double-circuit 380-kV-overhead line in existing corridor Röhrsdorf-Remptendorf (103 km) | [10 empty] | under consideration | 2020 | Progresses as planned |  | 45
45 | 45. 207 | Substations in South-Western part of 5 Hertz Transmission control area (DE) |  | Construction of new 380kV substation in Southern Magdeburg area and restructuring of existing 220kV equipment. total length: aprox .50 km | [10 empty] | planned | long term | Some of the investments are to be commissioned by the mid term and the some by long term. |  | 45
45 | 45. 208 | Lines and Substations in South-Western part of 5 Hertz Transmission control area (DE) |  | Construction of new 380kV double-circuit OHL in existing corridor Pulgar-Vieselbach (103 km) Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015/2020 | Progresses as planned |  | 45
45 | 45. 209 | Substations in 5 Hertz Transmission control area |  | Extension of existing and erection of new 380 kV-substations and several 380/110kV-substations, incl. reactive power compensation devices. | [10 empty] | design & permitting | mid term | This investment includes several substations in the control area of 50Hertz Transmission control area. Present status varies form design & permitting, planning to under consideration and the date of commissioning varies from short/mid to long term. |  | 45
| 45. A163 | Wolmirstedt (DE) | Wahle (DE) | New double circuit OHL 380 kV; Line length 111 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A164 | Vieselbach (DE) | Mecklar (DE) | New double circuit OHL 400 kV line in existing OHL corridor . (129 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A165 | Mecklar (DE) | Grafenrheinfeld (DE) | New double circuit OHL 400-kV-line (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A166 | Altenfeld (DE) | Grafenrheinfeld (DE) | New double circuit OHL 400-kV-line (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A169 | Grafenrheinfeld (DE) | Grossgartach (DE) | Additional 380 Kv circuit on a existing lines. Length: 160 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A167 | Redwitz (DE) | Schwandorf (DE) | New double circuit OHL 400 kV line in existing OHL corridor Redwitz-Mechlenreuth-Etzenricht-Schwandorf (185 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A168 | Raitersaich (DE) | Isar (DE) | New 400 kV line in existing OHL corridor Raitersaich - Ludersheim - Sittling - Isar (160 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
45 | 45. 153 | Redwitz (DE) | Grafenrheinfeld (DE) | Upgrade of 230kV connection Redwitz - Grafenrheinfeld to 400kV, including new 400kV switchgear Eltmann. Line length: 97km. | [10 empty] | design & permitting | mid term | Investment delay due to delay in the implementation of the line Halle-Schweinfurt(investment 45. 193) |  | 45
45 | 45. 154 | Redwitz (DE) |  | New 500 MVAr SVC in substation Redwitz. | [10 empty] | planned | mid term | Progresses as planned |  | 45
45 | 45. 155 | Raitersaich (DE) |  | New 500 MVAr SVC in substation Raitersaich. | [10 empty] | planned | mid term | Progresses as planned |  | 45
45 | 45. 47. 158 | [15 empty] | 0 | The investment contributes both to project 45 and project 47. For the technical description see project 47. | 45
46 | 46. 194 | wind farm cluster Baltic Sea East (DE) | Lüdershagen/ Lubmin (DE) | Offshore wind farm connection project (by AC-cables on transmission voltage level or by clustering with DC connections) has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. | >2000 | 4 | 1 | [6 empty] | 1 | design & permitting | 2012-2020 | This investment includes several connections of offshore wind farms in the eastern part of the Baltic Sea. The present expected date of commissioning varies from 2012 to 2020. |  | The integration of offshore wind generation in the Baltic Sea.
46 | 46. 195 | wind farm cluster Baltic Sea West (DE) | Bentwisch (DE) | Offshore wind farm connection project (by AC-cables on transmission voltage level or by clustering with DC connections) has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. | [10 empty] | design & permitting | 2013-2020 | This investment includes several connections of offshore wind farms in the western part of the Baltic Sea. The present expected date of commissioning varies from 2013 to 2020. |  | 46
47 | 47. A76 | Vöhringen / Leupolz (DE) | Westtirol (AT) | Upgrade of an existing OHL to 380 kV, extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. Transmissions routs Vöhringen - Westtirol and Pkt. Woringen - Memmingen. Length: 114 km. This project will increase the current power exchange capacity between the DE, AT and CH. | >2000 | 1 | 2 | [6 empty] | 3 | planned | long term | New investment in TYNDP |  | The reinforcement of the interconnection between Austria and Germany. Also the support the interaction between the RES in Northern Europe(mainly DE) with the pump storage in the Austrian Alps. The project scheduling is not related only to the network needs, but even to the feasibility and to the authorization process (the possibility to anticipate specific projects could be evaluated in the future considering the three above mentioned elements).
47 | 47. 158 | Irsching (DE) | Ottenhofen (DE) | Upgrade of 230kV connection Irsching - Ottenhofen to 400kV, including new 400kV switchgear Zolling. Length 76km. | [10 empty] | planned | mid term | Progresses as planned | The investment contributes also to project 45. | 47
47 | 47. 212 | Isar / Ottenhofen (DE) | St. Peter (AT) | New 400kV double circuit OHL Isar - St. Peter including new 400kV switchgears Altheim, Simbach and St. Peter, and one new 400/230kV transformer in substation Altheim and fourth circuit on line Isar - Ottenhofen. Line length: 90km. | [10 empty] | design & permitting | 2017 | Progresses as planned |  | 47
47 | 47. 26. 216 | St. Peter (AT) | Tauern (AT) | Completion of the 380kV-line St. Peter - Tauern. This contains an upgrade of the existing 380kV-line St. Peter - Salzburg from 220kV-operation to 380kV-operation and the erection of a new internal double circuit 380kV-line connecting the substations Salzburg and Tauern (replacement of existing 220kV-lines on optimized routes). Moreover the erection of the new substations Wagenham and Pongau and the integration of the substations Salzburg and Kaprun is planned. Line length: 130km. | [10 empty] | design & permitting | 2017/2019 | Preparation for the permitting procedure is ongoing. APG is making efforts to set the 380-kV-Salzburg-line 2017 into service. Depending on possible delays during the permitting procedure the commissioning is expected between 2017 and 2019 | The investment contributes also to project 26. | 47
47 | 47. 26. 218 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 47
47 | 47. 219 | Westtirol (AT) | Zell-Ziller (AT) | Upgrade of the existing 220kV-line Westtirol - Zell-Ziller and erection of additional 220/380kV-Transformers. Line length: 105km. | [10 empty] | partly under construction | 2013-2020 | Project consists of several measures and is on schedule |  | 47
47 | 47. 26. 220 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 47
47 | 47. 221 | St. Peter (AT) | Ernsthofen (AT) | Upgrade from 220kV-operation to 380kV and erection of a 380kV-Substation in Ernsthofen and St. Peter. | [10 empty] | under construction | 2013 | The project is on schedule. Permissions are obtained. Commissioning is expected for 2013 |  | 47
48 | 48. 214 | Gabcikovo (SK) | Gőnyü area (HU) | New interconnection (new 2x400 kV tie-line) between SK and HU starting from Gabčíkovo substation (SK) to the Gőnyü substation on Hungarian side ( preliminary decision). Project also includes the erection of new switching station Gabčíkovo next to the existing one. | 1100 SK -> HU; HU -> SK 400 | 3 | 2 | (North-West Hungary) | [5 empty] | 1 | under consideration | 2016 | The commissioning date has been moved to earlier term due to earlier erection of new 400 kV line Veľký Ďur - Gabčíkovo that help to evacuate power from new NPP. | Negotiations still in progress. This project is closely connected with the project of erection of new line between Rimavska Sobota substation (SK) and Sajoivanka substation (HU); see below. | This cluster will increase the transfer capacity between Slovak and Hungarian network systems and increase security of supply. The internal interconnections in Slovakia are necessary for the same objective. Also this cluster is important for support of North - South flow from RES in North of EU.
48 | 48. 298 | Veľký Ďur (SK) | Gabčíkovo (SK) | Erection of new 2x400kV line between two important substations and extension of the substation Veľký Ďur (SK) Line length:93km. | [10 empty] | planned | 2016 | The commissioning date has been moved to earlier term due to ensure security of power evacuation from new NPP in V.ĎUR area. |  | 48
48 | 48. A125 | Veľký Ďur (SK) | Levice (SK) | The erection of new 1x400 kV line between two important Veľký Ďur and Levice substations, including extension of the V.Ďur and Levice substation. The driver for this project is expected connection of to new generation units in Veľký Ďur area. | [10 empty] | under consideration | 2018 | New investment in TYNDP, which will significantly increase of the security and reliability of the power evacuation from new NPP. |  | 48
48 | 48. A126 | Rimavská Sobota (SK) | Sajóivánka (HU) | Connection of the two existing substations (R.Sobota (SK) - Sajoóivánka (HU)) by the new 2x400 kV line (preliminary armed only with one circuit). | [10 empty] | under consideration | 2016 | New investment in TYNDP | Negotiations/bilateral studies in progress. This project is closely connected with the project 2x400kV line Gabčíkovo (SK) - Hungary (see above). | 48
48 | 48. A127 | Sajóivánka (HU) |  | Second 400/120 kV transformer and 2x70 Mvar shunt reactors in station Sajóivánka | [10 empty] | under consideration | 2016 | New investment in TYNDP |  | 48
48 | 48. A128 | Győr (HU) |  | Third 400/120 kV transformer and 70 Mvar shunt reactor in station Győr | [10 empty] | under consideration | 2016 | New investment in TYNDP |  | 48
49 | 49. 235 | Tirana(AL) | Pristina (RS) | New 238km 400kV OHL; on 78km the circuit will be installed on the same towers as the Tirana-Podgorica OHL currently in construction (see project 233); the rest will be built as single circuit line. | 600 | 2 | 5 | [6 empty] | 1 | design & permitting | 2013 | Line in Albania is already constructed. The rest of the lines develops according to the schedule. |  | It increases significantly the North to South GTC thus accommodating bulk transports to GR, FYROM and AL
49 | 49. 236 | Leskovac(RS) | Stip (MK) | New 220km 400kV single circuit overhead interconnection between Serbia and FYR of Macedonia. A new 400/110 substation will be built in Serbia between connection nodes. | [10 empty] | under construction | Serbian part commissioned, Macedonian part : 2013 | Serbian part is completed. Regarding the Macedonian part, the design is finished; the land acquisition is ongoing and the construction tender is in preparation. |  | 49
49 | 49. 237 | TPP Kosovo (RS) | Skopje (MK) | A new 400kV OHL relevant to planning investment of 2000MW of TPP in the area of Kosovo and Metohija. Line length: 85km. | [10 empty] | under consideration | 2020 | Progresses as planned |  | 49
49 | 49. 252 | Melliti (GR) | Kardia (GR) | New 400kV double circuit OHL. Length:40km. | [10 empty] | design & permitting | long term | Due to new thermal generation in South Greece the investment is no more needed urgently and postponed to the longer term. (This investment mainly was initially designed to solve voltage problems in South Greece.) |  | 49
49 | 49. 253 | Kardia (GR) | Trikala (GR) | New 400kV double circuit OHL. Length:80km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 49
49 | 49. 254 | Larissa(GR) | Trikala (GR) | New 400kV double circuit OHL. Length:57km. | [10 empty] | under consideration | long term | Progresses as planned |  | 49
50 | 50. 238 | Pancevo (RS) | Resita (RO) | New 131 km double circuit 400kV OHL between existing substations in Romania and Serbia (63 km on Romanian side and 68 km on Serbian side). | 1000 | 1 | 3 | Area BeLgrade and south Banat region | [5 empty] | 1 | design & permitting | 2015 (2019?) | Due to financing gap, the commissioning deadline was postponed to 2019. RO intends to apply for funding through the Operational Programme 'Increase of Economic Competitiveness' - Priority Axis 4. This would ensure realization of the project and allow for faster finalization (2015 instead of estimated 2019). Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | This project increases the transfer capability between Serbia, Romania and accommodates new RES generation on the West/East part of Romanian, respectively Serbia. It also increases the transfer capability on the interface between RO+BG/RS+BA+ME.
50 | 50. 269 | Portile de Fier (RO) | Resita (RO) | New 400kV OHL between existing substation 400 kV Portile de Fier and new 400 kV substation Resita. Line length: 116km. New 400 kV substation Resita, with 400/220 kV and 400/110 kV transformers, as development of the existing 220/110 kV substation. | [10 empty] | design & permitting | 2016 | Constructive characteristics were updated as a result of progress of feasibility and design studies. Commissioning date has been slightly shifted. |  | 50
50 | 50. A116 | Beograd 2 (RS) |  | New 400/110 kV substation on the Belgrade territory | [10 empty] | under construction | 2012 | New investment in TYNDP | By taking large amount of load from other Belgrade substations, the investment will both in/ improve the local SoS significantly, and ii/ relieve the constraints on the EHV local network and enable greater inter-area transits. | 50
50 | 50. A117 | Kraljevo 3 (RS) |  | Upgrade of the existing 220/110kV substation Kraljevo 3 by constructing the 400 kV level. | [10 empty] | design & permitting | 2015 | New investment in TYNDP |  | 50
50 | 50. A118 | Kraljevo 3 (RS) | Bajina Basta (RS) | New 140km double circuit 400kV OHL between substation Kraljevo 3 and substation Bajina Basta. Kraljevo 3 (400kV) will be connected to Kragujevac 2 (400 kV) substation, which is connected to a Sofia (Bulgaria) through a 400 kV line. | [10 empty] | planned | >2015 | New investment in TYNDP | New axis for transits from East to the West, typically from Bulgaria to Bosnia and Montenegro, and further to the west. | 50
50 | 50. 270 | Resita( RO) | Timisoara-Sacalaz-Arad (RO) | Upgrade of an existing 220kV double circuit line to 400kV double circuit line and replacement of 220 kV substations Timisoara and Sacalaz with 400 kV substations. Line length: 156km. | [10 empty] | design & permitting | 2022 | Due to financing gap, the commissioning deadline was postponed to 2022. Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 50
51 | 51. 239 | Bitola (MK) | Elbasan (AL) | New 200km cross-border single circuit 400kV OHL between existing substations. New 400/110 kV substation in Ohrid area connected in/out to the new 400 kV line Bitola-Elbasan. | 1255 MW BG - AL ,>1000 BG-TR | 3 | 2 | [6 empty] | 1 | planned | 2015 | Change of date of commissioning due to : resolving the problems in the 110KV in S-W Macedonia; facilitate the market integration; increased interest of potential investors. | Selection of consultant for preparation of feasibility study | East-West corridor from Bulgaria to Italy. Investments 257, 258 and 262 can build up an independent sub-project, as they will both in/ develop altogether, specifically, grid transfer capability with Turkey; ii/ contributes with all other investments clustered in the project to developing GTC East-West from Bulgaria to BiH and Montenegro.
51 | 51. 244 | Filippi(GR) | Lagadas (GR) | New 400kV substation in Lagadas in Thessaloniki area and connection to the existing substation of Filippi via a new 110km double circuit 400kV OHL. | [10 empty] | under construction | 2013 | Initial delays due to authorization process.The project is now under construction |  | 51
51 | 51. 256 | Maritsa East 1 (BG) | N.Santa (GR) | New interconnection line BG-GR by a 130km single circuit 400kV OHL. | [10 empty] | design & permitting | long term | After the interconnection with Turkey, the project can be delayed to LT as it is mainly connected to further RES development. The final commissioning date is subject to change depending of the evolution in the area. |  | 51
51 | 51. 257 | Maritsa East 1 (BG) | Plovdiv (BG) | New 100km single circuit 400kV OHL in parallel to the existing one. | [10 empty] | design & permitting | 2014 | Investments 257,258 and 262 are postponed because the permitting procedures (environmental requirements) with the land owners induced delays . |  | 51
51 | 51. 258 | Maritsa East 1 (BG) | Maritsa East 3 (BG) | New 13km single circuit 400kV OHL in parallel to the existing one. | [10 empty] | design & permitting | 2014 |  |  | 51
51 | 51. 262 | Maritsa East 1 (BG) | Burgas (BG) | New 400kV OHL. Line length: 150km. | [10 empty] | design & permitting | 2014 |  |  | 51
52 | 52. 240 | Patras (GR) | 4 kV Continental System (GR) | New 400kV substation in Patras (GIS Technology) and in&out connection to the existing Axeloos - Distomo 400kV OHL via a new 15km double circuit line, part of which will consist of subsea cable. The project shall constitute the first 400kV corridor to Peloponnese. | 600-700 | 4 | 1 | Peloponnese area | [5 empty] | 1 | design & permitting | 2013 | The project is likely to be delayed mainly due to the environmental concerns; strong opposition by the local communities resulted in the delay in permitting procedures and subsequent delay in the expected date of commissioning |  | It increases significantly the GTC to/from the peninsula of Peloponnese, thus allowing the accommodation of large amount of RES in the peninsula and also contributes to market integration
52 | 52. 241 | Patras (GR) | Megalopolis (GR) | New 400kV substation in Megalopolis and connection to Patras 400kV substation via a 110km double circuit OHL. 2nd corridor to Peloponnese. | [10 empty] | design & permitting | 2013 |  |  | 52
52 | 52. 242 | Megalopolis (GR) | Korinthos (GR) | Construction of a new 400kV substation in Korinthos (GIS Technology) and connection to the Megalopolis substation via a 110km double circuit 400kV OHL. | [10 empty] | design & permitting | 2014 |  |  | 52
52 | 52. 243 | Korinthos (GR) | Koymoyndoyros (GR) | Replacement of the existing 150kV double circuit line by a 87km double circuit 400kV OHL. | [10 empty] | design & permitting | 2014 |  |  | 52
53 | 53. 276 | Suceava(RO) | Gadalin(RO) | New 400kV OHL between existing stations. Line length: 260km. | 2000-2500 | 4 | 1 | [6 empty] | 2 | planned | 2021 | Constructive design characteristics and time schedule were updated as a result of progress of feasibility and design studies. |  | The project will help evacuate important amount of new generation (wind +nuclear generation) in Eastern part of Romania
53 | 53. A131 | Stejaru(RO) | Gheorghieni(RO) | Reconductoring (with HTLS) of existing simple circuit 220kV line. | [10 empty] | under consideration | 2015 | New investment in the TYNDP, required to integrate new RES generation and maintain the GTC for the entire project. |  | 53
53 | 53. 273 | Cernavoda (RO) | Stalpu | New 400kV double circuit OHL between existing stations. Line length:145km. | [10 empty] | planned | 2017 | Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 53
53 | 53. 274 | Constanta (RO) | Medgidia(RO) | New 400kV double circuit (one circuit wired) OHL between existing stations. Line length:75km. | [10 empty] | planned | 2020 | As for other investments, the commissioning date was postponed due to financing gap. Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 53
53 | 53. 275 | Smardan(RO) | Gutinas(RO) | New 400kV double circuit OHL between existing stations. Line length:140km. | [10 empty] | planned | 2020 | As for other investments, the commissioning date was postponed due to financing gap. Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 53
53 | 53. 271 | connection IN-OUT in Medgidia(RO) of actual 4 kV OHL Isaccea(RO)-Varna (BG) |  | The 400kV Isaccea (RO) - Varna (BG) is passing near 400 kV substation Medgidia S. The line shall be connected in Medgidia S, through a double circuit OHL. New wind farms shall be connected to the 400 kV OHL Isaccea - Medgidia S section . Substation Medgidia S, 400 kV, shall be refurbished with GIS technology in order to provide necessary space for new connections. | [10 empty] | design & permitting | 2015 | As for other investments, the commissioning date was postponed due to financing gap. Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 53
53 | 53. A132 | Stalpu (RO) | Teleajen (RO) - Brazi (RO) | Upgrade of an existing 220kV single circuit line to 400kV. New 400 kV substations: Stalpu (400/110kV, 1x250 MVA), Teleajen (400/110kV, 1x400 MVA) | [10 empty] | planned | 2018 | New investment in TYNDP | This investment was merged with investment 273 in TYNDP 2010. They are now presented as separate investments in TYNDP 2012, according to internal project organization. The network development is still the same. | 53
53 | 53. A133 | Fantanele (RO) | Ungheni (RO) | Reconductoring (with HTLS) of existing simple circuit 220kV line. | [10 empty] | under consideration | long term | New investment in the TYNDP, required to accommodate new RES generation not foreseen in the TYNDP 2010, by increasing the GTC for the entire project. |  | 53
53 | 53. 272 | connection IN-OUT in Medgidia(RO) of actual 4 kV OHL Isaccea(RO)-Dobrudja(BG) |  | Connection IN-OUT in Medgidia (RO) of existing 400kV OHL Isaccea (RO)-Dobrudja (BG), passing nearby. The line shall be connected in Medgidia S, through a double circuit OHL. Substation Medgidia S, 400 kV, shall be refurbished with GIS technology in order to provide necessary space for new connections. | [10 empty] | design & permitting | 2015 | As for other investments, the commissioning date was postponed due to financing gap. Constructive characteristics were updated as a result of progress of feasibility and design studies. | New wind farms shall be connected to the 400 kV OHL Isaccea - Medgidia S section. | 53
53 | 53. A134 | Gheorghieni(RO) | Fantanele (RO) | Reconductoring (with HTLS) of existing simple circuit 220kV line. | [10 empty] | under consideration | 2015 | New investment in the TYNDP, required to accommodate new RES generation not foreseen in the TYNDP 2010, by increasing the GTC for the entire project. |  | 53
54 | 54. 293 | Voľa (SK) | point of splitting (SK) | Splitting of the existing single 400kV line between Lemešany and Veľké Kapušany substations to connect the new 400kV substation Voľa with transformation 400/110kV (replacing existing 220kV substation). New 400kV double circuit OHL. Length: 23km | 500 | 2 | 2 | [6 empty] | 1 | design & permitting | 2013 | Progresses as planned |  | This cluster will increase the transfer capacity between Slovak and Hungarian network systems and increase security of supply. The internal interconnections in Slovakia are necessary for the same objective. Also this cluster is important for support of North - South flow from RES in North of EU.
54 | 54. 294 | Lemešany (SK) | Veľké Kapušany (SK) | Erection of new 400 kV line between Lemešany and Veľké Kapušany substations. The project includes the extension both substations Lemešany and V.Kapušany. Line length:100 (including the loop erected under the Investment 54.293). | [10 empty] | planned | 2018 | Progresses as planned |  | 54
54 | 54. A127 | Veľké Kapušany (SK) | tbd (HU) | Erection of new 2x400 line between SK and Hungary (substation on Hungarian side still to be defined) | [10 empty] | under consideration | 2021 | New investment in TYNDP |  | 54
55 | 55. 302 | Vyskov (CZ) | Cechy stred (CZ) | New second circuit 400kV OHL; 1385 MVA. | 3000 | 5 | 5 | Prague area | [5 empty] | 1 | design & permitting | 2015 | Progresses as planned |  | This project is required both to ease power flows West to East and to enhance security of supply of Prague.
55 | 55. 303 | Babylon (CZ) | Bezdecin (CZ) | New second circuit 400kV OHL; 1385 MVA. | [10 empty] | planned | 2016 | Progresses as planned |  | 55
55 | 55. 304 | Babylon (CZ) | Vyskov (CZ) | New second circuit 400kV OHL; 1385 MVA. | [10 empty] | planned | 2018 | Progresses as planned |  | 55
55 | 55. A91 | Praha Sever (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA . | [10 empty] | planned | long term | New investment in TYNDP |  | 55
55 | 55. 310 | Vyskov (CZ) | Reporyje (CZ) | New connection between 2 existing substations line single circuit OHL 1385 MVA. | [10 empty] | under consideration | long term | Schedule harmonization with other priority investments: this investment has been delayed because of priority given to other investments |  | 55
56 | 56. A92 | Chodov (CZ) | Cechy stred (CZ) | Adding second circuit to existing single circuit line OHL upgrade in length of 35.1km. Target capacity 2x1385 MVA. | 1000 | 5 | 5 | [6 empty] | 1 | planned | 2021 | New investment in TYNDP |  | This project is required both to ease power flows West to East and for future generation evacuation.
56 | 56. A93 | Tynec (CZ) | Krasikov (CZ) | Adding second circuit to existing single circuit line OHL upgrade in length of 103.8km. Target capacity 2x1385 MVA. | [10 empty] | planned | 2025 | New investment in TYNDP |  | 56
57 | 57. 320 | Dargoleza (PL) |  | A new AC 400/110kV (450 MVA) substation between existing substations Słupsk and Żarnowiec in Northern Poland. New substation Dargoleza is connected by splitting and extending of existing 400kV line Słupsk - Dargoleza. | 3000 | 4 | 1 | [6 empty] | 2 | planned | 2020 | The new substation Dargoleza is required for the connection new wind generation in Northern Poland. The time horizon for comissioning of this investment has been changed due to change in wind farms connection schedule in the region. |  | Wind – the infrastructure in this project assures reliable connection of 3000 MW of wind generation in northern Poland. It also allows the evacuation of power in the southern direction.
57 | 57. 328 | Piła Krzewina (PL) | Bydgoszcz Zachód (PL) | New 84km 400kV double circuit 2x1870 MVA OHL interconnection line Piła Krzewina - Bydgoszcz Zachód temporarily on 220kV. | [10 empty] | design & permitting | 2016 | The time schedule of the project was shifted to meet the schedule of the RES (wind) generation connection. This one year delay in the plans appeared after updating of the NDP. The change in the NDP introduced a double circuit. |  | 57
57 | 57. 329 | Żydowo (PL) | Słupsk (PL) | A new AC 400/110kV substation next to existing 220/110kV substation in Northern Poland with transformation 400/110kV 450 MVA. New substation Żydowo is connected by new 70km 400kV 2x1870 MVA OHL double circuit lines Żydowo - Słupsk and Żydowo - Gdańsk Przyjaźń. Dismantling of existing 220/110kV transformers + Upgrade of substation SŁupsk | [10 empty] | planned | 2020 | The date of commissioning evolved due to regulatory, social and environmental issues. The investment also foresee upgrade works in substation Słupsk. |  | 57
57 | 57. 330 | Żydowo (PL) | Gdańsk Przyjaźń (PL) | A new AC substation in Gdańsk Agglomeration Area. New substation Gdańsk Przyjaźń is connected by splitting and extending of one circuit of existing line Żarnowiec - Gdańsk Błonia and new 150km 400kV 2x1870 MVA double circuit OHL line Żydowo - Gdańsk Przyjaźń with one circuit from Żydowo to Gdańsk temporarily on 220kV after dismantling of 220kV line Żydowo - Gdańsk. | [10 empty] | planned | 2020 | The date of commissioning evolved due to regulatory, social and environmental issues. |  | 57
57 | 57. 352 | Dunowo (PL) | Plewiska (PL) | Construction of a new double circuit 400kV OHL Dunowo - Żydowo (2x1870 MVA) partly using existing 220kV line + Construction of a new 400kV OHL Plewiska - Piła Krzewina - Żydowo (2x1870 MVA); single circuit temporarily working as a 220kV + A new AC 400kV switchgear in existing substation Pila Krzewina + upgrade of substation Dunowo | [10 empty] | design & permitting | 2020 | Progressed as planned. The investment also foresee upgrade works in substation Dunowo. |  | 57
58 | 58. 353 | Krajnik (PL) | Baczyna (PL) | Construction of a new double circuit 400kV OHL Krajnik - Baczyna (2x1870 MVA, 91km); single circuit temporarily working at 220kV on Krajnik - Gorzów part + New substation 400kV Baczyna will be connected by splitting and extending existing line Krajnik-Plewiska + Upgrading of limitations line Krajnik - Plewiska. | >1000 | 1 | 2 | [6 empty] | 2 | planned | 2020 | Progresses as planned |  | Bridge – third interconnection between Poland and Germany.
58 | 58. 355 | Mikułowa (PL) | Świebodzice (PL) | Double circuit line 220kV Mikułowa-Świebodzice will be upgraded to 400kV - single circuit temporarily working at 220kV. | [10 empty] | planned | 2020 | Progresses as planned |  | 58
58 | 58. A67 | Gubin (PL) |  | New 400 kV substation planned near the PL-DE border. The substation will be connected to planned line Eisenhüttenstadt (DE) - Plewiska (PL) creating new lines Eisenhüttenstadt (DE) - Gubin (PL) and Gubin (PL) - Plewiska (PL). | [10 empty] | planned | 2020 | New investment in TYNDP | This new substation on the third DE-PL connection is necessary for future generation connection while ensuring interconnection capability. | 58
58 | 58. 140 | Eisenhüttenstadt (DE) | Plewiska (PL) | New 400kV double circuit OHL Eisenhüttenstadt (DE) - Plewiska (PL) including the construction of new substation Plewiska Bis (PL) | [10 empty] | planned | 2020 | Progresses as planned |  | 58
59 | 59. 368 | Ełk (PL) | PL-LT border (LT) | Construction of a new 400kV OHL Ełk to PL-LT border. (2x1870 MVA, 108km). | 1000 | 1 | 5 | South LT and NE/central PL | [5 empty] | 3 | design & permitting | 2015 | Progresses as planned |  | “LitPol Link” project. Interconnection of Lithuanian power system with Polish power system via Back to Back station. This project allows integration of Baltics to the internal European power market,
59 | 59. 369 | Siedlce Ujrzanów (PL) | Miłosna (PL) | Construction of a new 400kV OHL Siedlce Ujrzanów - Miłosna (1870 MVA, 84km) + A new AC 400kV switchgear in existing substation Siedlce Ujrzanow with transformation 400/110kV 400 MVA. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 59
59 | 59. 370 | Ełk (PL) | Łomża (PL) | Construction of a new 400kV double circuit OHL Ełk - Łomża (2x1870 MVA, 95km) + A new AC 400kV switchgear in existing substation Elk + A new 400 kV AC substation Łomża | [10 empty] | design & permitting | 2015 | Łomża has been elected as end substation for the project and the technical description is adapted accordingly. Progresses as planned otherwise. |  | 59
59 | 59. 371 | Ostrołęka (PL) | Narew (PL) | Construction of a new 400kV OHL Ostrołęka-Łomża-Narew (1870 MVA, 120km) + A new AC 400kV switchgear in existing substation Ostroleka (in two stages) with transformation 400/220kV 500 MVA and with transformation 400/110kV 400 MVA + extension of 400 switchgear in substation Narew. | [10 empty] | design & permitting | 2015 | Progressed as planned. The investment also foresee extension works in substation Narew. |  | 59
59 | 59. 372 | Oltarzew (PL) |  | A new AC substation with two transformers 400/220kV 2x500 MVA and one 400/110kV 330 MVA will be connected by splitting 400kV line Rogowiec-Miłosna and Miłosna-Płock and 220kV line Mory-Sochaczew and Mory-Janów. | [10 empty] | under construction | 2015 | Progresses as planned |  | 59
59 | 59. 373 | Ostrołęka (PL) | Stanisławów (PL) | Single circuit line 220kV Ostrołęka-Miłosna will be partly upgraded to double circuit line 400kV (2x1870 MVA, 106km) with development of Ostrołęka 400kV substation + New substation 400kV Stanisławów will be connected by splitting and extending existing line Miłosna-Narew and Miłosna-Siedlce. | [10 empty] | design & permitting | 2020 | Progresses as planned |  | 59
59 | 59. 374 | Kozienice (PL) | Siedlce Ujrzanów (PL) | Existing single circuit line will be upgraded to 400kV line in the same direction (1870 MVA, 90km) + upgrade of Kozienice substation to connect the new line | [10 empty] | design & permitting | 2020 | Progressed as planned. The investment also foresee extension works in substation Kozienice |  | 59
59 | 59. 375 | Płock (PL) | Olsztyn Mątki (PL) | New single circuit line 400kV (1870 MVA, 180km) with development of Olsztyn Mątki 400kV substation. | [10 empty] | design & permitting | 2020 | Progresses as planned |  | 59
59 | 59. 376 | Alytus (LT) | PL-LT border (PL) | Construction of Back-to-Back convertor station near Alytus 330kV substation. Construction of double circuit 400 kV OHL between Alytus and PL – LT border (2 x 1,870 MVA, 51 km). | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 59
59 | 59. 379 | Kruonis (LT) | Alytus (LT) | New double circuit 330kV OHL (2x1080 MVA, 53km). | [10 empty] | planned | 2015 | Progresses faster than intially planned to support the LitPol project |  | 59
60 | 60. 377 | Klaipeda (LT) | Telsiai (LT) | New single circuit 330kV OHL (943 MVA, 85km). | 700 | 3 | 3 | West LV region | [5 empty] | 2 | under construction | 2014 | Project delayed because of land renting issues. |  | “Nordbalt“ project. Planned DC connection between Lithuania and Sweden. The project will connect the Baltic grid to the Nordic and integrate the Baltic countries with the Nordic electricity market, increases security of supply. Possibility to connect offshore wind farms as well.
60 | 60. 378 | Panevezys (LT) | Musa (LT) | New single circuit 330kV OHL (1080 MVA, 80km). | [10 empty] | planned | 2018 | Project postponed after investment portfolio optimization |  | 60
60 | 60. 383 | Klaipeda (LT) | Nybro (SE) | (NordBalt) A new 300kV HVDC VSC partly subsea and partly underground cable between Lithuania and Sweden. (440km). | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 60
60 | 60. 62. 384 | RigaCHP1 (LV) | Imanta (LV) | A new 12.5km AC 330kV cable will be built from RigaCHP1 substation to Imanta substation. Both substations will be reconstructed, according new line connecting. New cable will be underground and one part will be underwater (under Daugava river). Expected capacity: 880MW. | [10 empty] | under construction | 2012 | Progresses as planned | The investment contributes also to project 62 | 60
60 | 60. A52 | Ekhyddan (SE) | Nybro/Hemsjö (SE) | New single circuit 400 kV OHL | [10 empty] | under consideration | 2019 | New investment in TYNDP |  | 60
60 | 60. 62. 385 | Grobina (LV) | Imanta (LV) | Kurzeme roject a Latvian grid reinforcement roject with new 330kV OHL construction and connection to the Riga node. New 330kV OHL construction mainly instead of the existing 110kV double circuit line route, 110kV line will be renovated at the same time and both will be assembled on the same towers. Length 380km, Capacity 800MW | [10 empty] | design & permitting | 2018 | Investment delays due to authorization process and the extensive works. | The investment contributes also to project 62 | 60
61 | 61. 380 | Visaginas (LT) | Kruonis (LT) | New single circuit 330kV OHL (1080 MVA, 200km). | 1400 | 4 | 5 | [6 empty] | 1 | planned | 2020 | Progresses as planned |  | “New NPP” project. Grid development for connection of new Lithuanian nuclear power plant planned in Visaginas to the power system. This project allows safe and reliable integration of new NPP to the power system.
61 | 61. 382 | Vilnius (LT) | Neris (LT) | New single circuit 330kV OHL (943 MVA, 50km). | [10 empty] | planned | 2020 | Progresses as planned |  | 61
62 | 62. 60. 384 |  |  |  | 450-600 | 1 | 1 | Riga region | [5 empty] | 1 |  |  | 0 | The investment contributes both to project 62 and project 64. For the technical description see project 62 | This project will increase the transfer capability between Estonia and Latvia and will accommodate RES generation in the Baltic Sea. This will be the 3rd corridor between these countries.
62 | 62. 60. 385 | [15 empty] | 0 | The investment contributes both to project 62 and project 64. For the technical description see project 62 | 62
62 | 62. 386 | Kilingi-Nomme(EE) | RigaCHP2(LV) | Estonia-Latvia third interconnection will consist of 330 kV AC OHL Harku-Lihula-Sindi in Estonian part and OHL between Kilingi-Nõmme substation in Estonia and TEC2 substation in Latvia. The third interconnection allows to increase the NTC between Estonia and Latvia additionally in the range of 450 to 600 MW . | [10 empty] | planned | 2020 | Progresses as planned |  | 62
62 | 62. 387 | Tartu (EE) | Sindi (EE) | A new 162km internal connection will be established on existing route resulting in double circuit line with 2 different voltages (330kV / 110kV). | [10 empty] | under construction | 2014 | Progresses as planned |  | 62
62 | 62. 388 | Harku (EE) | Sindi (EE) | New double circuit OHL with 2 different voltages 330 kV and 110 kV and with capacity 1200 MVA/240 MVA and a length 140 km. Major part of new internal connection will be established on existing right of way on the Western part of Estonian mainland. | [10 empty] | design & permitting | 2018 | Progresses as planned |  | 62
63 | 63. 389 | Eesti (EE) | Püssi (EE) | Reinforcement of existing 57km single circuit 330kV OHL. Expected capacity:1200 MVA. | 650 | 3 | 2 | NW Estonia | [5 empty] | 2 | commissioned | commissioned | Commissioned |  | Estlink2 ; The main driver for this cluster is integration need of Electricity Market. This project will increase the transfer capability between Estonia and Finland and will accommodate RES generation in the North of Estonia and will increase the SOS in the Baltics.
63 | 63. 390 | Balti (EE) | Püssi (EE) | Reconstruction of 68km single circuit 330kV OHL. | [10 empty] | commissioned | commissioned | Commissioned |  | 63
63 | 63. 391 | Püssi (EE) | Anttila (FI) | A new HVDC (450kV) connection will be built between Estonia and Finland. On the Finnish side, a 14km DC overhead line will be built to a new substation Anttila where the converter station will be placed. On the Estonian side, a 11km DC cable line will be built to a existing substation Püssi where the converter station will be placed. length of marine cable is 140km. Expected capacity: 650MW. | [10 empty] | under construction | 2014 | The expected date of commissioning is beginning of 2014, postponed a few months compared to the preliminary estimate end of 2013. |  | 63
64 | 64. 392 | Yllikkälä (FI) | Huutokoski (FI) | New 155km single circuit 400kV OHL and renovation of 400kV substations in Yllikkälä and Huutokoski. Expected capacity: 1850 MVA. | 700-1400 | 3 | 2 | West coast Finland | [5 empty] | 1 | under construction | 2013 | Progresses as planned. Expected date of commission is beginning of 2013. |  | Several 400 kV AC lines are planned in Finland to be built to increase the North-South transmission capacity thus enabling the integration of new renewable and conventional generation in northern Finland and to compensate the dismantling of the obsolescent exiting 220 kV lines. The commissioning of the lines is scheduled to take place in segments both in mid and long term.
64 | 64. 393 | Seinäjoki Ulvila Ventusneva (FI) | Tuovila (FI) Kristinestad (FI) Pyhänselkä (FI) | Four new single circuit 400kV OHL are part of project in upgrading Ostrobothnian 220kV system into 400kV, and strengthening the 400 kV grid in Northern Finland. Commissioning of first section in year 2011, second in 2014 third in ca. 2018 and fourth ca. 2020. total length of lines: 520 km. Expected capacity: 1850 MVA. | [10 empty] | under construction | 2011/2020 | Project has progressed as planned. Since TYNDP 2010 Seinäjoki-Tuovila has been constructed and Ulvila-Kristinestad has progressed to design and permitting phase. Keminmaa-Pyhänselkä is now presented as a separate investment item. |  | 64
64 | 64. A62 | Pyhänselkä (FI) | Petäjävesi or Vihtavuori (FI) | New single circuit 400 kV OHLs will be built from middle Finland to Oulujoki Area to increase the capacity between North and South Finland. | [10 empty] | design & permitting | 2020 | New investment in TYNDP |  | 64
65 | 65. 394 | Hikiä (FI) | Forssa (FI) | New 80km single circuit 400kV OHL and building of 400 kV substation in Forssa. | 800 | 2 | 4 | SW Finland | [5 empty] | 1 | design & permitting | 2015 | Progresses as planned |  | Reinforcements due to changed exchange patterns and reliable grid operation of South-West Finland.
65 | 65. A63 | Forssa (FI) | Lieto (FI) | New 67km single circuit 400 kV OHL. | [10 empty] | under consideration | 2017 | New investment in TYNDP
66 | 66. 400 | Ekhyddan (SE) | Barkeryd (SE) | New single circuit 400kV OHL. | 1250 | 4 | 1 | [6 empty] | 2 | design & permitting | 2017 | Progresses as planned |  | The new subsea connection to the island of Gotland will be two connections with a capacity of 500 MW for each cable.
66 | 66. 401 | Västervik (SE) | Gotland (SE) | New DC subsea cable interconnection ±300kV (2*500 MW). | [10 empty] | design & permitting | 2017 -2021 | The first cable is progressing as planned but the second cable is planned to be in commission after 2017 due to adjustments to RES. | The new subsea connection to the island of Gotland will be two connections with a capacity of 500 MW for each cable. The first cable is planned to be in commission 2017 and the second is planned to be in commission between 2020 and 2021. | 66
67 | 67. 402 | Barkeryd (SE) Hallsberg (SE) | Tveiten (NO) Hurva (SE) | "South West link" consisting of three main parts: 1) New 400kV line between Hallsberg and Barkeryd (SE) 2) New double HVDC VSC underground cable and OHL between Barkeryd and Hurva (SE) 3) New double HVDC VSC line between Barkeryd (SE) and Tveiten (NO). The project also include new substations and converter stations in the connection points line double circuit new OHL Hallsberg - Barkeryd 170km, underground VSC Barkeryd - Hurva 250km and VSC Barkeryd - Tveiten with 103km on the Norwegian side. Expected capacity: 1200MW. | 1400 (E-W), 1200 (N-S) | 3 | 2 | [6 empty] | 3 | design & permitting | 2014-2019 | Commissioning date updated after bilateral negotiations between the two countries. Hallsberg-Barkeryd-Hurva expected in 2014; Barkeryd-Tveiten in 2019 |  | 5 investments of HVDC and AC lines in Sweden and Norway as well as between the countries, resulting in increased GTC and market integration
67 | 67. 411 | Rød (NO) | Sylling (NO) | Voltage upgrading of existing single circuit 300kV OHL Rød-Tveiten-Flesaker-Sylling in connection with the new HVDC line to Sweden, the Syd Vest link. | [10 empty] | design & permitting | 2018/2020 | Investment postponed, especially because of long permitting processes. |  | 67
67 | 67. 412 | Rød (NO) - Sylling (NO) - Flesaker (NO) - | Hasle (NO) Tegneby (NO) Tegneby (NO) | Reinvestment and capacity increase Oslofjord 400kV subsea cables. Three cables: Filtvedt - Brenntangen, Solberg - Brenntangen, and Teigen - Evje. | [10 empty] | design & permitting | 2015 | Investment delayed, especially because of long permitting processes. One cable is under construction. |  | 67
68 | 68. 421 | Ofoten (NO) | Balsfjord (NO) | New 160km single circuit 400kV OHL. | 350-1500 | 2 | 1 | Northern Norway | [5 empty] | 2 | design & permitting | 2016 | Investment delayed, especially because of long permitting processes. |  | The main purpose of this project is to secure the northern part of NO.
68 | 68. 422 | Balsfjord (NO) | Hammerfest (NO) | New 360 km single circuit 400kV OHL. | [10 empty] | design & permitting | 2018 | Investment delayed, especially because of long permitting processes.
68 | 68. 423 | Skaidi (NO) | Varangerbotn (NO) | New 230 km single circuit 400kV OHL. | [10 empty] | planned | 2022 | Investment postponed, especially because of long permitting processes.
69 | 69. 424j | Bramford (GB) | Twinstead (GB) | New 400kV double circuit | 2600 | 4 | 1 | [6 empty] | 2 | Design & Permitting | 2018/2019 | Delayed by one year to 2018/19 due to an anticipated slower growth in the uptake of wind. |  | This project supports the evacuation of energy from a new nuclear power plant and from the offshore wind parks of the Eastern coast of GB.
69 | 69. A39 | Sizewell C (GB) | Bramford (GB) | Reconductor Sizewell C-Bramford-Sizewell | 1800 | [9 empty] | Planned | 2015/16 | New investment in TYNDP, answering an expected growth in offshore wind and nuclear generation in and around Norfolk and East Anglia, above what was anticipated for the TYNDP 2010. |  | 69
69 | 69. A40 | Norwich Main (GB) | Bramford (GB) | Norfolk Offshore Wind: NORW-BRFO Tee-in to Lowestoft | [10 empty] | Planned | 2015/16 | New investment in TYNDP, answering an expected growth in offshore wind and nuclear generation in and around Norfolk and East Anglia, above what was anticipated for the TYNDP 2010. |  | 69
69 | 69. A41 | Walpole (GB) | Bramford (GB) | Reconductoring Norwich Main-Walpole and Bramford-Norwich Main | [10 empty] | Under Construction | 2015/2016 | New investment in TYNDP, answering an expected growth in offshore wind and nuclear generation in and around Norfolk and East Anglia, above what was anticipated for the TYNDP 2010. |  | 69
70 | 70. 405 | Kristiansand (NO) | Rød (NO) | Voltage upgrading of an existing single circuit 300kV OHL and a new section of OHL between Rød and Bamle. Total length: 175km. | 700 | 5 | 2 | [6 empty] | 2 | design & permitting | 2014 | Progresses as planned |  | Market integration and RES integration.
70 | 70. 426 | Kristiansand (NO) | Tjele (DK) | Skagerak 4: 4th HVDC connection between Southern Norway and Western Denmark, built in parallel with the existing 3 HVDC cables; new 700MW including 230km 500kV DC subsea cable. | [10 empty] | Under construction | 2014 | Progresses as planned |  | 70
71 | 71. 427 | Endrup (DK) | Eemshaven (NL) | COBRA: New single circuit HVDC connection between Jutland and the Netherlands via 350km subsea cable; the DC voltage will be up to 320kVand the capacity 600-700MW. | 700 | 5 | 2 | [6 empty] | 2 | design & permitting | 2016 | Progresses as planned |  | Cobra
72 | 72. 430 | Revsing (DK) | Landerupgård (DK) | New 18km single circuit 400kV line via cable with capacity of approx. 1200 MW. | 950 | 4 | 1 | DK west and north DE | [5 empty] | 2 | Planned | 2017 | Progresses as planned |  | The main purpose of the project is to integrate and transmit large scale wind power in DK west.
72 | 72. 435 | Endrup (DK) | Revsing(DK) | Upgrade of 50km double-circuit 400kV OHL to reach a capacity of approx. 2000MW. | [10 empty] | design & permitting | 2015 | Earlier date of commissioning than initially expected caused by reprioritization of project. Also one of the substations has been changed: Endrup was replaced by Tjele. |  | 72
72 | 72. 436 | Idomlund (DK) | Endrup (DK) | New 74km single circuit 400kV line via cable with capacity of approx. 1200MW. | [10 empty] | under consideration | 2018/2020 | Envisaged route changed from Idomlund-Tjele to Idomlund-Endrup |  | 72
73 | 73. 432 | Asvæsværket (DK) | Kyndbyværket (DK) | New 60km single circuit 400kV line via cable with capacity of approx. 1200 MW. | >1000 | 4 | 4 | [6 empty] | 1 | design & permitting | 2014 | Progresses as planned |  | The project will increase the stability of the DK eastern power system and allow for larger transmission and transit.
73 | 73. 433 | Glentegård (DK) | Amagerværket & H.C. Ørstedværket (DK) | New 22km single circuit 400kV line via cable with capacity of approx. 1200MW. | [10 empty] | planned | 2016 | Progresses as planned |  | 73
74 | 74. 443 | Richborough (GB) | Zeebrugge (BE) | Nemo Project: New DC sea link including 135km of 250kV DC subsea cable with 1000MW capacity | >1000 | 1 | 2 | Thames estuary | [5 empty] | 2 | Planned | 2018 | Investment delayed to 2018 due to authorization delays related to needed internal grid reinforcements | Nemo project | Interconnection between UK and the mainland Europe(BE).
74 | 74. 449 | Richborough (GB) | Canterbury (GB) | New 400kV double circuit OHL and new 400kV substation in Richborough | [10 empty] | Planned | 2019/2020 | Progresses as planned | The reinforcements shown here reflect initial options but are subject to consultation and review of other feasible options. | 74
74 | 74. 450 | Sellindge (GB) | Dungeness (GB) | Reconductor Sellindge-Dungeness | [10 empty] | Planned | 2014/2015 | The reconductoring of the Sellindge to Dungeness circuits (Project 450) remain as originally planned in the TYNDP 2010. |  | 74
75 | 75. 444 | Zomergem (BE) | Zeebrugge (BE) | New approx. 50km double-circuit 380kV ( 3000MVA for each circuit) between Zomergem and Zeebrugge to evacuate the locally (offshore) produced power line and allow connection of NEMO to 380 kV grid. | 1500 | 4 | 1 | [6 empty] | 2 | design & permitting | 2014 | Progresses as planned | Stevin project | The project allows the connection of 2,3 GW of offshore wind production. It also allows onshore RES connection. This project enhances security of supply of Belgian coastal area and allows the NEMO connection.
75 | 75. A28 | Zeebrugge (BE) | offshore platform (BE) | 2 offshore platforms connected to AC grid with underground cables including compensation | [10 empty] | planned | 2016 | New investment in TYNDP, resulting from recent studies demonstrating such a platform would be optimal for Belgian offshore wind off take. Planning and implementation of the project depends on the evolution of Belgian legislation. | Belgian offshore platform | 75
76 | 76. A42 | Pelham (GB) | Waltham Cross (GB) | Reconductor Pelham-Rye House-Waltham Cross | 7600 | 4 | 1 | London area | [5 empty] | 3 | Design & Permitting | 2015/2016 | New investment in TYNDP | New projects in the London area, not previously reported in the TYNDP 2010. All of these investments are required due to a combination of age related asset replacement, increasing power flows and changing customer demand connection requirements. A further driver for all of these projects is that power flows through London increase during interconnector export to mainland Europe (Power flows from the north through London to the interconnectors within the Thames Estuary). | All of these investments are required due to a combination of age related asset replacement, increasing power flows and changing customer demand connection requirements. A further driver for all of these projects is that power flows through London increase during interconnector export to mainland Europe (Power flows from the north through London to the interconnectors within the Thames Estuary).
76 | 76. A43 | Hackney (GB) | Waltham Cross (GB) | Uprate to 400kV Hackney-Tottenham-Waltham Cross | [10 empty] | Design & Permitting | 2015/2016 | New investment in TYNDP |  | 76
76 | 76. A44 | Hackney (GB) | St. John's Wood (GB) | New 400kV St. John's Wood-Hackney double circuit | [10 empty] | Design & Permitting | 2017/2018 | New investment in TYNDP |  | 76
76 | 76. A45 | Tilbury (GB) | Elstree (GB) | Uprate to 400kV Tilbury-Warley-Elstree | [10 empty] | Planned | 2021/22 | New investment in TYNDP |  | 76
76 | 76. A46 | St. John's Wood (GB) | Wimbledon (GB) | New 400kV St. John's Wood-Wimbledon cables | [10 empty] | Design & Permitting | 2017/2018 | New investment in TYNDP |  | 76
76 | 76. A47 | West Weybridge (GB) | Beddington (GB) | Uprate to 400kV West Weybridge-Chessington-Beddington | [10 empty] | Planned | 2017/2018 | New investment in TYNDP |  | 76
77 | 77. 452 | Deeside (GB) | Hunterston (GB) | New 2000MW HVDC Link via 360km 500kV DC subsea cable on the West Coast of the UK and new 400kV substation in Deeside | 4000 | 4 | 1 | [6 empty] | 3 | Design & Permitting | 2015/2016 | Progresses as planned (still targetting the financial year 2015/2016) |  | This project facilitates the connection of RES and the connection of the remote Scottish Islands.
77 | 77. 453 | Peterhead (GB) | Hawthorn Pit (GB) | New 2000MW HVDC Link via 365km 500kV DC subsea cable on the East Coast of the UK and new 400kV substation in Hawthorn Pit | [10 empty] | Planned | 2018/2019 | Progresses as planned (still targetting the financial year 2018/2019) |  | 77
77 | 77. 454 | Hawthorn Pit (GB) | Norton (GB) | Uprate to 400kV Hawthorn Pit-Norton | [10 empty] | Planned | 2018/2019 | Progresses as planned (still targetting the financial year 2018/2019) |  | 77
77 | 77. 456 | Harker (GB) | Quernmore (GB) | Reconductor Harker-Hutton-Quernmore | [10 empty] | Design & Permitting | 2014/2015 | Progresses as planned (still targetting the financial year 2014/2015) |  | 77
77 | 77. 449a | Gravir (GB) | Beauly (GB) | Western Isles link. New 450MW HVDC link, +/- 150kV. Route length 156km (80km subsea, 76km onshore underground cable). | [10 empty] | design & permitting | 2015 | The 2010 TYNDP showed commissioning scheduled for 2013. However the developers of the large Western Isles wind farm projects which drive the need for the link, have experienced commercial delays. Commissioning of the link is therefore now projected for 2015. |  | 77
77 | 77. 450a | Kergord and Caithness (GB) | Blackhillock (GB) | The Moray Firth HVDC development - Shetland and Caithness links with offshore HVDC hub. Three ended HVDC link, 2 x 600MW legs and common 1200MW leg. Total route length 395km. | [10 empty] | design & permitting | 2016 | Projected commissioning is now 2016. The 2010 TYNDP showed commissioning scheduled for 2014. At that time the concept was to include an offshore node in a subsea HVDC link that was planned from Shetland to the Scottish mainland. That link was being designed to connect the Viking Energy wind farm project on Shetland. The Shetland link was termed the Base Project and the node was referred to as Incremental Works. The node would receive a connection from Caithness in 2016 for the export of renewables from that region and would also offer the potential for connection of adjacent offshore wind farms. However, the Viking project suffered consenting delays, and so late in 2010 the Caithness to Moray HVDC link was re-designated as the Base Project into which the node would be incorporated. The achievable timetable for the Caithness leg with commissioning in 2016 then became the timetable for the investment. |  | 77
77 | 77. 451a | Dounreay (GB) | Beauly (GB) | String a second 275kV OHL circuit on existing towers. | [10 empty] | under construction | 2012 | Progresses as planned |  | 77
77 | 77. 452a | Beauly (GB) | Kintore (GB) | Reconductor existing 275kV overhead line route. | [10 empty] | design & permitting | 2014 | Progresses as planned (still targetting the financial year 2014/2015) |  | 77
77 | 77. 453a | Blackhillock (GB) | Kincardine (GB) | Reinsulate existing 275kV route for 400kV operation and establish three new 400kV substations en-route. | [10 empty] | design & permitting | 2016 | Scheduled completion in 2016 is one year later than foreseen in the 2010 TYNDP. The north of Scotland transmission system is significantly depleted by construction outages to accommodate the main Beauly-Denny rebuild by 2014. The system access that is available for this investment (453a) to accommodate a build-up of renewable generation leads to the revised completion date in 2016. |  | 77
77 | 77. 455 | Beauly (GB) | Denny (GB) | New double circuit 400kV OHL (220km) with new terminal substations and substation extensions en route. | [10 empty] | under construction | 2014 | Progresses as planned |  | 77
77 | 77. 457 | Harker (GB) | Stella West (GB) | New 400kV series and shunt compensation at a number of locations across the Anglo-Scottish border. | [10 empty] | design & permitting | 2014/2015 | Progresses as planned |  | 77
78 | 78. 458 | Hinkley (GB) | Seabank (GB) | New 60km double circuit 400kV OHL | 3200 | 4 | 1 | [6 empty] | 2 | design & permitting | 2019/20 | Seabank has been delayed by three years due to corresponding delays to the associated new nuclear project. |  | Project needed for renewables off of the South West peninsula, the replanting of Hinkley Point nuclear power station and further CCGT at Seabank
79 | 79. A48 | Trawsfynydd (GB) | Treudyyn (GB) | Reconductor Trawsfynydd-Treuddyn | 1700 | 4 | 1 | [6 empty] | 3 | Planned | 2017/2018 | New investment in the TYNDP, as it was mistakenly omitted from the TYNDP 2010 submission. It is necessary due to RES Integration in North Wales. |  | Reinforcement of the internal grid to integrate the additional flows from the RES generation.
79 | 79. 459 | New Substation (GB) | Legacy-Shrewsbury Tee (GB) | New 400kV double circuit OHL and new 400kV substation in Mid-Wales | 880 | [9 empty] | Design & Permitting | 2016/2017 | Progresses as planned (still targetting the financial year 2016/2017) | Investment needed to connect Mid-Wales wind farms | 79
79 | 79. 459b | Wylfa (GB) | Pembroke (GB) | New HVDC bipolar interconnection with possible offshore connection points at the Irish Sea offshore wind farm. | 2000 | [9 empty] | Planned | 2020/21 | Design Change – The design of the HVDC reinforcement circuit from Wylfa has changed from that in the TYNDP 2010 to now terminate at Pembroke instead of Mid-Wales. This has the potential to save some onshore consenting challenges. Additional benefits may be realised by coordinating the development of the offshore transmission assets with that of the onshore system. The location of the Wylfa HVDC termination may yet move offshore to be located closer to the wind turbines. The expected commissioning date has remained at 2020. |  | 79
79 | 79. 460 | Pentir (GB) | Trawsfynydd (GB) | Upgrade Pentir-Trawsfynydd to double circuit | 3800 | [9 empty] | planned | 2016/2017 | Slight delay in expected commissioning date | Investment needed to accommodate new wind generation off Anglesey and nuclear replanting at Wylfa | 79
79 | 79. 460b | Wylfa (GB) | Pentir (GB) | New 400kV Wylfa-Pentir double circuit | 3600 | [9 empty] | planned | 2017/2018 | Progresses as planned (still targetting the financial year 2017/2018) | Investment needed to connect offshore wind and nuclear | 79
80 | 80. 461 | Woodland (IE) | Deeside (GB) | A new 260 km HVDC (200 kV DC) underground and subsea connection between Ireland and Britain with 500MW capacity. On the Irish side, a 45km direct current underground cable will be built to the Woodland substation where the VSC converter station will be placed. | 500 | 3 | 2 | Island of Ireland? | [5 empty] | 2 | under construction | 2012 | Investment still on schedule for 2012, with less than 1-year delay |  | This medium term project will establish 500MW interconnection capacity between Ireland and GB
81 | 81. 462 | Woodland (IE) | Turleenan (NI) | A new 140 km single circuit 400 kV 1500 MVA OHL from Turleenan 400/275 kV in Northern Ireland to Woodland 400/220 kV in Ireland. This is a new interconnector project between Ireland and Northern Ireland. | 600 | 3 | 2 | NE Ireland | [5 empty] | 1 | design & permitting | 2016 | Project delayed due to permitting process in both jurisdictions. The intermediate station Moyhill is differed pending outcome of future load growth. |  | This medium term project will increase transfer capacity between Ireland and N Ireland to improve security of supply and facilitate Single Market development
82 | 82. 470 | Bellacorick (IE) | Cashla or Flagford (IE) | New 130km single circuit 400 kV OHL from north West Mayo to the EHV system. | 650 | 4 | 1 | [6 empty] | 3 | design & permitting | 2019 | Investment technical description and commissioning date are now defined, and status changed to "design and permitting". |  | The infrastructure development is required to facilitate connection of renewables in the North and West of the Island; It will further integrate the Ireland and N Ireland transmission systems and provide capacity for substantial demand growth in the area.
82 | 82. A37 | tbd (NI) | Tunes Wind (NI) | North coast off-shore wind farm. Multiple connection options are under consideration. | 300 | [9 empty] | under consideration | 2020 | New investment in TYNDP |  | 82
82 | 82. 463 | tbd (IE) | tbd (NI) | Strengthening of EHV networks (partial uprate and new) into Donegal and North and West of Northern Ireland and enhanced links between the two countries. Various technologies are being considered. | 1500-2000 | [9 empty] | under consideration | 2020 | New investment in TYNDP |  | 82
83 | 83. 467 | Moneypoint (IE) | Kilpaddoge (IE) | A new 10km single circuit 220kV 500MVA (underground+subsea) cable constructed across the River Shannon Estuary from Moneypoint in Co. Clare to Tarbert or a new Kilpaddoge station in Co. Kerry. A new 400/220kV transformer at Moneypoint station is included in this project. | 1500-2000 | 4 | 1 | [6 empty] | 2 | design & permitting | 2014 | Project delayed by 2 years because awaiting the completion of the Moneypoint 400 kV station redevelopment works to facilitate the new connection, and a delay due to foreshore permitting arising from a change in one of the connection points (from Tarbert to Kilpaddoge) |  | The infrastructure development is required to facilitate connection of renewables in the South of the Island; the project will also facilitate new interconnection connecting to the grid in the south.
83 | 83. 468 | Moneypoint (IE) | North Kerry (IE) | A new 27km single 400 kV circuit, consisting of a submarine cable from Moneypoint across the Shannon Estuary and an overhead line to a new 400 kV station in north Kerry | [10 empty] | design & permitting | 2019 | Investment technical description and commissioning date are now defined, and status changed to "design and permitting". | Increased capacity between the South-West and the Mid-West regions. | 83
83 | 83. 469 | Knockraha (IE) | Dunstown (IE) | A new 250km single circuit 400kV OHL from Cork to the east, with one intermediary station in the South-East. | [10 empty] | design & permitting | 2020 | Investment technical description and commissioning date are now defined, and status changed to "design and permitting". | Increased capacity between Knockraha in the South-West and Dunstown in the Mid-East regions. The project will also facilitate future interconnection. | 83
84 | 84. 471 | Maynooth (IE) | Woodland (IE) | A new 25km single circuit 400kv OHL from Woodland 400 kV station to a new 400 kV station near or at Maynooth 220 kV station. The project may involve upgrading existing 220 kV circuits to 400 kV or utilizing the route. | 1500-2000 | 4 | 1 | Dublin area | [5 empty] | 2 | under consideration | >2020 | TYNDP 2010 investment 471 now presented in two parts (471 and IE2) |  | This project will provide a high capacity path around Dublin improving security of supply to the city and operability of the Dublin network
84 | 84. A31 | Finglas / Huntstown (IE) | Woodland (IE) | A new 25km single circuit 400 kV from Woodland 400 kV station to a new 400 kV station in the vicinity of Huntstown and Finglas 220 kV stations. | [10 empty] | under consideration | >2020 | New investment in TYNDP to avoid overloads in Dublin City network and to ensure supply to north Dublin City load |  | 84
84 | 84. A32 | Dunstown (IE) | Maynooth (IE) | A new 40km single circuit 400kV OHL circuit from Dunstown 400 kV station to a new 400 kV station in the vicinity of Maynooth 220 kV station. | [10 empty] | under consideration | >2020 | New investment in TYNDP to avoid overloads in Dublin City network, split out from TYNDP2010 investment 471 |  | 84
84 | 84. A33 | Carrickmines (IE) | Dunstown (IE) | A new 45km single circuit 400kV OHL from Dunstown 400 kV station to a new 400 kV station in the vicinity of Carrickmines 220 kV station. | [10 empty] | under consideration | >2020 | New investment in TYNDP to avoid overloads in Dublin City network |  | 84
85 | 85. A3 | F. Alentejo - Ourique - Tavira (PT) |  | New 122km double-circuit 400+150 kV OHL F. Alentejo-Ourique-Tavira. The realization of this connection can take advantage of some already existing 150kV single lines, which can be reconstructed as double circuit line 400+150kV, with needed extension of existing Ourique substation to include 400 kV facilities. | 1390 | 4 | 1 | [6 empty] | 1 | planned | 2018/2019 | New investment in TYNDP This project helps integrate new solar and wind power plans in Alentejo and Algarve area |  | This project integrates new amounts of solar (and also some wind) generation in the south of Portugal. The existing network of 150 kV is not sufficient to integrate these amounts of power and a new 400 kV axis should be launched in this region, establishing a connection between the two Southern interconnections between Portugal and Spain, the Ferreira do Alentejo-Alqueva-Brovales and Tavira-Puebla de Gusman. This axis will also close a ring of 400 kV in the Southern part of Portugal that will guarantee the load growth in the region (Algarve is one of the regions that presents the biggest growth rate in Portugal) in a safe, secure and quality way.
86 | 86. A49 | Keadby (GB) | Grimsby West (GB) | KEAD-KILL KILL-SHBA KEAD-GRIW circuit uprate | 5200 | 4 | 1 | [6 empty] | 2 | under consideration | long term | New investment in TYNDP | These investments are required due to unprecedented volumes of offshore wind generation connection requests. | This projects helps accommodate new offshore RES generation in the North Sea .
86 | 86. A50 | Under Consideration (GB East Coast) | Under Consideration (GB East Coast) | Connection of Triton Knoll, Doggerbank & Hornsea GB Wind Farms and all associated works | [10 empty] | under consideration | long term | This investment groups former 424b, 424c, 424d, 424e, 424f, 424g, 424h and 424i investments of TYNDP 2010. The group of projects on the east coast of Great Britain has been removed as work is in progress to optimize the onshore/offshore coordination and reduce potential consenting issues. Given the potential for more than 20 GW of renewable offshore generation capacity in UK waters on the East Coast it is expected that multiple connection sites will be required together with suitable circuit capacity, both onshore and offshore. |  | 86
87 | 87. A53 | Forsmark (SE) | Råsten (SE) | New 50km single circuit 400kV OHL | 1215 | 2 | 4 | [6 empty] | 2 | design & permitting | 2019 | New investment in TYNDP |  | Several 400 kV AC lines and stations due to increase of nuclear power and RES, result in increased GTC
87 | 87. A54 | Råsten (SE) | Hamra (SE) | New 85km single circuit 400kV OHL | [10 empty] | design & permitting | 2019 | New investment in TYNDP |  | 87
87 | 87. A55 | Forsmark (SE) | Stackbo (SE) | New 70km single circuit 400kV OHL | [10 empty] | design & permitting | 2018 | New investment in TYNDP |  | 87
87 | 87. A56 | Ängsberg (SE) | Horndal (SE) | New 55km single circuit 400kV OHL | [10 empty] | under consideration | 2020 | New investment in TYNDP |  | 87
87 | 87. A57 | Horndal (SE) | Lindbacka (SE) | New 145km single circuit 400kV OHL | [10 empty] | under consideration | 2020 | New investment in TYNDP |  | 87
87 | 87. A58 | Hamra (SE) | Västerås (SE) | New 50km single circuit 400kV OHL | [10 empty] | planned | 2021 | New investment in TYNDP |  | 87
87 | 87. 399 | Vasteras (SE) | Lindbaka (SE) | Upgrade/Replacement of existing single circuit 220kV lines to 400kV. | [10 empty] | under consideration | 2021 | All investments in project 87 has been prioritized and result in new commissioning dates |  | 87
88 | 88. A23 | offshore wind farms (FR) | several French substations (FR) | Subsea cables and substations works | 3000(MT) 6000 (LT) | 4 | 1 | [6 empty] | 3 | planned | 2015-2020 | New investment in TYNDP, required to connect offshore wind farms as decided by the French government in 2010 | Project development will adapt to the pace of generation installation | Connection of 6 GW offshore wind farms in 2 phases. First 3 GW phase in progress (tender).
89 | 89. A24 | Calan (FR) | Plaine-Haute (FR) | New 80km double circuit 220kV underground cable with 2 phase shifters and T-connection of an existing HV substation; 1150 MVARs of capacitors and SVC; new transformer 400/220kV | 500 MW | 2 | 4 | Brittany area | [5 empty] | 1 | design & permitting | 2017 | New investment in TYNDP, required to secure Brittany's supply, along with DSM management plan and a new CCGT in Finistère area. |  | This project is necessary to security Brittany's supply.
90 | 90. 131 | Bickigen (CH) |  | Addition of a second 400/220kV transformer in an existing substation. | 4000 | 1 | 2 | [6 empty] | 3 | design & permitting | 2012 | Progresses as planned |  | This project increase the transfer capability between FR, DE , AT towards pump storage in CH.
90 | 90. 132 | Mühleberg (CH) |  | Construction of a new 400/220kV substation. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 90
90 | 90. 134 | Bassecourt (CH) | Romanel (CH) | Construction of different new 400kV line sections and voltage upgrade of existing 225kV lines into 400kV lines. Total length: 140km. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 90
90 | 90. 136 | Area of Bodensee (DE, AT, CH) |  | Construction of new lines, extension of existing ones in direction of 400/220/110kV-substation. This project will increase the current power exchange capacity between the DE, AT and CH. The project is expected to increase NTC and Improved the security of supply. | [10 empty] | planned | long term | Progress as planned |  | 90
90 | 90. 129 | Beznau (CH) | Mettlen (CH) | Upgrade of the existing 65km double circuit 220kV OHL to 400kV. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 90
90 | 90. 130 | La Punt (CH) | Pradella / Ova Spin (CH) | Installation of the second circuit on existing towers of a double-circuit 400kV OHL (50km). | [10 empty] | planned | 2017 | Delays due to authorization process. |  | 90
90 | 90. 133 | Bonaduz (CH) | Mettlen (CH) | Upgrade of the existing 180km double circuit 220kV OHL into 400kV. | [10 empty] | under consideration | 2020 | Progresses as planned |  | 90
90 | 90. 44. 170 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 172 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 173 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 176 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 45. 177 | Goldshöfe (DE) | Bünzwangen (DE) | A new 380kV OHL. Length: 45km. | [10 empty] | under consideration | 2020 | Progresses as planned | The investment contributes also to project 45. | 90
91 | 91. 121 | Bickigen (CH) | Romanel (CH) | Construction of different new 400kV OHL sections and voltage upgrade of existing 225kV lines into 400kV lines. Total length: 250km. | >4000 | 4 | 1 | [6 empty] | 2 | design & permitting | 2015 | Delays due to authorization process. |  | The investments help accommodating new pumping storage units which support mainly the increasing RES generation in North Sea area.
91 | 91. 122 | Chippis (CH) | Lavorgo (CH) | Construction of different new 400kV line sections and voltage upgrade of existing 225kV lines into 400kV. Total length: 120km. | [10 empty] | design & permitting | 2017 | Delays due to authorization process. |  | 91
91 | 91. 123 | Mettlen (CH) | Ulrichen (CH) | Construction of different new 400kV line sections and voltage upgrade of existing 225kV lines into 400kV lines. Total length: 90km. | [10 empty] | planned | 2019 | Delays due to authorization process. |  | 91
91 | 91. 125 | Schwanden (CH) | Limmern (CH) | New 400kV double circuit (OHL and underground cable) between Schwanden and Limmern. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 91
91 | 91. 126 | Golbia (CH) | Robbia (CH) | New 2x 400kV cable connection between Golbia and the Bernina line double circuit. | [10 empty] | under consideration | 2019 | Progresses as planned |  | 91
91 | 91. 127 | Magadino (CH) | Verzasca (CH) | Upgrade of existing 150kV line into 220kV line. | [10 empty] | under consideration | 2020 | Progresses as planned |  | 91
91 | 91. 128 | Bâtiaz (CH) | Nant de Drance (CH) | New 400kV double circuit OHL between Bâtiaz and Châtelard. New 2x 400kV cable connection between Châtelard and Nant de Drance. Total length: 22km. | [10 empty] | design & permitting | 2016 | Delays due to authorization process. |  | 91
92 | 92. 146 | Aachen/Düren region (DE) | Lixhe (BE) | Connection between Germany and Belgium including new 100km HVDC underground cable and extension of existing 380kV-substations. On Belgian side, new 380 kV circuit between Lixhe and Herderen and second 380 kV overheadline in/out from Herderen to Lixhe. In Belgium, addition of 2 transformers 380/150 kV in Lixhe and in Limburg part; | 1000 | 3 | 2 | Northern Belgium | [5 empty] | 2 | design & permitting | 2017 | The project entered design and permitting phase in 2011, technical description has been completed and expected date of comissioning is 2017 | Alegro Project | First Belgium-Germany interconnection. This project enhances security of supply of both BE and DE. This HVDC link in an AC grid brings flexibility and bidirectional power control allowing integration of RES in both countries. This project aims to be a demonstration for HVDC link integration in the AC meshed grid.
93 | 93. 413 | Ørskog (NO) | Fardal (NO) | New 285 km single circuit 400kV OHL. | 2250 | 3 | 3 | South west of Trondheim (county Møre and Romsdal) | [5 empty] | 3 | under construction | 2015 | Investment delayed due to due to long permitting procedure. | The project is key to improve SoS in Mid-Norway: presently, for several N-1 contingencies, load might be disconnected. The project is also the pre-requisite to lift the ban on RES development in the whole area covered by the new line Ørskog - Fardal. | Security of supply for mid-Norway (Møre and Romsdal mainly) and RES integration in western Norway.
93 | 93. 398A | Under consideration (SE) |  | New shunt compensation of OHL. | [10 empty] | under consideration | 2015 | New part of investment 398 in TYNDP 2010 | Investment 398 in TYNDP 2010 have been divided into 398A and 398B. 398B is described in project 104. | 93
93 | 93. 403 | Scandinavia north (SE) | Scandinavia South (SE) | A joint Stattnett & Svenska Kraftnat study north - south reinforcement (AC or VSC), expected length: 400 - 500km under study. | [10 empty] | under consideration | 2025 | Postponed after reprioritization of the project portfolio |  | 93
93 | 93. 414 | Fardal (NO) | Aurland (NO) | Voltage upgrading of existing single circuit 300kV OHL Fardal-Aurland Extension of 413 - Ørskog - Fardal. | [10 empty] | planned | 2020 | Investment postponed, especially because of long permitting processes. |  | 93
93 | 93. 417 | Aura/Viklandet (NO) | Fåberg (NO) | Voltage upgrading of existing single circuit 300kV OHL Aura/Viklandet-Fåberg. | [10 empty] | under consideration | long term | Investment postponed, especially because of long permitting processes. |  | 93
93 | 93. 416 | Klæbu (NO) | Aura/ Viklandet (NO) | Voltage upgrading of existing single circuit 300kV OHL Klæbu-Aura. | [10 empty] | design & permitting | 2018 (2016-2020) | Investment postponed, especially because of long permitting processes. |  | 93
94 | 94. 139 | Vierraden (DE) | Krajnik (PL) | Upgrade of existing 220 kV line Vierraden-Krajnik to double circuit 400 kV OHL. | >1000 | 1 | 2 | [6 empty] | 1 | design & permitting | long term | Expected date of commissioning was adjusted due to long permitting process and strong local public resistance. |  | PSTs – Control of the transits of power on the polish synchronous profile (increase of import capacity, increase of grid operation safety).
94 | 94. A68 | Krajnik (PL) |  | Upgrade 400 kV | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A69 | Mikułowa (PL) |  | Upgrade 400 kV | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A70 | Krajnik (PL) |  | New PST | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A71 | Mikułowa (PL) |  | New PST | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
95 | 95. A119 | Dobrudja(BG) | Burgas (BG) | New 140km single circuit 400kV OHL in parallel to the existing one. | 1500 | 4 | 3 | [6 empty] | 1 | planned | 2016 | New investment in TYNDP, required to accommodate 2000MW RES in Dobrudja region |  | It contributes to the accommodation of large amount of RES in Dobrudja region (2000 MW). It also contributes to North-South transfers and increases the SoS in Burgas region.
95 | 95. 265 | Vidno (BG) | Svoboda (BG) | New 400kV double circuit OHL to accommodate 2000 MW RES generation in N-E Bulgaria (Dobruja region). Line length: 2x70km. | [10 empty] | planned | 2015 | Moved from LT(TYNDP 2010) to MT due to high interest for very fast implementation of about 2000MW RES generation in Dobrudja region |  | 95
95 | 95. 263 | SS 4 /11 kV Svoboda(Krusari) |  | New 400/110kV substation to accommodate the expected RES generation(2000MW) in N-E Bulgaria (Dobruja region) | [10 empty] | planned | 2015 |  |  | 95
95 | 95. 264 | SS 4 /11 kV Vidno |  | New 400/110kV substation to accommodate the expected RES generation(2000MW) in N-E Bulgaria (Dobruja region) | [10 empty] | planned | 2015 |  |  | 95
95 | 95. 266 | IN-OUT in Svoboda on actual 4 kV OHL Isaccea(RO)-Varna (BG) |  | New 400kV double circuit OHL to accommodate the expected RES generation(2000MW) in N-E Bulgaria (Dobruja region). Line length: 2x10km. | [10 empty] | planned | 2015 |  |  | 95
96 | 96. A64 | Keminmaa (FI) | Pyhänselkä (FI) | Integration of new generation + increased transmission capacity demand. | 1000 | 4 | 1 | [6 empty] | 1 | under consideration | 2019 | New investment in TYNDP, split out from investment 393, and now been moved as a stand-alone project cluster because of his specific benefits. |  | Integration of new generation and increased transmission capacity demand.
97 | 97. A65 | Uusnivala (FI) | Pyhäjoki (FI) | New double circuit 400 kV OHLs | 1600 | 4 | 5 | [6 empty] | 1 | under consideration | 2020 | New investment in TYNDP, required to connect Fennovoimas new 1 250-1 700 MW nuclear power plant that will be built in Pyhäjoki |  | New investment in TYNDP, required to connect Fennovoimas new 1 250-1 700 MW nuclear power plant that will be built in Pyhäjoki
98 | 98. A66 | Rauma (FI) | Forssa (FI) Lieto (FI) Ulvila (FI) | New single circuit 400 kV OHLs | 1600 | 4 | 5 | [6 empty] | 1 | under consideration | 2020 | New investment in TYNDP, required to connect TVO's new 1 000-1 800 MW nuclear power plant that will be built in Olkiluoto. |  | New investment in TYNDP, required to connect TVO's new 1 000-1 800 MW nuclear power plant that will be built in Olkiluoto
99 | 99. 324 | Dobrzeń (PL) | Wrocław/ Pasikurowice (PL) | New 76 km 400kV 2x1870 MVA OHL double circuit line from Dobrzeń to splitted Pasikurowice - Wrocław line + upgrade and extension of 400 kV switchgear in substation Dobrzeń. | 1800 | 4 | 5 | Warsaw and lower Silesia area | [5 empty] | 1 | design & permitting | 2017 | Progresses globally as planned. Technical description and commissioning date have been updated so as to deliver full benefit as from 2017 |  | Dobrzeń - the project introduces new infrastructure (2x400 kV line) to allow power evacuation from two (2x9000 MW) conventional units to be installed in existing power plant Opole. The new line provides power supply for agglomeration Wroclaw, it increases the SoS for this area.
100 | 100. 335 | Ostrołęka (PL) | Olsztyn Mątki (PL) | New 138km 400kV 2x1870 MVA double circuit OHL line Ostrołęka - Olsztyn Mątki after dismantling of 220kV line Ostrołęka - Olsztyn with one circuit from Ostrołęka to Olsztyn temporarily on 220kV. | 1000 | 4 | 5 | [6 empty] | 1 | design & permitting | 2017 | The time schedule of the project was shifted to meet the schedule of the generation connection. |  | Ostrołęka - the new 400 kV line allows power evacuation from new 1000 MW conventional unit to be installed in existing power plant Ostroleka.
101 | 101. 327 | Kozienice (PL) | Ołtarzew (PL) | New 130km 400kV 2x1870 MVA OHL double circuit line Kozienice - Ołtarzew + upgrade and extension of 400 kV switchgear in substation Kozienice for the connection of new line | 1000 | 4 | 5 | Warsaw area | [5 empty] | 1 | design & permitting | 2017 | The time schedule of the project was shifted to meet the schedule of the generation connection. |  | Kozienice - the new 2x400 kV line allows power evacuation from new 1000 MW conventional unit to be installed in existing power plant Kozienice. The new unit is foreseen to supply Warsaw agglomeration area. The project also allows to close the 400 kV ring around Warsaw agglomeration are increasing the SoS significantly.
101 | 101. 338 | Kozienice (PL) | Mory/ Piaseczno (PL) | Replacement of conductors (high temperature conductors). | [10 empty] | under construction | 2014 | Progresses as planned, with commissioning now expected in 2014 |  | 101
102 | 102. A72 | Gdańsk Błonia (PL) |  | Extension and upgrade of an existing 400/110 kV substation Gdańsk Błonia for connection of planned 900 MW power plant. | 2900 | 4 | 5 | [6 empty] | 2 | planned | 2020 | New investment in TYNDP | Power Evacuation North. The upgraded substation will connect a planned 900 MW CCPP. | North - the North-South corridor provides necessary capacity to evacuate the power from new 2900 MW of conventional generation planned to be installed in northern Poland.
102 | 102. 334 | Pątnów (PL) | Grudziądz (PL) | New 174km 400kV 2x1870 MVA double circuit OHL line Pątnów - Grudziądz after dismantling of 220kV line Pątnów - Jasiniec (two parallel lines) and Jasiniec - Grudziądz. One circuit from Pątnów to Grudziądz via Jasiniec temporarily on 220kV. | [10 empty] | design & permitting | 2020 | The time schedule of the project was shifted to meet the schedule of the generation connection. | Power Evacuation North | 102
102 | 102. 326 | Grudziądz (PL) | Gdańsk Przyjaźń (PL) | A new AC 400/110kV substation between existing substation Grudziądz and planned substation Gdańsk Przyjaźń. New substation Pelplin is connected by new 110km 400kV 2x1870 MVA OHL double circuit lines Grudziądz - Pelplin and Pelplin - Gdańsk Przyjaźń after dismantling of 220kV line Jasiniec - Gdańsk. | [10 empty] | planned | 2020 | The time schedule of the project was shifted to meet the schedule of the generation connection. | Power Evacuation North | 102
103 | 103. 145 | Niederrhein (DE) | Doetinchem (NL) | New 400kV line double circuit DE-NL interconnection line. Length:60km. | 13900 | 3 | 1 | NW part of Netherlands | [5 empty] | 3 | design & permitting | >=2013 | Delays due to authorization process. |  | The project reinforces the Dutch grid to accommodate new conventional and renewable generation, to handle new flow patterns and to increase the interconnection capacity between DE and NL"
103 | 103. 438 | Eemshaven (NL) | Diemen (NL) | New 175-200km AC overhead line with capacity of 2x2650 MVA of 380kV. | [10 empty] | design & permitting | 2018 | Delays due to authorization process. |  | 103
103 | 103. 439 | Borssele (NL) | Geertruidenberg (NL) | New 100-130km double-circuit 380kV OHL with 2x2650 MVA capacity. | [10 empty] | design & permitting | 2016 | Delays due to authorization process. |  | 103
103 | 103. 440 | Maasvlakte (NL) | Beverwijk (NL) | New 380 kV double-circuit mixed project (OHL+ underground cable) including approximately 20km of underground cable for 2650 MVA. The cable sections are a pilot project. The total length of cable at 380kV is frozen until more experience is gained. | [10 empty] | under construction | 2016 | Delays due to authorization process. |  | 103
103 | 103. 441 | Zwolle (NL) | Hengelo (NL) | Upgrade of the capacity of the existing 60km double circuit 380kV OHL to reach a capacity of 2x2650 MVA. | [10 empty] | under consideration | long term | Progresses as planned. |  | 103
103 | 103. 442 | Krimpen aan de Ijssel (NL) | Maasbracht (NL) | Upgrade of the capacity of the existing 150km double circuit 380kV OHL to reach a capacity of 2x2650 MVA. | [10 empty] | under consideration | long term | Progresses as planned. |  | 103
104 | 104. 398B | Under consideration (SE) |  | New series compensation of OHL. | 1200 | 2 | 1 | [6 empty] | 2 | under consideration | 2015 | Reprioritization of projects. | Investment 398 in TYNDP 2010 have been divided into 398A and 398B. 398A is described in project 93. | RES integration in mid-Norway (Trøndelag and Nordland) and reinforcement of Swedish internal interconnections in order to facilitate wind power integration in northern Sweden
104 | 104. 415 | Namsos (NO) | Klæbu and Storeheia (NO) | New line and voltage upgrade of 286km single circuit 400kV OHL | [10 empty] | design & permitting | 2015 | Delays due to authorization process. | New line and voltage upgrade to facilitate new wind power generation | 104
104 | 104. 418 | Nedre Røssåga (NO) | Namsos (NO) | Upgrade of 70km single circuit 400kV OHL | [10 empty] | design & permitting | 2019 | Investment postponed, especially because of long permitting processes. | Increased capacity between north and mid Norway. Facilitates RES integration | 104
104 | 104. 420 | Storheia (NO) | Orkdal / Trollheim (NO) | New 130km single circuit 400kV OHL | [10 empty] | design & permitting | 2017-2020 | Investment postponed due to long permitting procedure. | New line to facilitate wind power generation | 104
104 | 104. A59 | Råbäcken (SE) | Letsi - Betåsen (SE) | New 55km single circuit 400kV OHL | [10 empty] | under consideration | 2017 | New investment in TYNDP. Will probably be postponed after 2020 due to later development of wind power in the area |  | 104
104 | 104. A51 | Svartisen (NO) | Nedre Røssåga (NO) | New 116km 400kV OHL | [10 empty] | planned | 2020 | New investment in TYNDP | New line to facilitate wind power generation | 104
105 | 105. A60 | Skogssäter (SE) | Stenungsund/Stenkullen (SE) | New 80km single circuit 400kV OHL | 600 | 2 | 1 | [6 empty] | 1 | under consideration | 2019 | New investment in TYNDP |  | This project facilitates the connection of wind power along the Swedish west coast
106 | 106. A34 | tbd (IE) | tbd (GB) | A new HVDC subsea connection between Ireland and Great Britain | 700-1000 | 3 | 2 | [6 empty] | 2 | under consideration | long term | New investment in TYNDP, conceptual, cost benefit analysis to be confirmed |  | This project will increase interconnection capacity between Ireland and Great Britain
107 | 107. A25 | tbd (IE) | tbd (FR) | A new HVDC subsea connection between Ireland and France | 700-1000 | 3 | 2 | [6 empty] | 3 | under consideration | long term | New investment in TYNDP, conceptual, cost benefit analysis to be confirmed |  | This project will establish interconnection capacity between Ireland and France
108 | 108. A134 | Tarnita (RO) | Mintia (RO) | New 145km double circuit 400kV OHL | 1000 | 4 | 1 | [6 empty] | 1 | planned | 2018 | New investment in TYNDP | Connection of pumped storage hydro plant Tarnita Lapustesti to the grid. The plant has an installed capacity of 1000 MW and will support system balancing, especially in order to face the intermittent RES output. | The project will connect to the grid 1000MW hydro pump storage.
108 | 108. A135 | Tarnita (RO) | Cluj E - Gadalin (RO) | New 40km double circuit 400kV OHL | [10 empty] | planned | 2018 | New investment in TYNDP |  | 108
108 | 108. A136 | Tarnita (RO) |  | New 400kV substation | [10 empty] | planned | 2018 | New investment in TYNDP |  | 108
109 | 109. A35 | Oriel (IE) | Oriel Wind Farm (IE) | Oriel off-shore wind farm connecting to a new Oriel 220 kV station located on the Louth - Woodland 220 kV circuit | 330 | 4 | 1 | [6 empty] | 2 | under consideration | 2016 | New investment in TYNDP, required to connect Offshore Wind |  | This project will facilitate the connection of offshore wind
109 | 109. A36 | Carrickmines (IE) | Kish Bank Wind Farm (IE) | Kish Bank off-shore wind farm connecting to the existing Carrickmines 220 kV station | 364 | [9 empty] | under consideration | 2015 | New investment in TYNDP, required to connect Offshore Wind |  | 109
109 | 109. A38 | Northern Ireland (NI) | East Coast Offshore (IE) | 'East Coast Off-shore' wind farm connecting to a 275 kV station to be determined. Multiple connection options are under consideration. | 300-600 | [9 empty] | under consideration | 2018 | New investment in TYNDP, required to connect Offshore Wind |  | 109
110 | 110. 424 | Kvilldal (NO) | tbd (GB) | A new 1000MW HVDC bipolar installation connecting Western Norway and Great Britain via 800km subsea cable; DC voltage is to be determined. | 1000-1400 | 1 | 2 | [6 empty] | 3 | design & permitting | 2018/2021 | Capacity revised. Investment postponed, especially because of long permitting processes. |  | Market integration. Facilitate RES integration in southern and western Norway and improve security of supply.
111 | 111. 396 | Finland North (FI) | Sweden North (SE) | Third single circuit 400kV AC OHL between Sweden and Finland. Expected capacity: 1850 MVA. | 700 | 3 | 2 | [6 empty] | 1 | under consideration | 2021 | The projects reinforcing the North-South transmission in the Scandinavia have been prioritized ahead of this project. Based on common estimation project can be delayed to 2021. SvK will evaluate the project and the timetable in ongoing studies |  | Third AC 400 kV cross border line between North-Sweden and North-Finland is under consideration. Strengthening the AC connection between Finland and Sweden is necessary due to new wind power generation, larger conventional units and decommissioning of the existing 220 kV interconnector.
112 | 112. 98 | Pordenone (IT) |  | Voltage upgrade of the existing Pordenone 220kV substation up to 400kV. The substation will be connected in and out to the existing Udine O. – Cordignano 400kV line. | 2150 | 2 | 5 | Triveneto area | [5 empty] | 1 | planned | long term | Progresses as planned |  | This projects helps to increase the security of supply in the N-E part of Italy.
112 | 112. 105 | Treviso (IT) |  | New 380/132kV substation in Treviso area, connected in and out to the existing 380kV line “Sandrigo - Cordignano". | [10 empty] | design & permitting | mid term | Project delayed by 2 years due to longer than expected permitting procedure. |  | 112
112 | 112. 106 | Schio (IT) |  | New 220/132kV substation in Schio area, providing the connection in and out to the existing 220kV line "Ala-Vicenza Monte Viale”. | [10 empty] | planned | mid term | Project delayed by 2 years due to longer than expected permitting procedure. |  | 112
112 | 112. 107 | Vicenza Industrial (IT) |  | New 380/132kV substation in the industrial area of Vicenza, connected in and out to the existing Sandrigo-Dugale 400kV line. | [10 empty] | planned | long term | Progresses as planned |  | 112
112 | 112. 108 | North West Padova (IT) |  | New 220/132kV substation in North West Padova area, complying with 400kV standards, providing the connection in and out to the existing Dugale-Marghera Substation1 220kV line. | [10 empty] | planned | long term | Progresses as planned |  | 112

## CSW report
5 July 2012
TYDNP 2012 package - Table of projects Continental South West Regional Group Investment Plan
Project identification |  |  |  |  | Project assessment
Project number | Investment number | Substation 1 | Substation 2 | Brief technical description | Grid Transfer Capability Increase [MW] | Socio-economic Welfare | RES integration | Improved Security of Supply | Losses variation | CO2 mitigation | Technical resilience | Flexibility | Social and environmental Impact | Project costs | Present status | Expected date of commissioning | Evolution compared to the TYNDP 2010 situation | Investment comment | Project comment
1 | 1. 1 | Frades B (PT) | Pedralva 1&2 (PT) | Creation of a new 400kV station in Frades B connected to Pedralva by means of two new 400kV, 40km lines. The realization of this two connections can take advantage of some already existing 150kV single lines, which will be reconstructed as double circuit lines 400+150kV line and partially sharing towers with those 400kV circuits. | 3800 | 4 | 1 | Tras -so Montes and the Alto Duore area | [5 empty] | 2 | design & permitting | 2014 | Adjustment resulting from the new date of the hydro power plant. |  | This project integrates new amounts of Hydro Power Plants in the Northern region of Portugal (3200 MW of which 2700 MW with pumping) creates better conditions to evacuate Wind Power already existent and new with authorization for connection. These new amounts of power will increase the flows in the region, and it is estimated that the flows could reach 3800 MW, which must be evacuated to the littoral strip and south Portugal through three new independent routes. Part of these flows will interfere and accumulate with the already existent flows entering in Portugal through the international interconnections with Spain on the North, the Alto Lindoso-Riba de Ave-Recarei and Lagoaça-Aldeadávila axis, which induces additional needs for reinforcement of this axis in a coordinated way.
1 | 1. 2 | Pedralva (PT) | Alfena (PT) | New 50km double circuit Pedralva (PT) - Alfena (PT) 400kV OHL, (only one circuit installed in a first step). This line is going to use partially a corridor of a existing single 150 OHL. | [10 empty] | planned | 2017 | Adjustment resulting from the new date of the hydro power plant. |  | 1
1 | 1. 3 | Pedralva (PT) | Vila Fria (PT) | New 55km double circuit Pedralva - Vila Fria 400kV OHL (one circuit installed), with needed extension of existing Vila Fria substation to include 400kV facilities. | [10 empty] | design & permitting | 2014/2015 | Delays due to authorization process. |  | 1
1 | 1. 4 | Frades B - Ribeira de Pena - Feira (PT) |  | New 160km double-circuit 400kV OHL Frades B (PT) -Ribeira de Pena (PT) - Feira (PT) (one circuit operated at 220kV between R. Pena and Feira) with a new 400/60kV substation in Rib. Pena. In a first step, only the 130km section Rib. de Pena (PT) - Feira (PT) will be constructed and operated at 220kV as Vila Pouca Aguiar (PT) - Carrapatelo (PT) - Estarreja (PT) (see project 1.6). In a second step, one circuit of this line will be operated at 400kV. | [10 empty] | design & permitting | 2015/2016 | Progresses as planned |  | 1
1 | 1. 5 | Macedo de Cavaleiros (PT) | Vila Pouca de Aguiar (PT) | New 75km double circuit 400+220kV OHL Macedo de Cavaleiros (PT) -Valpaços (PT) - Vila Pouca de Aguiar (PT). | [10 empty] | partly under construction, design & permitting | 2011/2012 | Delays due to authorization process. A section of the line Macedo de Cavaleiro-Vila Pouca de Aguiar between Macedo de Cavaleiros and Valpaços (53 km) was commissioned at the end of 2011. | This investment allows the connection of RES (mainly wind) and increases the transmission capacity in the Douro area. | 1
1 | 1. 6 | V. P. Aguiar - Carrapatelo - Estarreja (PT) |  | New 400+220kV double circuit OHL (initially only used at 220kV) Vila Pouca Aguiar - (Rib. Pena) - Carrapatelo - Estarreja . Total length of line: 2x(90+49)km. | [10 empty] | design & permitting | 2013 | Delays due to authorization process. | This investment allows the connection of the RES (mainly wind) and new load in the area. | 1
1 | 1. A1 | Ribeira de Pena - Guarda (PT) |  | New 192km double/single-circuit 400kV OHL Ribeira de Pena (PT) - Guarda (PT). In a first step, only the 75 km section Ribeira de Pena - Guarda will be constructed and operated at 220 kV between Vila Pouca de Aguiar and Macedo de Cavaleiros (see project 5), in a second step one circuit of this line will be operated at 400 kV. Between Macedo de Cavaleiros zone and Pocinho zone a single line will be constructed, between Pocinho zone and Chafariz zone a double circuit 400 kV OHL will be constructed (only one circuit installed in a first step), this last line will use one circuit of the line V. Chã B - Guarda (see project 2. A2) to establish the line Ribeira de Pena (PT) - Guarda (PT). | [10 empty] | planned | 2022 | New investment in TYNDP. This investment the supports the integration of new hydro and wind power plant in Northern Portugal |  | 1
2 | 2. 8 | V. Chã B - Arg./Góis - Penela - Paraimo / Batalha (PT) |  | New single circuit 400kV OHL Vila Chã B-Arganil/Gois-Penela (90km) plus new double circuit 400kV OHL (15km) to connect Penela substation to Paraimo - Batalha line. Two new 400/60kV substations at Vila Chã B and Arg./Góis are needed, as well as the expansion of the existing Penela substation to include 400kV facilities. | 1800 | 4 | 1 | [6 empty] | 2 | design & permitting | 2015/2016 | Progresses as planned |  | This project integrates new hydro power plants (590 MW with pumping) and evacuates the existent and new wind generation in the inner central region of Portugal (it is expected to connect more 800 MW of new wind, but the wind target in this region overcomes surmounts of more than 2000 MW). The existing network of 220 kV and 150kV is no more adequate to integrate these new amounts of power, and a new 400kV axis should be launched in this region in a two major routes: one to the littoral strip (Penela/Paraimo/Batalha) and another by the interior, establishing a connection to Falagueira substation, where there is an interconnection with Spain (Falagueira-Cedillo).
2 | 2. 9 | Guarda - Ferro B - (C. Branco) - Falagueira (PT) |  | New double circuit 400+220kV OHL Guarda (PT) -Ferro B (PT) -'Castelo Branco zone' (PT) (between Guarda and Ferro B only the 400kV circuit will be installed) plus new double circuit 400+150kV OHL 'Castelo Branco zone' (PT) -Falagueira (PT). New 400/60kV substations in Guarda and Ferro B. Total length of line: 135km. | [10 empty] | design & permitting | 2015/2016 | Adjustment resulting from the new date of the renewables project. |  | 2
2 | 2. 10 | Falagueira (PT) | Pego (PT) | New 40km double circuit 400+150kV OHL substituting for an existing 150kV line. | [10 empty] | design & permitting | 2014 | Progresses as planned |  | 2
2 | 2. A2 | V. Chã B - Guarda (PT) |  | New double circuit 400kV OHL Vila Chã B-Guarda (55km) | [10 empty] | planned | 2020 | New investment in TYNDP This investment supports the integration of new hydro and wind power plant in Northern Portugal |  | 2
3 | 3. 12 | Rio Maior - Alm. Bispo - Fanhões (PT) |  | New 71km double circuit 400kV OHL feeding Lisbon area from north with creation of a 400/220/60kV substation in Almargem do Bispo. A section of this reinforcement (between Rio Maior and Carvoeira zone) will be finished earlier included on a 400/220kV double circuit line linking Rio Maior and Carregado substations. | 1880 | 2 | 5 | Lisboa and Setúbal Peninsula | [5 empty] | 1 | planned | 2016/2019 | Progresses as planned |  | This project reinforceS the security of supply of Lisbon and Setubal region (north and south Tagus river) by creating a strong semi-ring of 400 kV, with two new 400kV substations that can guarantee the load growth in the region in a safe, secure and quality way. Currently there are only 3 400/VHV substations (Alto de Mira, Fanhões and Palmela), and two of them are quite far from the main load. This new project will create two new 400 kV substations near the main loads.
3 | 3. 13 | Palmela - F. Ferro -Ribatejo (PT) |  | Expansion of Fernão Ferro substation to include 400kV facilities and connection to the existent Palmela (PT) - Ribatejo (PT) single circuit line by a new 25km double-circuit 400kV OHL. | [10 empty] | under construction | 2012 | Progresses as planned Line Palmela-F.Ferro-Ribatejo was commisined at the end of 2011. The expansion of Fernão Ferro substation to include the 400 kV will be concluded only in 2012. |  | 3
3 | 3. 14 | Marateca - Pegões - Fanhões (PT) |  | New 400/60kV substations in Pegoes. New 90km double-circuit 400kV OHL . This new line will be connected to already existing line Palmela (PT) - Sines 2 (PT) , so making a direct link Sines-Pegões (PT) -Fanhões (PT) substations. | [10 empty] | under construction | 2012 | Progresses as planned |  | 3
4 | 4. 16 | Aldeadávila (ES) | Lagoaça (PT) - Armamar (PT) - Recarei (PT) | New Duero Interconnection 400kV New 400kV OHL interconnection line Aldeadávila (ES) - Lagoaça (PT) , including new Lagoaça substation (PT). Also associated, the lines Lagoaça-Armamar-Recarei 400kV in PT and the Armamar (PT) 400/220kV substation. On a first phase (2009) a new 400/220kV substation (Lagoaça - PT) will be created with only 220kV level installed, and there will be some rearrangements and reinforcements on the local 220kV network structure. On river crossing a new 220kV double line with separated circuits, firstly Aldeadavila (ES) - Lagoaça (PT) 1 & 2 and changing later to Aldeadavila (ES) - Pocinho (PT) 1 & 2, will substitute the existing two 220kV lines Aldeadavila (ES) – Bemposta (PT) and Aldeadavila (ES)-Pocinho (PT). Total length: 1km (ES)+105km (PT). | P>E 1700 - E>P 1400 | 3 | 2 | [6 empty] | 2 | partly commissioned, design & permitting | Aldeadavila-Lagoaça 400kV (cros border ), Aldeadavila (ES) - Pocinho (PT) 1 & 2 220 kV, Lagoaça 400/220 kV Substation, Armamar (PT)-Lagoaça (PT) 400 kV commissioned in 2010. Armamar (PT)-Recarei (PT) expected in 2012. | Aldeadavila-Lagoaça 400kV (cross-border), Aldeadavila (ES) - Pocinho (PT) 1 & 2 220 kV, Lagoaça 400/220 kV Substation, Armamar (PT)-Lagoaça (PT) 400 kV completed. Portuguese section Armamar (PT)-Recarei (PT) delayed in autorization process. |  | This project increases the capacity between PT and ES. Larger and more volatile flows are expected between both countries due to the huge increase of volatile sources and the market interchanges. The project includes two interconnection routes, besides the internal reinforcements required, one in the North and other in the South, due to the important loop flows between the two countries and, consequently, only both interconnections allow to reach a reasonable import/export capacities that will reach the "3.2 GW" .
4 | 4. 17 | Guillena (ES)-Puebla de Guzman (ES) | Tavira (PT)-Portimao (PT) | New Southern Interconnection New 400kV OHL double-circuit line between Guillena (ES)-Puebla de Guzman (ES) - Tavira (PT) - Portimão (PT), including new Tavira (PT) and P.Guzman (ES) 400kV substations. On the interconnection section P.Guzmán (ES) –Tavira (PT), initially only one circuit will be placed. Total length: 25km (ES)+110km(PT). | P>E 1700 - E>P 1400 | [9 empty] | partly under construction, design & permitting | 2013 | Portuguese section commissioned.P. Guzman -Guillena (ES) built and operating at 220kV. Difficulties in the authorization process in the Spanish section P. Guzman - border and connection to Guillena 400 Kv. |  | 4
4 | 4. 18 | Boboras (ES)-O Covelo (ES) | Vila Fría (PT)- Vila Conde (PT) - Recarei (PT) | New northern interconnection. New double circuit 400kV OHL between O Boboras (ES) -O Covelo (ES) - Vila Fria (PT) - Vila do Conde (PT) - Recarei (PT), including new 400kV substations O Covelo (ES), Boboras (ES), Vila Fria (PT) and Vila do Conde (PT). On the section O Covelo (ES) – Vila do Conde (PT), only one circuit will be placed. Total length: 50km (ES)+112km (PT). | P>E 1700 - E>P 1400 | [9 empty] | design & permitting | 2014 | Progresses as planned. Changes in route and connecting point in Spain due to environmental constraints |  | 4
4 | 4. 21 | Aldeadavila (ES) JM Oriol (ES) | Villarino (ES) Caceres (ES) | Uprating the existing Aldeadávila-Villarino 400kV OHL in order to increase its capacity from 1350MVA to 1690MVA. Uprating the existing line JM Oriol-Caceres 220 kV | [10 empty] | under construction | 2013 | Progress ans planned, although there are difficulties to find a suitable period for a planned outage to carry on the project. |  | 4
4 | 4. 21 | JM Oriol (ES) | Arenales -Caceres (ES) | New 220kV JM Oriol-Arenales, and new Arenales substation. | P>E 1700 - E>P 1400 | [9 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 4
5 | 5. 19 | Vic (ES) | Pierola (ES) | Upgrading (uprating) the existing 75km single circuit Vic-Pierola 400kV line in order to increase its capacity from 1360 MVA to 1710 MVA. | 1200-1400 in both directions | 1 | 2 | Perpignan, Gerona | [5 empty] | 2 | under construction | 2012 | Delays due to authorization process. |  | Mid-term interconnection project between France and Spain ("2.8 GW") . It includes cross border lines and internal lines required to assure NTC.
5 | 5. 20 | Arkale (ES) | Hernani (ES) | Upgrading the existing single circuit Arkale-Hernani n°2 220kV OHL in order to increase its capacity up to 640 MVA. | [10 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 5
5 | 5. 36 | Sta.Llogaia (ES) | Baixas (FR) | New HVDC (VSC) bipolar interconnection in the Eastern part of the border, via 320kV DC underground cable using existing infrastructures corridors and converters in both ending points. | [10 empty] | partly under construction, design & permitting | 2014 | Progresses as planned. |  | 5
5 | 5. 37 | Santa Llogaia (ES) | Bescanó (ES) | New double circuit Sta.Llogaia-Ramis-Bescano-Vic/ Senmenat 400kV OHL (single circuit in some sections) New 400kV substations in Bescano, Ramis and Sta.Llogaia, with 400/220kV transformers in Ramis and Bescano. | [10 empty] | under construction | 2011-2013 | Bescano-Vic/Senmenat 400 KV commissioned. Difficulties in the authorization process of the section Bescano-Sta Llogaia 400kV |  | 5
5 | 5. 46 | Baixas (FR) | Gaudière (FR) | Reconductoring of existing 70km double circuit 400kV OHL to increase its capacity. | [10 empty] | design & permitting | end 2013 | Progresses as planned |  | 5
6 | 6. 22 | Boimente (ES) | Grado (ES) | North axis Project between Galicia and the Basque Country. Part of the project is considered as the Asturias Ring. New double circuit Boimente-Pesoz-El Palo-Salas Grado 400kV OHL. Change of voltage level of the existing Soto-Tabiella single circuit from 220kV to 400kV, and connection as input/output in Grado. New single circuit Soto-Penagos 400kV OHL. New double circuit Aguayo/Penagos-Udalla-Abanto 400kV OHL New double circuit Zierbena-Abanto-Gueñes 400kV OHL. New double circuit Gueñes-Ichaso OHL. New double circuit Gozón-Reboria--Sama-Lada 400kV OHL. New double circuit Sama-Velilla 400kV OHL. Uprating the single circuit Lada-Robla 400kV OHL in order to increase its capacity by around 300 MVA. It includes new 400kV substations Pesoz, El Palo,Salas, Grado, Gozón, Sama, Reboria , Costa Verde, Penagos, Solorzano, Udalla, Abanto and several transformers to 220kV. | 2000- 4200 | 5 | 2 | [6 empty] | 2 | partly commissioned, design & permitting | 2012-2014 | Section Pesoz-Salas commissioned. El Palo connection is in progress. Difficulties in the authorization process of the section Boimente-Pesoz and Salas-Grado |  | Larger and more volatile West East power flows from Galicia to the Basque Country, triggered especially by the development of new generation sources in the North and North Western part of the country (mainly wind, a new pumping hydro power plant, and some CCGT that will replace former coal power plants) and the need to feed the high industrial and demanding regions of the North and Northeastern part of Spain.
6 | 6. 22 | Soto -Grado- Gozon-Reboria (ES) | Costaverde-Sama (ES) | [11 empty] | design & permitting | 2015 | Changes in the definition of the investment: Subestation Valle del Nalón 400kV is not required as the link can not take advantage of existing 132kV due to technical and environmental problems, connection Gozón-Carrio 400kV can not use existing corridor of lower voltage lines and requires therefore a new substation Reboria 400kV. |  | 6
6 | 6. 22 | Soto (ES) | Penagos (ES) | [11 empty] | commissioned | commissioned | Commissioned |  | 6
6 | 6. 22 | Sama (ES) | Velilla (ES) | [11 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 6
6 | 6. 22 | Lada (ES) | Robla (ES | [11 empty] | commissioned | commissioned | Commissioned |  | 6
6 | 6. 22 | Penagos/Aguayo (ES) | Abanto (ES) | [11 empty] | partly commissioned, design & permitting | 2012 | From Penagos/Aguayo to udalla commissioned. The connection from udalla to Abanto has delays in authorization process |  | 6
6 | 6. 22 | Zierbena (ES) | Abanto (ES) | [11 empty] | commissioned | commissioned | Commissioned |  | 6
6 | 6. 22 | Abanto/Gueñes (ES) | Ichaso (ES) | [11 empty] | design & permitting | 2016 | Delays due to authorization process. |  | 6
7 | 7. 23 | Ichaso (ES) | Castejón (ES) | Northern part of the new Cantabric-Mediterranean axis. New double circuit Castejón-Muruarte-Dicastillo-Ichaso 400kV OHL, with new 400kV substations in Muruarte and Dicastillo with 400/220kV transformers. Section Castejón-Muruarte 400kV already in service | 1320--4280 | 1 | 1 | [6 empty] | 2 | partly commissioned, design & permitting | 2017 | Castejón-Muruarte section have been commissioned. Muruarte-Dicastillo-Ichaso has difficulties in the authorization process which led to change the route and connection (Ichaso substitutes Vitoria) |  | Larger and more volatile Cantabric-Mediterranean power flows in Spain, triggered by the development of local RES but also influenced by transits flows caused by the generation/demand situations in the North and Levante areas.
7 | 7. 23 | La Serna (ES) | Magallón (ES) | New double circuit La Serna-Magallón 400kV OHL. | [10 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 7
7 | 7. A4 | Tudela (ES) | Magallón (ES) | New CCRS (Combination of Reactors step by step) in Magalló 220 kV | [10 empty] | design & permitting | 2013 | New investment in the TYNDP, as it is required to ensure the GTC increase for the entire project |  | 7
7 | 7. A5 | Dicastillo (ES) | Moncayo (ES) | New double circuit Dicastillo-El Sequero-Santa Engracia-Magaña-Moncayo 220kV OHL. | [10 empty] | design & permitting | 2013-2017 | New investment in the TYNDP. Ensures the GTC increase of the project while helping to evacuate the generation in Soria and Aragón. |  | 7
7 | 7. 23 | Aragón (ES) Tudela (ES) La Serna (ES) | Peñaflor (ES) Magallón (ES) Ichaso (ES) | Uprating the existing Aragón-Peñaflor 400kV OHL , Tudela-Magallón 220kV and La Serna-Ichaso 220 kV. | [10 empty] | design & permitting | 2013-2014 | New investment in the TYNDP. Difficulties in the authorization process |  | 7
7 | 7. 24 | Fuendetodos /Mudejar (ES) | Eliana/ Godelleta(ES) | Southern part of the new Cantabric-Mediterranean axis. New double circuit Fuendetodos-Muniesa-Mezquita-Platea-Godelleta 400kV OHL. New double circuit Teruel-Mudejar-Morella-la Plana/Godelleta 400kV-OHL. the new TGodelleta substation will be equipped with a 400/220kV transformer and connected to the existing 400kV lines Cofrentes-La Eliana, and Catadau-Requena 400kV lines. New 400kV substations Mezquita, Platea, Muniesa, Mudejar and Godelleta with 400/220kV transformer units | [10 empty] | design & permitting | 2012-2015 | Turis substation is substituted by Godelleta due to environmental reasons. Uprate Eliana-La Plana and new circuit is rejected due to environmental reason. As alternative a double circuit connection morella-Godelleta/La plan. These issues delay the project up to 2015 |  | 7
8 | 8. 25 | Aragón (ES) | Isona (ES) | New double circuit Aragón/Peñalba-Arnero-Isona 400kV OHL with new 400kV substations Arnero and Isona, and a 400/220kV transformer in Arnero. | 3870 | 1 | 3 | [6 empty] | 1 | design & permitting | 2014 | Delays due to authorization process.. In addition, Monzón substation is substituted by Arnero |  | Larger and more volatile South- NorthEastern power flows from Aragón to Catalunya, triggered especially by the development of new RES in the south of Catalunya and Aragón, that joined to the existing generation sources (RES and conventional) in this area and further in the south causes higher flows, that would naturally flow to the large consumption areas in Catalunya.
8 | 8. 25 | Escatron (ES) | La Secuita (ES) | New single circuit Escatrón-Els Aubals-La Secuita 400kV OHL with new 400kV substation in Els Aubals and La Secuita with 400/220kV transformer. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 8
8 | 8. A6 | Torres del Segre(ES) | Mequinenza (ES) | New SSSC (Static Synchronous Series Compensator) in Torres del Segre-Mequinenza 220kV. | [10 empty] | design & permitting | 2013 | New investment in the TYNDP. Ensures the GTC increase of the project while alleviating present and the future congestion in the parallel 220kV axis |  | 8
8 | 8. A7 | Mangraners (ES) | Begues (ES) | New Double circuit Mangraners-Espluga-Begues and Mangraners-Juneda-Secuita-Perafort-Begues 220 kV | [10 empty] | design & permitting | 2013 | New investment in the TYNDP. Ensures the GTC increase of the project while alleviating present and the future congestion in the parallel 220kV axis |  | 8
8 | 8. A8 | Espluga (ES) | Penedes (ES) | Uprate 116km single circuit 220kV OHL | [10 empty] | design & permitting | 2011-2013 | New investment in the TYNDP. Ensures the GTC increase of the project while alleviating present and the future congestion in the parallel 220kV axis |  | 8
8 | 8. A9 | Garraf (ES) | Vandellos (ES) | Uprate 108km single circuit 400kV OHL | [10 empty] | design & permitting | 2015 | New investment in the TYNDP. Ensures the GTC increase of the project while alleviating present and the future congestion in the parallel 220kV axis |  | 8
8 | 8. A10 | Isona (ES) | Calders (ES) | uprate 79km single circuit 400kV OHL | [10 empty] | design & permitting | 2015 | New investment in the TYNDP. Ensures the GTC increase of the project while alleviating present and the future congestion in the parallel 220kV axis |  | 8
9 | 9. 26 | Catadau (ES) | Benajama (ES) | New double-circuit Catadau-Jijona-Benejama 400kV OHL .A new 400kV substation will be created at Jijona and transformers installed in Jijona and Catadau. | 1840 | 2 | 5 | Costablanca area | [5 empty] | 1 | design & permitting | 2017 | Delays due to authorization process. |  | Security of supply of the Costablanca area in Levante Mediterranean coast
9 | 9. 26 | Catadau (ES) | Jijona (ES) | 220 kV lines from Catadau to Jijona in the coast of Costablanca using partially the 132KV lines | [10 empty] | design & permitting | 2016-2019 | New investment in the TYNDP complementing the previous one to alleviate congestion in the 132kV lines that supplies Casabanca area. 132 kV lines will be upgraded to 220KV. |  | 9
10 | 10. 28 | Cofrentes (ES) | Ayora (ES) | New single circuit Cofrentes-Ayora 400kV OHL. | 3380-4270 | 4 | 1 | [6 empty] | 1 | design & permitting | 2015 | Delays due to authorization process. forcing to reschedule the investment |  | Larger and more volatile East-West flows triggered mainly due to new RES generation development in Valencia, Albacete and Ciudad Real .
10 | 10. 28 | Ayora (ES) | Pinilla (ES) | New single circuit Cofrentes-Ayora-Campanario-Pinilla 400kV OHL. This project also includes a new 400kV substation in Campanario. | [10 empty] | design & permitting | 2012-2013 | Progresses globally as planned |  | 10
10 | 10. 33 | Romica (ES) | Manzanares (ES) | Transmanchega project New double circuit line Romica-Manzanares 400kV OHL. New substation Manzanares with a 400/220kV transformer unit. | [10 empty] | design & permitting | 2016 | Postponed in new national Master Plan as need is not imminent |  | 10
10 | 10. 33 | Manzanares (ES) | Brazatortas (ES) | Transmanchega project New double circuit line Manzanares-Brazatortas 400kV OHL. The new 400kV substation Brazatortas will be connected to the existing line Guadame-Valdecaballeros. | [10 empty] | design & permitting | 2013 | Progresses as planned |  | 10
11 | 11. 29 | Cartuja (ES) | Guadame (ES) | New double circuit Cartuja-Arcos de la Frontera-La Roda-Cabra-Cordoba-Guadame 400kV OHL (partly already commissioned) . It includes new 400kV substations Cartuja and Cordoba, with 400/220kV transformers. | 1270 | 4 | 1 | [6 empty] | 1 | partly commissioned, design & permitting | 2011/2014 | Arcos-Cabra-Guadame section commissioned. Cordoba connection postponed in new National Master Plan as need for demand is not imminent. Cartuja-Arcos faces difficulties in the authorization process. |  | Larger and more volatile South-North power flows, triggered especially by the development of new RES in Cadiz, that joined to the existing generation sources (RES and conventional) in the area causes higher flows, that would naturally flow to the large consumption areas in the North.
11 | 11. A11 | Cartuja-Pto Sta Maria (ES) | Facinas (ES) | New 52km single circuit 220 kV OHL Puerto Sta Maria-Pto.Real-Parralejo-Facinas | [10 empty] | design & permitting | 2012/2013 | New investment in the TYNDP, contributing also to evacuate the generation in the coast of Cadiz |  | 15
12 | 12. 30 | Don Rodrigo (ES) | Aznalcollar (ES) | New double circuit 400kV OHL: Aznalcollar-Guadaira-Don Rodrigo. Aznalcollar substation will also have a new input/output in Guillena-Palos 400kV. This project also includes new 400kV substations in Aznalcollar and Guadaira with 400/220kV transformers. | 2150-1600 | 3 | 4 | [6 empty] | 2 | design & permitting | 2017 | Delays due to authorization process. which led that Guillena-Guadaira connection is substituted by Aznalcollar-Guadaira with a new topology. |  | Larger and more volatile Southwestern-Northwestern power flows, triggered especially by the development of new generation sources in Sevilla and Huelva (mainly wind and solar), but also in Extremadura, that joined to the existing generation sources in the area causes higher flows, that would naturally flow to the large consumption areas in the South (Sevilla) or in the North (towards Madrid), depending on the demand/generation situation.
12 | 12. 30 | Guillena (ES) | Almaraz (ES) | New double circuit 400kV OHL Guillena-Brovales-Arroyo S.Servan-Carmonita- Almaraz. This project also includes new 400kV substations in Arroyo S.Servan, Carmonita with 400/220kV transformers. | [10 empty] | design & permitting | 2012 | Alcuescar substation substituted by Carmonita. Progresses as planned otherwise |  | 12
13 | 13. 31 | Caparacena (ES) | La Ribina (ES) | New double circuit Caparacena-Baza-La Ribina 400kV OHL, with two new 400kV substations in Baza and La Ribina (these substations will be also connected to Carril-Litoral 400kV line ). | 1950-3400 | 4 | 1 | [6 empty] | 1 | design & permitting | 2016 | Delays due to authorization process. |  | The project aims at ensuring the connection to the transmission network of new RES (wind, solar and pumping hydro) and ensuring the possibility of more volatile power flows between the Almeria and Granada.
13 | 13. 31 | Caparacena (ES) | Litoral (ES) | The existing single circuit Litoral-Tabernas-Hueneja-Caparacena 400kV line will be uprated in order to increase its capacity . | [10 empty] | under construction | 2012 | Final phase of permitting.. Progress as planned although there are difficulties to find a suitable period for a planned outages to carry out the work |  | 13
14 | 14. 34 | Trives (ES) | Tordesillas (ES) | New line Trives-Aparecida-Arbillera-Tordesillas 400kV OHL and Trives-Conso-Valparaiso-Tordesillas 220kV OHL. New 400kV substations in Aparecida, | 600+3000 | 1 | 2 | [6 empty] | 2 | under construction | 2011-2012 | Progress as planned. Trives-Tordesillas 400kV axis shares towers with the Trives-Tordesilla 220kV line. Final phase of permitting. |  | Larger and more volatile Northwestern- Centre power flows , triggered especially by the development of new RES in Galicia and Castilla-León, that joined to the existing generation sources (RES and conventional) in the area and further in the north causes higher flows, that would naturally flow to the large consumption areas in the center of Spain, mainly Madrid.
14 | 14. 34 | Tordesillas (ES) | La Cereal /Moraleja (ES) | New double circuit Tordesillas-Segovia- Galapagar 400kV OHL. | [10 empty] | under construction | 2012-2013 | Partly commissioned. Progresses as planned |  | 14
14 | 14. 34 | Segovia (ES)-PST Galapagar | Moraleja (ES) | New input/output of Moraleja in Segovia-Galapagar 400kV OHL and new PST in the 400kV line Galapagar-Moraleja. | [10 empty] | design & permitting | 2013-2015 | Delays due to authorization process. |  | 14
14 | 14. 34 | Loeches (ES) | SSReyes (ES) | Upgrade of the existing 21km single circuit Loeches-SS Reyes 220kV OHL to 400kV in order to increase its capacity. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 14
14 | 14. 34 | Fuencarral (ES) | Galapagar (ES) | Uprate Galapagar-Fuencarral 400kV. | [10 empty] | design & permitting | 2014 | New investment in TYNDP |  | 14
14 | 14. 34 | Mudarra (ES) | Tordesillas (ES) | New double circuit 400kV Mudarra-Tordesillas OHL and upgrade of the existing single-circuit Mudarra-Tordesillas 400kV line in order to increase its capacity. | [10 empty] | partly under construction, design & permitting | 2018 | Uprate fostered because of necessity. New line postponed in new Master Plan. |  | 14
15 | 15. A12 | Olmedilla (ES) | Valdemingomez (ES) | New double circuit Olmedilla-Villares-Morata-Valdemingomez 400kV OHL, and New substation Villares and Valdemingomez 400kV, with 400/220 kV transformers in T.Velasco | 8700 | 5 | 1 | [6 empty] | 1 | design & permitting | 2016/2017 | New investment in TYNDP |  | Larger and more volatile South- Centre power flows , triggered especially by the development of new RES in Cuenca, that would naturally flow to the large consumption area of Madrid but also influenced by transits flows caused by higher flows coming from the south of Spain.
15 | 15. 32 | (Castilla) (ES) | (Madrid) (ES) | Uprate Cofrentes-Minglanilla-Belinchon-Morata 400kV,double circuit Trillo-Villanueva Escuderos-Olmedilla-Belinchon 400kV, double circuit Valdecaballeros-Arañuelo 400 kV, double circuit Morata-Villamiel-Almaraz 400 kV, double circuit Villaviciosa- Almaraz 400 kV, double circuit Aldeadavila-Arañuelo and Aldeadavila- Hinojosa-Almaraz 400kV, Picon-Aceca-Los Pradillos-Torrejon de Velasco and Añover-Torrejón de Velasco-Pinto Ayuden-El Hornillo-Villaverde 220 kV | [10 empty] | partly under construction, design & permitting | 2011/2018 | Some of the investments progressed as planned. Other have problems either in permitting process or finding a suitable period for a planned outage to carry out the works. |  | 15
16 | 16. 38 | Gatica (ES) | Aquitaine (FR) | New HVDC interconnection in the western part of the border via DC subsea cable in the Biscay Gulf. | Fr->Es 1200 ; Es ->Fr 2000 | 1 | 2 | Biarritz, Basque country | [5 empty] | 3 | under consideration | ca. 2020 | New investment in TYNDP, defined since last release, aiming 4 GW capacity between France and Spain. |  | Long-term interconnection project between France and Spain ("4 GW") . It includes cross border lines and internal lines required to assure NTC.
16 | 16. A14 | Amorebieta (ES) Garraf (ES) Adrall (ES) Orcoyen (ES) | Gueñes (ES) Secuita (ES) La Pobla (ES) Elgea (ES) | Uprates required in basque country and Catalonia in order to use fully the benefit of the longterm ES-FR interconnection. | [10 empty] | under consideration | 2016 | New investment in TYNDP meant to solve congestion in this area. |  | 16
16 | 16. A17 | Arkale (ES) |  | New PST on Arkale-Argia 220 kV interconnection line | [10 empty] | design & permitting | 2016 | New investment enabling to take full advantage of the transfer capacity of the new subsea interconnection. |  | 16
17 | 17. 42 | Lonny (FR) | Vesle (FR) | Reconstruction of the existing 70km single circuit 400kV OHL as double circuit OHL. | 9000 | 1 | 2 | Reims, Paris area | [5 empty] | 3 | design & permitting | 2016 | Progresses as planned |  | Project needed to cope with larger and more volatile North South power flows from Normandy to Champagne, triggered especially by the development of new generation sources (along the Channel coasts, from Picardie to Champagne and further North abroad) that would naturally flow to large consumption areas: Paris area, but also more broadly from Brittany to Reims.
17 | 17. 44 | Havre (FR) | Rougemontier (FR) | Reconductoring of existing 54km double circuit 400kV OHL to increase its capacity. | [10 empty] | under construction | 2018 | As the pace of generation installation is lower than expected, the investment has been postponed. | This investment is needed for integrating new generation in Le Havre area. As the pace of generation installation is lower than assumed earlier, the investment has been postponed from 2015 to 2018 | 17
17 | 17. A18 | tbd (FR) | tbd (FR) | New network reinforcement between Haute Normandy and the south of Paris area. Length about 160 km. | [10 empty] | under consideration | long term | New investment in TYNDP, defined since last release | Either existing assets uprate or new HVDC, actual needs still being evaluated, depending on uncertainties on generation location | 17
17 | 17. 45 | Taute (FR) | Oudon (FR) | "Cotentin-Maine "Project : new 163km double circuit 400kV OHL connected to existing network via two new substations in Cotentin and Maine regions. | [10 empty] | under construction | 2013 | Delays due to authorization process. |  | 17
17 | 17. A144 | Cergy (FR) | Terrier (FR) | MORP project : new single circuit 400-kV line between existing 400-kV substations | [10 empty] | planned | 2018 | New investment in TYNDP, defined since last release, triggered by larger and more volatile power flows between generation developing North of Paris and Paris area. |  | 17
18 | 18. 48 | Gaudière (FR) | Rueyres (FR) | Reconductoring with ACCS limiting section (10km) of existing single circuit 400kV OHL. | >1000 | 3 | 5 | Provence area | [5 empty] | 3 | under construction | end 2012 | Progresses as planned |  | Larger and more volatile North South power flows in South-Western France, triggered by the development of local RES generation but also influenced by transits flows with neighboring countries.
18 | 18. A19 | tbd (FR) | tbd (FR) | Restructuration of whole EHV grid in Massif Central area | [10 empty] | under consideration | long term | New investment in TYNDP, defined since last release, triggered by larger and more volatile power flows in South West France. |  | 18
18 | 18. 20. A20 | (Provence) (FR) | (Midi) (FR) | New subsea HVDC link between Marseille area and Languedoc | [10 empty] | design & permitting | 2018 | New investment in TYNDP, defined since last release, triggered by larger and more volatile power flows in South West France. |  | 18
19 | 19. 51 | Boutre (FR) | La Bocca (FR) | PACA "Filet de sécurité" project: construction of 3 new AC 220kV underground cables (Boutre - Trans [65 km], Biançon - Fréjus [26 km] & Biançon - La Bocca [17 km]) and installation of reactive power compensation devices in 220 kV Boutre and Trans substations | 500 | 2 | 5 | French riviera | [5 empty] | 1 | design & permitting | 2015 | Progresses as planned |  | Security of supply of the French riviera
20 | 20. 53 | Coulange (FR) | Le Chaffard (FR) | Reconductoring (with ACCS / ACCR) of two existing double circuit 400kV OHL (Coulange - Pivoz-Cordier - Le Chaffard and Coulange - Beaumont-Monteux - Le Chaffard). Total length of both lines: 275km | 2400 | 1 | 5 | South East France | [5 empty] | 2 | under construction | 2016 | Progresses as planned | Construction over 4 years because the works are only possible during limited periods every years on this strategic corridor | The project aims at ensuring the reliable grid operation to cope with new generation development along the Rhone Valley and more volatile power flows between the Alps and South Western France.
20 | 20. 18, A20 | [15 empty] | 0 | The investment contributes both to project 18 and project 20. For the technical description see project 18 | 20
21 | 21. 54 | Cornier (FR) | Piossasco (IT) | Replacement of conductors (by ACCS) on Albertville (FR) - Montagny (FR) - Cornier (FR) and Albertville (FR) - La Coche (FR) - La Praz (FR) - Villarodin (FR) - Venaus (IT) - Piossasco (IT) single circuit 400kV OHLs. In addition, change of conductors and operation at 400kV of an existing single circuit OHL between Grande Ile and Albertville (FR) currently operated at lower voltage, and associated works in Albertville (FR) 400kV substation. (Total length of lines : 257 km) | 1800 from FR to IT, (600 in the MT) | 1 | 5 | [6 empty] | 3 | under construction | 2012/2013 | Mainly progresses as planned although the works on existing lines take slightly longer than initially thought |  | Planned France-Italy interconnection development
21 | 21. 55 | Grande Ile (FR) | Piossasco (IT) | "Savoie - Piémont" Project : New 190km HVDC (VSC) interconnection FR-IT via underground cable and converter stations at both ends (two poles, each of them with 600MW capacity). The cables will be laid in the security gallery of the Frejus motorway tunnel and possibly also along the existing motorways' right-of-way. | [10 empty] | design & permitting | 2017/2018 | Progresses as planned |  | 21
21 | 21. 81 | Trino (IT) | Lacchiarella (IT) | A new 380kV double circuit OHL between the existing 380kV substations of Trino and Lacchiarella in North West Italy area. Total line length: 95km, Voltage upgrade of the existing Magenta 220/132kV substation up to 380kV. | [10 empty] | under construction | 2013 | Authorization process ended, construction phase on going |  | 21
21 | 21. 84 | Casanova (IT) | Vignole (IT) | Voltage upgrade of the existing 100km Casanova-Vignole 220kV OHL to 400kV and new 400/220/150kV substation in Asti area. | [10 empty] | design & permitting | long term | Delays due to authorization process. |  | 21
21 | 21. 101 | Turin (IT) |  | Restructuring of the 220kV network in the urban area of Turin. Some new 220kV cables, some new 220/132kV substations and some reinforcements of existing assets are planned. Total length: 63km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 21
22 | 22. 57 | under consideration (FR) | under consideration (CH) | Reinforcement of the interconnection in the area of Geneva's lake. | < 1000 from FR to CH and < 1500 from CH to FR | 3 | 2 | [6 empty] | 1 | under consideration | long term | Progresses as planned. Several technical options (route, technologies) have been designed and are being investigated. | The very uncertain environment, regarding commissioning and decommissioning of generation in particular makes the assessment complex. | France-Switzerland interconnection development under consideration.
23 | 23. 60 | under consideration (FR) | under consideration (BE) | To be determined. | 1800-3000 | 3 | 2 | Lille, Ruien area | [5 empty] | 2 | under consideration | 2018-2020 | Project entered a feasibility study phase. Expected date of commissioning is now 2018. |  | France-Belgium interconnection development: internal French grid reinforcements, that are prerequisite to maintain the present NTC and further interconnection development under consideration. This project enhances security of supply in Belgium and allows intra and inter countries RES integration.
23 | 23. A21 | Avelin (FR) | Mastaing (FR) | Operation at 400 kV of existing line currently operated at 220 kV | [10 empty] | design & permitting | 2017 | New investment in the TYNDP | Upgrade of all grid assets in Northern France at the same standard | 23
23 | 23. A22 | Avelin (FR) | Gavrelle (FR) | Substitution of a new double-circuit 400kV OHL to an existing 400-kV single circuit OHL | [10 empty] | design & permitting | 2017 | New investment in the TYNDP |  | 23
25 | 25. 62 | Under Consideration (FR) | Under Consideration (GB) | IFA2:New subsea HVDC link between the UK and France. Capacity is still to be determined. (Possibly 1000MW) | 1000 | 1 | 5 | [6 empty] | 2 | under consideration | 2020 | Further investigations during the feasibility phase have led to reassess the expected commissioning date for "IFA2" |  | France-UK interconnection development under consideration
40 | 40. 446 | Bascharage (LU) | Aubange (BE) | As a first step(2016) a PST could be placed in the existing 225kV line between LU and BE. In a second stage, two solutions are currently investigated (4 TSOs - Elia, Amprion, CREOS, RTE are involved). Solutions 1 would be a new interconnection between Creos grid in LU and ELIA grid in BE via a 16km double circuit 225kV underground cable with a capacity of 1000 MVA. Solution 2 would be the interconnection between CREOS grid in LU and ELIA grid in BE via a new 380 kV double circuit. The current study will investigate the impact of this new interconnection on other boundaries (impact of loop flow) and on internal grids . The potential reinforcements of the other boundaries and the internal grids will also be taken into account in the evaluation. | 380-900 | 2 | 5 | Luxemburg area | [5 empty] | 2 | under consideration | 2016/2020 | The commissioning date and status changed as the study to determine the best investment is still ongoing. |  | Increase the transfer capability between LU,DE, BE and FR.
40 | 40. A29 | Bascharage (LU) | tbd (BE, DE, &/o FR) | New interconnection with neighbor(s) either 220kV or 400kV | [10 empty] | under consideration | 2020 | New investment in TYNDP | An ongoing network study (4 TSOs involved) investigates the robustness of the planned 220kV connection between LU and BE and the potentially need for an upgrading to a 400kV interconnector in the South. | 40
40 | 40. 447 | Heisdorf (LU) | Berchem (LU) | New 20km double-circuit mixed (underground cable+OHL) 225kV project with 1000 MVA capacity including substations for in feed in lower voltage levels. | [10 empty] | design & permitting | 2012/2017 | Progresses as planned |  | 40
40 | 40. A30 | Bascharage (LU) | Niederstedem (DE) or tbd (DE) | Upgrading and new construction of an interconnector to DE, in conjunction with the interconnector in the south of LU; Partial upgrading of existing 220kV lines and partial new construction of lines; With power transformer station in LU | [10 empty] | under consideration | 2020 | New investment in TYNDP |  | 40
85 | 85. A3 | F. Alentejo - Ourique - Tavira (PT) |  | New 122km double-circuit 400+150 kV OHL F. Alentejo-Ourique-Tavira. The realization of this connection can take advantage of some already existing 150kV single lines, which can be reconstructed as double circuit line 400+150kV, with needed extension of existing Ourique substation to include 400 kV facilities. | 1390 | 4 | 1 | [6 empty] | 1 | planned | 2018/2019 | New investment in TYNDP This project helps integrate new solar and wind power plans in Alentejo and Algarve area |  | This project integrates new amounts of solar (and also some wind) generation in the south of Portugal. The existing network of 150 kV is not sufficient to integrate these amounts of power and a new 400 kV axis should be launched in this region, establishing a connection between the two Southern interconnections between Portugal and Spain, the Ferreira do Alentejo-Alqueva-Brovales and Tavira-Puebla de Gusman. This axis will also close a ring of 400 kV in the Southern part of Portugal that will guarantee the load growth in the region (Algarve is one of the regions that presents the biggest growth rate in Portugal) in a safe, secure and quality way.
88 | 88. A23 | offshore wind farms (FR) | several French substations (FR) | Subsea cables and substations works | 3000(MT) 6000 (LT) | 4 | 1 | [6 empty] | 3 | planned | 2015-2020 | New investment in TYNDP, required to connect offshore wind farms as decided by the French government in 2010 | Project development will adapt to the pace of generation installation | Connection of 6 GW offshore wind farms in 2 phases. First 3 GW phase in progress (tender).
89 | 89. A24 | Calan (FR) | Plaine-Haute (FR) | New 80km double circuit 220kV underground cable with 2 phase shifters and T-connection of an existing HV substation; 1150 MVARs of capacitors and SVC; new transformer 400/220kV | 500 MW | 2 | 4 | Brittany area | [5 empty] | 1 | design & permitting | 2017 | New investment in TYNDP, required to secure Brittany's supply, along with DSM management plan and a new CCGT in Finistère area. |  | This project is necessary to security Brittany's supply.
107 | 107. A25 | tbd (IE) | tbd (FR) | A new HVDC subsea connection between Ireland and France | 700-1000 | 3 | 2 | [6 empty] | 3 | under consideration | long term | New investment in TYNDP, conceptual, cost benefit analysis to be confirmed |  | This project will establish interconnection capacity between Ireland and France
| 15 | Falagueira-Estremoz - Divor - Pegões (PT) |  | New 400/60kV substations in Pegoes and Divor connected by a new 116km Pegoes (PT) - Divor (PT) - Estremoz (PT) single circuit 400kV OHL. In addition, the operating voltage of the existing Estermoz substations and the 93km single circuit Falagueira (PT) -Estremoz (PT) 150kV OHL will be changed to 400kV (were prepared for that). | [10 empty] | cancelled | cancelled | The construction of the project is linked with the construction of the High Speed Train infrastructure which has been suspended. Therefore the project was also suspended.
| 27 | Morvedre (ES) | Santa Ponsa (ES) | Connection of Balearic Islands to Mainland New bipolar 2x200MW HVDC (LCC) 250km connection between Morvedre (mainland) and Santa Ponsa (Mallorca) via 250kV. subsea cable. In addition, Mallorca will be connected to Menorca with a new HVDC 120km link between Santa Ponsa (Mallorca) and Torrente (Menorca). A second connection between Mallorca and Ibiza (60km) will also be constructed. | [10 empty] | design & permitting | 2013-2015 | The cable Morvedre-Sta Ponsa was commissioned according to the plan. The remaining investments are in delay due to authorization process.
| 35 | tbd (ES) | tbd (ES) | Reinforcements in the 220kV network overall the country, in addition to upgrading of 300km of 220kV network , due to wind power evacuation. | [10 empty] | design & permitting | 2011-2018 | Project as planned.
| 40 | Avelin (FR) Mastaing (FR) |  | Installation of a 3rd busbar in Avelin (existing 400-kV substation) & replacement of components to increase the ability to withstand short-circuit power; Connection of Mastaing (existing 400kV substation) to existing 400kV circuit between Avelin (FR) & Lonny (FR) | [10 empty] | commissioned | commissioned | Commissioned
| 41 | Fruges, Sud-Aveyron, Marne-Sud, Somme (FR) |  | New 400-kV substations connected to existing 400-kV network and equipped with transformers to 220 kV or high voltage networks | [10 empty] | design & permitting | mid term | Project progress according to the plan
| 52 | Feuillane (FR) | Realtor (FR) | Operation at 400 kV of existing 63km double circuit OHL previously operated at 220kV, creation of a new 400 kV substation and restructuration of the existing 220 kV local network | [10 empty] | under construction | 2012 | To be commissioned by end 2012 - delays due to longer than expected authorization process
| 61 | Moulaine (FR) | Belval (LU) | Connection of SOTEL (industrial grid in LU) to RTE network by mixed (underground cable & OHL) single circuit 220kV line. Parts of the new line use existing ones. | [10 empty] | under construction | short term | Commissioned in 2010 for the French part, the LU part is still pending
| 11 | Batalha-Lavos-Paraimo (PT) |  | Two new 400kV lines Batalha-Lavos and Lavos-Paraimo, needed to accommodate two new combined cycle power plants (4x435MW) on Littoral Central Region. Total length: 115km. | [10 empty] | commissioned | commissioned | Line Batalha-Lavos completed. Line Lavos-Paraimo was commissioned at the end of 2011.
| 39 | Avelin (FR) | Warande (FR) | Reconductoring (with ACSS) of both circuits of existing 400kV OHL between Avelin, Weppes & Warande. Total length : 85km | [10 empty] | commissioned | commissioned | Commissioned in 2010
| 43 | Mandarins (FR) |  | Replacement of thyristors in the AC/DC substation (IFA 2000 interconnector, DC voltage 270 kV) | [10 empty] | commissioned | commissioned | Currently under final tests. Will be commissioned in Summer 2012.
| 47 | Tamareau (FR) | Tavel (FR) | Reconductoring with ACCS of both circuits of existing 92km double circuit 400kV OHL to increase its capacity. | [10 empty] | commissioned | commissioned | Commissioned in 2011
| 49 | Cantegrit (FR) | Mouguerre (FR) | Reconductoring (with ACSS) of existing 83km single-circuit 220kV OHL to increase its capacity. | [10 empty] | commissioned | commissioned | Commissioned in 2011
| 50 | Néoules (FR) | Broc-Carros (FR) | The second circuit (formerly operated at 220kV) of a 197km double-circuit 400kV OHL will be operated at 400kV and 400/225 autotransformers installed in relevant substations. | [10 empty] | commissioned | commissioned | Commissioned in 2010
| 56 | Camporosso (IT) |  | New 450 MVA PST in Camporosso (IT) 220kV substation on Camporosso (IT) - Menton (FR) - Trinité-Victor (FR) OHL. | [10 empty] | under construction | 2012 | will be commissioned in 2012
| 59 | Moulaine (FR) | Aubange (BE) | Installation of a second circuit on the existing 220kV cross-border OHL | [10 empty] | commissioned | commissioned | Commissioned in 2010
| 7 | Armamar - Bodiosa - Paraimo (PT) |  | This 120km double-circuit OHL has been constructed according to 400kV standards but is currently operated at 220kV as Valdigem (PT) - Bodiosa (PT) -Paraimo (PT). The project consists of operating one circuit at 400kV while creating a new 400/220kV substation in Armamar and upgrading the existing Bodiosa substation from 220/60kV to 400/60kV. Total length of line : 120km. | [10 empty] | commissioned | commissioned | Commissioned
| A15 | Torernte (Ibiza) | Formentera | New double circuit Ibiza-Formentera 132 kV | [10 empty] | design & permitting | 2013/2017 | New project

## CCS report
5 July 2012
TYDNP 2012 package - Table of projects Continental Central South Regional Group Investment Plan
Project identification |  |  |  |  | Project assessment
Project number | Investment number | Substation 1 | Substation 2 | Brief technical description | Grid Transfer Capability Increase [MW] | Socio-economic Welfare | RES integration | Improved Security of Supply | Losses variation | CO2 mitigation | Technical resilience | Flexibility | Social and environmental Impact | Project costs | Present status | Expected date of commissioning | Evolution compared to the TYNDP 2010 situation | Investment comment | Project comment
5 | 5. 19 | Vic (ES) | Pierola (ES) | Upgrading (uprating) the existing 75km single circuit Vic-Pierola 400kV line in order to increase its capacity from 1360 MVA to 1710 MVA. | 1200-1400 in both directions | 1 | 2 | Perpignan, Gerona | [5 empty] | 2 | under construction | 2012 | Delays due to authorization process. |  | Mid-term interconnection project between France and Spain ("2.8 GW") . It includes cross border lines and internal lines required to assure NTC.
5 | 5. 20 | Arkale (ES) | Hernani (ES) | Upgrading the existing single circuit Arkale-Hernani n°2 220kV OHL in order to increase its capacity up to 640 MVA. | [10 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 5
5 | 5. 36 | Sta.Llogaia (ES) | Baixas (FR) | New HVDC (VSC) bipolar interconnection in the Eastern part of the border, via 320kV DC underground cable using existing infrastructures corridors and converters in both ending points. | [10 empty] | partly under construction, design & permitting | 2014 | Progresses as planned. |  | 5
5 | 5. 37 | Santa Llogaia (ES) | Bescanó (ES) | New double circuit Sta.Llogaia-Ramis-Bescano-Vic/ Senmenat 400kV OHL (single circuit in some sections) New 400kV substations in Bescano, Ramis and Sta.Llogaia, with 400/220kV transformers in Ramis and Bescano. | [10 empty] | under construction | 2011-2013 | Bescano-Vic/Senmenat 400 KV commissioned. Difficulties in the authorization process of the section Bescano-Sta Llogaia 400kV |  | 5
5 | 5. 46 | Baixas (FR) | Gaudière (FR) | Reconductoring of existing 70km double circuit 400kV OHL to increase its capacity. | [10 empty] | design & permitting | end 2013 | Progresses as planned |  | 5
16 | 16. 38 | Gatica (ES) | Aquitaine (FR) | New HVDC interconnection in the western part of the border via DC subsea cable in the Biscay Gulf. | Fr->Es 1200 ; Es ->Fr 2000 | 1 | 2 | Biarritz, Basque country | [5 empty] | 3 | under consideration | ca. 2020 | New investment in TYNDP, defined since last release, aiming 4 GW capacity between France and Spain. |  | Long-term interconnection project between France and Spain ("4 GW") . It includes cross border lines and internal lines required to assure NTC.
16 | 16. A14 | Amorebieta (ES) Garraf (ES) Adrall (ES) Orcoyen (ES) | Gueñes (ES) Secuita (ES) La Pobla (ES) Elgea (ES) | Uprates required in basque country and Catalonia in order to use fully the benefit of the longterm ES-FR interconnection. | [10 empty] | under consideration | 2016 | New investment in TYNDP meant to solve congestion in this area. |  | 16
16 | 16. A17 | Arkale (ES) |  | New PST on Arkale-Argia 220 kV interconnection line | [10 empty] | design & permitting | 2016 | New investment enabling to take full advantage of the transfer capacity of the new subsea interconnection. |  | 16
17 | 17. 42 | Lonny (FR) | Vesle (FR) | Reconstruction of the existing 70km single circuit 400kV OHL as double circuit OHL. | 9000 | 1 | 2 | Reims, Paris area | [5 empty] | 3 | design & permitting | 2016 | Progresses as planned |  | Project needed to cope with larger and more volatile North South power flows from Normandy to Champagne, triggered especially by the development of new generation sources (along the Channel coasts, from Picardie to Champagne and further North abroad) that would naturally flow to large consumption areas: Paris area, but also more broadly from Brittany to Reims.
17 | 17. 44 | Havre (FR) | Rougemontier (FR) | Reconductoring of existing 54km double circuit 400kV OHL to increase its capacity. | [10 empty] | under construction | 2018 | As the pace of generation installation is lower than expected, the investment has been postponed. | This investment is needed for integrating new generation in Le Havre area. As the pace of generation installation is lower than assumed earlier, the investment has been postponed from 2015 to 2018 | 17
17 | 17. A18 | tbd (FR) | tbd (FR) | New network reinforcement between Haute Normandy and the south of Paris area. Length about 160 km. | [10 empty] | under consideration | long term | New investment in TYNDP, defined since last release | Either existing assets uprate or new HVDC, actual needs still being evaluated, depending on uncertainties on generation location | 17
17 | 17. 45 | Taute (FR) | Oudon (FR) | "Cotentin-Maine "Project : new 163km double circuit 400kV OHL connected to existing network via two new substations in Cotentin and Maine regions. | [10 empty] | under construction | 2013 | Delays due to authorization process. |  | 17
17 | 17. A144 | Cergy (FR) | Terrier (FR) | MORP project : new single circuit 400-kV line between existing 400-kV substations | [10 empty] | planned | 2018 | New investment in TYNDP, defined since last release, triggered by larger and more volatile power flows between generation developing North of Paris and Paris area. |  | 17
18 | 18. 48 | Gaudière (FR) | Rueyres (FR) | Reconductoring with ACCS limiting section (10km) of existing single circuit 400kV OHL. | >1000 | 3 | 5 | Provence area | [5 empty] | 3 | under construction | end 2012 | Progresses as planned |  | Larger and more volatile North South power flows in South-Western France, triggered by the development of local RES generation but also influenced by transits flows with neighboring countries.
18 | 18. A19 | tbd (FR) | tbd (FR) | Restructuration of whole EHV grid in Massif Central area | [10 empty] | under consideration | long term | New investment in TYNDP, defined since last release, triggered by larger and more volatile power flows in South West France. |  | 18
18 | 18. 20. A20 | (Provence) (FR) | (Midi) (FR) | New subsea HVDC link between Marseille area and Languedoc | [10 empty] | design & permitting | 2018 | New investment in TYNDP, defined since last release, triggered by larger and more volatile power flows in South West France. |  | 18
19 | 19. 51 | Boutre (FR) | La Bocca (FR) | PACA "Filet de sécurité" project: construction of 3 new AC 220kV underground cables (Boutre - Trans [65 km], Biançon - Fréjus [26 km] & Biançon - La Bocca [17 km]) and installation of reactive power compensation devices in 220 kV Boutre and Trans substations | 500 | 2 | 5 | French riviera | [5 empty] | 1 | design & permitting | 2015 | Progresses as planned |  | Security of supply of the French riviera
20 | 20. 53 | Coulange (FR) | Le Chaffard (FR) | Reconductoring (with ACCS / ACCR) of two existing double circuit 400kV OHL (Coulange - Pivoz-Cordier - Le Chaffard and Coulange - Beaumont-Monteux - Le Chaffard). Total length of both lines: 275km | 2400 | 1 | 5 | South East France | [5 empty] | 2 | under construction | 2016 | Progresses as planned | Construction over 4 years because the works are only possible during limited periods every years on this strategic corridor | The project aims at ensuring the reliable grid operation to cope with new generation development along the Rhone Valley and more volatile power flows between the Alps and South Western France.
20 | 20. 18, A20 | [15 empty] | 0 | The investment contributes both to project 18 and project 20. For the technical description see project 18 | 20
21 | 21. 54 | Cornier (FR) | Piossasco (IT) | Replacement of conductors (by ACCS) on Albertville (FR) - Montagny (FR) - Cornier (FR) and Albertville (FR) - La Coche (FR) - La Praz (FR) - Villarodin (FR) - Venaus (IT) - Piossasco (IT) single circuit 400kV OHLs. In addition, change of conductors and operation at 400kV of an existing single circuit OHL between Grande Ile and Albertville (FR) currently operated at lower voltage, and associated works in Albertville (FR) 400kV substation. (Total length of lines : 257 km) | 1800 from FR to IT, (600 in the MT) | 1 | 5 | [6 empty] | 3 | under construction | 2012/2013 | Mainly progresses as planned although the works on existing lines take slightly longer than initially thought |  | Planned France-Italy interconnection development
21 | 21. 55 | Grande Ile (FR) | Piossasco (IT) | "Savoie - Piémont" Project : New 190km HVDC (VSC) interconnection FR-IT via underground cable and converter stations at both ends (two poles, each of them with 600MW capacity). The cables will be laid in the security gallery of the Frejus motorway tunnel and possibly also along the existing motorways' right-of-way. | [10 empty] | design & permitting | 2017/2018 | Progresses as planned |  | 21
21 | 21. 81 | Trino (IT) | Lacchiarella (IT) | A new 380kV double circuit OHL between the existing 380kV substations of Trino and Lacchiarella in North West Italy area. Total line length: 95km, Voltage upgrade of the existing Magenta 220/132kV substation up to 380kV. | [10 empty] | under construction | 2013 | Authorization process ended, construction phase on going |  | 21
21 | 21. 84 | Casanova (IT) | Vignole (IT) | Voltage upgrade of the existing 100km Casanova-Vignole 220kV OHL to 400kV and new 400/220/150kV substation in Asti area. | [10 empty] | design & permitting | long term | Delays due to authorization process. |  | 21
21 | 21. 101 | Turin (IT) |  | Restructuring of the 220kV network in the urban area of Turin. Some new 220kV cables, some new 220/132kV substations and some reinforcements of existing assets are planned. Total length: 63km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 21
22 | 22. 57 | under consideration (FR) | under consideration (CH) | Reinforcement of the interconnection in the area of Geneva's lake. | < 1000 from FR to CH and < 1500 from CH to FR | 3 | 2 | [6 empty] | 1 | under consideration | long term | Progresses as planned. Several technical options (route, technologies) have been designed and are being investigated. | The very uncertain environment, regarding commissioning and decommissioning of generation in particular makes the assessment complex. | France-Switzerland interconnection development under consideration.
23 | 23. 60 | under consideration (FR) | under consideration (BE) | To be determined. | 1800-3000 | 3 | 2 | Lille, Ruien area | [5 empty] | 2 | under consideration | 2018-2020 | Project entered a feasibility study phase. Expected date of commissioning is now 2018. |  | France-Belgium interconnection development: internal French grid reinforcements, that are prerequisite to maintain the present NTC and further interconnection development under consideration. This project enhances security of supply in Belgium and allows intra and inter countries RES integration.
23 | 23. A21 | Avelin (FR) | Mastaing (FR) | Operation at 400 kV of existing line currently operated at 220 kV | [10 empty] | design & permitting | 2017 | New investment in the TYNDP | Upgrade of all grid assets in Northern France at the same standard | 23
23 | 23. A22 | Avelin (FR) | Gavrelle (FR) | Substitution of a new double-circuit 400kV OHL to an existing 400-kV single circuit OHL | [10 empty] | design & permitting | 2017 | New investment in the TYNDP |  | 23
25 | 25. 62 | Under Consideration (FR) | Under Consideration (GB) | IFA2:New subsea HVDC link between the UK and France. Capacity is still to be determined. (Possibly 1000MW) | 1000 | 1 | 5 | [6 empty] | 2 | under consideration | 2020 | Further investigations during the feasibility phase have led to reassess the expected commissioning date for "IFA2" |  | France-UK interconnection development under consideration
26 | 26. 63 | Lienz (AT) | Veneto region (IT) | The project foresees the reconstruction of the existing 220kV-interconnection line as 380kV-line on an optimized route to minimize the environmental impact. Total length should be in the range of 100-150km. | 750 | 3 | 2 | [6 empty] | 3 | planned | long term | Progresses as planned |  | Reinforcement of the interconnection between Italy and Austria. Also the support the interaction between the RES in mainly Italy with the pump storage in the Austrian Alps.
26 | 26. 47. 220 | Lienz (AT) |  | Erection of a new 220/220kV- PST in the substation Lienz (AT). | [10 empty] | under construction | 2012 | Project is in errecion and expected to be commissioned 2012 according to the schedule | The investment contributes also to project 47. | 26
26 | 26. 47. 216 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 26
26 | 26. 64 | Bressanone (IT) | New substation near Innsbruck (AT) | New double circuit 400kV interconnection through the pilot tunnel of the planned Brenner Base Tunnel. Total line length: 65km. | [10 empty] | under consideration | >2022 | Progresses as planned |  | 26
26 | 26. 66 | Prati di Vizze (IT) | Steinach (AT) | Upgrade of the existing 44km Prati di Vizze (IT) – Steinach (AT) single circuit 110/132kV OHL, currently operated at medium voltage and installing a 110kV/132kV PST. | [10 empty] | design & permitting | mid term | Investment delayed with 2 years due to the permitting process |  | 26
26 | 26. 83 | Volpago (IT) | North Venezia (IT) | Realization of a new 380kV line between the existing substation of North Venezia and the future 380kV substation of Volpago, connected in and out to the 380kV "Sandrigo - Cordignano” . Total line length: 31km. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 26
26 | 26. 93 | Dolo (IT) | Camin (IT) | New 15km double circuit 400kV OHL between existing Dolo and Camin 400kV substations, to be built in parallel with the existing line. | [10 empty] | under construction | 2014 | Authorization process ended, construction phase on going |  | 26
26 | 26. 97 | Polpet (IT) |  | Voltage upgrade of the existing Polpet 150kV/medium voltage substation up to 220kV, complying with 400kV standards. The substation will be connected by two shorts links to the existing Soverzene-Lienz 220kV line. | [10 empty] | design & permitting | 2015 | Authorization process started, project phase on going |  | 26
26 | 26. 47. 218 | Obersielach (AT) | Lienz (AT) | New 190km 380kV OHL connecting the substations Lienz (AT) and Obersielach (AT) to close the Austrian 380kV-Ring in the southern grid area. Line length: 190km. | [10 empty] | under consideration | long term | Progresses as planned | The investment contributes also to project 47. | 26
26 | 26. A102 | New interconnection between Italy and Austria |  | New possible interconnection line between Italy and Austria | [10 empty] | under consideration | long term | This investment replaces investment n°65 mentioned on TYNDP 2010. The previous investment evolved so much that it is substituted by a new project. Feasibility studies ongoing including internal reinforcements. |  | 26
27 | 27. 68 | Okroglo (SI) | Udine (IT) | New 120km double circuit 400kV OHL with installation of a PST in Okroglo. The thermal rating will be 1870 MVA per circuit. | >1800 | 1 | 3 | [6 empty] | 2 | planned | long term | Progresses as planned |  | This project increases the capacity between Slovenia - Italy and Slovenia - Hungary. Project will remove congestion and strengthen connection on North-South and East-West axis.
27 | 27. 92 | West Udine (IT) | Redipuglia (IT) | New 40km double circuit 400kV OHL between the existing substations of West Udine and Redipuglia, providing in and out connection to the future 400kV substation of South Udine. | [10 empty] | design & permitting | 2015 | The investment is delayed due to longer than expected authorization procedures. |  | 27
27 | 27. A96 | New interconnection between Italy and Slovenia |  | New interconnection between Italy and Slovenia | [10 empty] | under consideration | long term | Feasibility studies ongoing including the internal reinforcements. | Need for strengthening the connection between Slovenia and Italy and increasing of power exchange capability | 27
27 | 27. 223 | Cirkovce (SI) | Heviz (HU) Zerjavenec (HR) | The existing substation of Cirkovce (SI) will be connected to one circuit of the existing Heviz (HU) -Zerjavinec (HR) double circuit 400kV OHL by erecting a new 80km double circuit 400kV OHL in Slovenia. The project will result in two new cross-border circuits: Heviz (HU) - Cirkovce (SI) and Cirkovce (SI) - Žerjavenec (HR). | [10 empty] | design & permitting | 2016 | Presently in the authorization process. This investment was delayed due to permitting process. |  | 27
27 | 27. 224 | Krsko (SI) | Bericevo (SI) | New 400kV double circuit OHL. This project will strengthen connection between East and Central part of Slovenia and connect an internal loop. Line length: 80km. | [10 empty] | under construction | 2015 | Authorization process ended, construction phase is on going. This investment was delayed due to permitting process. |  | 27
27 | 27. 225 | Divaca (SI) | Cirkovce (SI) | Upgrading 220kV lines to 400kV in corridor Divaca-Klece-Bericevo-Podlog-Cirkovce. Line length: 193km. | [10 empty] | planned | long term | Progresses as planned |  | 27
27 | 27. A105 | Lika(HR) | Brinje(HR) | New 55km single circuit 400 kV OHL replacing aging 220 kV overhead line | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. A106 | Lika(HR) | Velebit(HR) | New 60km single circuit 400 kV OHL replacing aging 220 kV overhead line | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. A107 | Lika (HR) |  | New 400/110 kV substation, 2x300 MVA | [10 empty] | planned | 2017 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. A108 | Brinje (HR) |  | New 400/220 kV substation, 1x400 MVA | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. 229 | Plomin (HR) | Melina(HR) | New 90 km double circuit OHL, with two connecting substations and transformer 400/220 kV, 400 MVA | [10 empty] | design & permitting | >2016 | Project moved to long term, due to postponed commissioning date of thermal power plant Plomin |  | 27
27 | 27. 227 | Banja Luka (BA) | Lika (HR) | New 400kV interconnection line between BA and HR | [10 empty] | under consideration | 2020 | End points of OHL and commissioning date defined after bilateral HR-BA agreement |  | 27
28 | 28. 70 | Villanova (IT) | Lastva (ME) | New 1000MW HVDC interconnection line between Italy and Montenegro via 375km 500kV DC subsea cable and converter stations at both ending points. | 1000 | 1 | 2 | [6 empty] | 3 | under construction | 2015 | Authorization process ended, construction phase on going. The substations on the ME side has been changed. |  | It contributes significantly to the increase of GTC between the West Balkans and IT such contributing to market integration; complements the ME - IT cable
28 | 28. 86 | Foggia (IT) | Villanova (IT) | New 178km double circuit 400kV OHL between existing Foggia and Villanova 400kV substations, also connected in and out to the Larino and Gissi substations. A PST will be installed on the new 400kV line. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 28
28 | 28. 89 | Fano (IT) | Teramo (IT) | New 200km single circuit 400kV OHL between the existing 400kV substations of Fano and Teramo, providing the connection in and out to the future substation to be built in Macerata area. | [10 empty] | design & permitting | long term | The investment is delayed due to longer than expected authorization procedures. |  | 28
28 | 28. 232 | Visegrad (BA) | Pljevlja (ME) | New 70km single circuit 400kV OHL between Visegrad and Pljevlja | [10 empty] | planned | 2015 | Feasibility study for 400kV interconnections RS-ME-BA proposed under Infrastructure Projects Facility for Western Balkans |  | 28
28 | 28. 233a | Lastva (ME) |  | A new substation will be connected to the existing line 400kV Podgorica 2(ME)-Trebinje(BA), with two transformers 2X300MVA 400/110kV, and convertor station for the DC cable Lastva(Tivat)-Villanova (see 70). | [10 empty] | design & permitting | 2015 | Feasibility study covering the aspects of route planning, substation location, environmental and social issues and equipment selection is due to end in second half of 2011 |  | 28
28 | 28. 233b | Lastva (ME) | Pljevlja (ME) | New 160 km double circuit 400kV OHL existing substation Pljevlja and new substation Tivat. | [10 empty] | design & permitting | 2016 | Feasibility study covering the aspects of route planning, substation location, environmental and social issues and equipment selection is due to end in second half of 2011 |  | 28
28 | 28. A109 | Bajina Basta (RS) | Visegrad (BA) | New 400kV interconnection OHL between Serbia and BiH, and reconstruction of existing two OHL 220 kV between BiH and Serbia. | [10 empty] | planned | >2016 | New investment in TYNDP | New 400 kV overhead line between Serbia and BIH. It will eliminate constraints in the region for electric energy transits and exchange. | 28
28 | 28. A110 | Bajina Basta (RS) | TPP Obrenovac (RS) | New double circuit 400 kV OHL between new substation Bajina Basta (see infra), and substation Obrenovac | [10 empty] | design & permitting | >2016 | New investment in TYNDP | Obrenovac is the "strongest" 400 kV node in Serbia, thus providing significant upgrade for evacuation and energy transfer from north to south, and further down in Montenegro, through the new line between Bajina Basta and Pljevlja (ME) | 28
28 | 28. A111 | Bajina Basta (RS) | Pljevlja (ME) | New 86 km single circuit 400kV OHL connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS). | [10 empty] | planned | >2016 | New investment in TYNDP |  | 28
28 | 28. A112 | Bajina Basta (RS) |  | New 400/110 kV substation in Bajina Basta, upgrading an existing 220/110 kV substation. | [10 empty] | planned | >2016 | New investment in TYNDP |  | 28
28 | 28. A113 | Bistrica (RS) |  | New 220/110 kV substation | [10 empty] | design & permitting | 2015 | New investment in TYNDP | After a topology change in the area, the investment will eliminate firm connection in "Vardiste" (secure and stable operation in Serbian network and systems of Bosnia and Herzegovina and Montenegro), to eliminate constraints in the region for electric energy transits and exchange. | 28
28 | 28. A114 | Konjsko(HR) | Velebit(HR) | New 100km single circuit 400 kV OHL replacing ageing 220 kV overhead line | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 28
28 | 28. 231 | Konjsko(HR) |  | Installation of a 150MVAr reactive power device | [10 empty] | design & permitting | 2014 | Investment postponed 1 year due to permitting process |  | 28
28 | 28. A115 | Plat (HR) |  | New 220/110 kV substation | [10 empty] | under construction | 2013 | New investment in TYNDP, contributing to mesh the network surrounding HVDC link IT-ME and to increase the reliability of the EHV system |  | 28
28 | 28. 228 | Trebinhe(BA) | Plat(HR) | Re-establishment of two previously existing 220kV single circuit interconnection Trebinje(BA)-Plat(HR); Total length 10km. | [10 empty] | planned | 2014 | Progresses as planned |  | 28
29 | 29. 73 | El Aouaria (TU) | Partanna (IT) | New 350km 1000 MW HVDC line between Tunisia and Italy via Sicily with 400kV DC subsea cable and converters stations at both ends. | 1500 | 3 | 5 | [6 empty] | 2 | design & permitting | long term | The investment is delayed due to longer than expected authorization procedures. | This project will be realized in 2 steps. In the previous TYNDP just the first part of the investment was mentioned (500MW). | Interconnection between Italy and North Africa. Other interconnection projects between North Africa and Italy are still under investigation and under study
29 | 29. 76 | Partanna (IT) | Ciminna (IT) | New 65km single circuit 400kV OHL in Sicily between existing Partanna and Ciminna substations. | [10 empty] | planned | long term | Progresses as planned |  | 29
29 | 29. A97 | unknown (IT) | unknown (AL) | New interconnection between Italy and Algeria -new DC submarine cable | [10 empty] | under consideration | long term | New investment in TYNDP | Need for a new interconnection between Algeria and Italy and increasing of power exchange capability with North Africa frontier. feasibility study on going | 29
30 | 30. 74 | Chiaramonte Gulfi (IT) | Sorgente (IT) | Realization of 380kV ring grid, trough the construction of 3 new 380kV line: "Chiaramonte Gulfi - Ciminna", "Sorgente - Ciminna" and "Paternò - Priolo". It will be realized a new 380/150kV substation in Caltanissetta area and the voltage upgrade of the existing Ciminna substation up to 380kV. Total line length: 365km. New 380/150 kV substation in Sorgente area will be temporally connected in and out to the existing 400 line kV "Paterno - Sorgente" and to the local 220 kV and 150 kV network. | 1000 | 4 | 1 | Palermo, Catania, Agrigento and Messina area | [5 empty] | 3 | planned | 2016/long term | Feasibility studies carried out have led to adapt the schedule. |  | Sicilian 400kV transmission ring.
30 | 30. 75 | Sorgente (IT) | Rizziconi (IT) | New 90km double circuit 400kV line, partly via subsea cable and partly via OHL. This line is part of a larger project that foresees the creation of the future 400kV ring grid of Sicily. | [10 empty] | under construction | 2014 | Delays on construction phase |  | 30
30 | 30. 77 | Partinico (IT) | Fulgatore (IT) | New 45km single circuit 400kV OHL between Partinico and Fulgatore in Western Sicily. | [10 empty] | planned | 2016 | Feasibility studies carried out have led to adapt the schedule. |  | 30
30 | 30. 87 | Feroleto (IT) | Maida (IT) | New 400kV OHL across Calabria between the existing substation of Feroleto and the future substation of Maida, while restructuring the existing grid in North Calabria. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 30
30 | 30. A98 | Mineo (IT) |  | New 380/150 kV substation in Mineo area connected in and out to the existing 400 line kV "Chiaramonte Gulfi - Paterno" and to the local HV network. | [10 empty] | planned | long term | New investment in TYNDP | needed to overcome the expected congestions on the central-east HV network of Sicily affected by the flows of consistent production from renewable plants | 30
31 | 31. 85 | Pavia area (IT) | Piacenza area (IT) | New 45km double circuit 400kV OHL between 2 substations in the Pavia area and Piacenza. | >1000 | 3 | [7 empty] | 2 | planned | long term | Initial design partially changed, with new reinforcements and rearrangements activities on the neighboring areas resulting from further studies |  | Increase interconnection capability between IT and CH.
31 | 31. 95 | Mese (IT) |  | Voltage upgrade of the existing 220/132kV Mese substation up to 400kV. | [10 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 31
31 | 31. 99 | Avise (IT) | Chatillon (IT) | Voltage upgrade of the existing 40km Avise-Villeneuve-Chatillon single circuit 220kV OHL up to 400kV. | [10 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 31
31 | 31. 100 | Milan (IT) |  | Restructuring of the 220kV network in the urban area of Milan. Some new 220kV cables (33km), a new 220kV substation (Musocco) and some reinforcements of existing assets (35km) are planned. | [10 empty] | design & permitting | mid term | The cables in the Milan area are in operation, the appropriate substations are under construction and the reinforcements are under design and permitting. |  | 31
31 | 31. 103 | Brescia (IT) |  | New 400/132kV substation in South East area of Brescia, connected in and out to the existing Flero-Nave 400kVOHL, while restructuring the 132kV network. | [10 empty] | planned | mid term | Progresses as planned |  | 31
31 | 31. 112 | Tirano (IT) | Verderio(IT) | New 140km single circuit 400kV OHL between Tirano and Verderio substations connecting also the new 400kV substation Grosio/Piateda. | [10 empty] | planned | long term | Progresses as planned |  | 31
31 | 31. 124 | Mettlen (CH) | Airolo (CH) | Upgrade of existing 225kV OHL into 400kV. Line length: 90km. | [10 empty] | under consideration | 2020 | Progresses as planned |  | 31
31 | 31. A101 | New interconnections between Italy and Switzerland |  | Up to 4 interconnection projects are under discussion, one or two probably will be implemented | [10 empty] | under consideration | long term | This investment replaces investment n° 120 mentioned on TYNDP 2010. The previous investment evolved so much that it is substituted by a new project. Feasibility studies ongoing including the internal reinforcements. |  | 31
32 | 32. 88 | Montecorvino (IT) | Benevento (IT) | New 70km double circuit 400kV OHL between the existing 400kV substations of Montecorvino and Benevento II, providing in and out connection to the future substation to be build in Avellino North area, which will be also connected to the existing "Matera-S. Sofia" 400kV line. | 1900 | 4 | 1 | Naple urban area, Sorrento Penninsul, minor Campania islands and Tirrenic South coast Italy | [5 empty] | 3 | design & permitting | mid term | The Avelino substation is under construction, the line is in delay due to authorization process. |  | Reinforcement between South and Central-South of Italy to accommodate increasing market flows.
32 | 32. 91 | Foggia (IT) | Benevento II (IT) | Upgrade of the existing 85km Foggia-Benevento II 400kV OHL and installation of a PST on this line. | [10 empty] | under construction | 2013-2014 | Authorization process ended, construction phase on going |  | 32
32 | 32. 96 | Deliceto (IT) | Bisaccia (IT) | New 30km single circuit 400kV OHL between the future substations of Deliceto and Bisaccia, in the Candela area. | [10 empty] | design & permitting | mid term | The 2 substations are in operation from 2011. The connecting line is still in design and permitting. This delay is due to authorization process. |  | 32
32 | 32. 96a | Several new 38 kV substations in Central / South of Italy for RES (IT) |  | It will be realized few new 380/150kV substations. The new substations will be connected to the wind power plants in order to avoid the congestions on the 150kV network and to dispatch the renewable energy produced. | [10 empty] | under construction | mid term | The realization of the substations is delayed. These investments are highly sensitive to the construction of the wind/solar plants that are meant to connect. |  | 32
32 | 32. 102 | Naples (IT) |  | Restructuring of the 220kV network in the urban area of Naples. Some new 220kV cables and some reinforcements of existing assets are planned. Total length: 36km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 32
32 | 32. 110a | Aliano (IT) | Montecorvino (IT) | New connection OHL 400 kV between north Basilicata and Campania region. | [10 empty] | planned | long term | Progresses as planned |  | 32
32 | 32. A99 | Restructuring of North Calabria (IT) |  | New 400kV OHL between the existing substations of Laino and Altomonte in Calabria and a new 380/150 kV substation in Aliano connected in and out to the existing 400 line kV "Matera - Laino" and to the local HV network. Related to this project will be acted a great restructuring of the local HV network, downgrading the existing 220 kV lines to 150 kV level and the demolition of great part of existing 150 kV lines inside the Pollino Park. | [10 empty] | partly under construction, design & permitting | 2012/mid term | New investment in TYNDP (initial design partially changed, evolution including new reinforcements and rearrangements activities on the neighboring areas resulting from further studies) |  | 32
33 | 33. 90 | Calenzano (IT) | Colunga (IT) | Voltage upgrade of the existing 80km Calenzano-Colunga 220kV OHL to 400kV, providing in and out connection to the existing 220/150kV substation of S. Benedetto del Querceto (which already complies with 400kV standards). | 500 | 2 | 5 | central part of Italy | [5 empty] | 2 | design & permitting | mid term | Delays due to authorization process. |  | Reinforcement between Northern and Central part of Italy to accommodate increasing market flows.
33 | 33. 94 | Mantova area (IT) | Modena area (IT) | New 35km 400kV OHL between the 2 substations in Modena and Mantova area. | [10 empty] | planned | long term | During the preliminary consultation process the substations have became uncertain. |  | 33
33 | 33. 104 | Rome (IT) |  | Restructuring of the network in the Rome area. The work consists of : a new 380/150kV substation in south-West area of Rome, connected in and out to the existing 380kV line "Rome West-Rome South", a voltage upgrade of the existing Flaminia substation up to 380kV to be connected in and out to the foreseen 380kV line "Rome West - Rome North" and a restructuring of the 150kV network. | [10 empty] | design & permitting | 2013/long term | Progresses as planned |  | 33
33 | 33. 109 | North Bologna (IT) |  | New 400/132kV substation in North Bologna area connected in and out to the existing Sermide–Martignone 400kV line. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 33
33 | 33. 111 | Lucca (IT) |  | New 380/132kV substation in Lucca area connected in and out to the existing 380kV line “La Spezia-Acciaiolo”. | [10 empty] | planned | long term | Progresses as planned |  | 33
33 | 33. 113 | Monte S. Savino (IT) |  | New 400/220/132kV substation in Monte S. Savino area connected to the existing S. Barbara 400kV substation by upgrading an existing 220kV line. | [10 empty] | design & permitting | 2015/long term | Delays due to authorization process. |  | 33
34 | 34. A100 | Codrongianos (IT) | Suvereto (IT) | Repowering of existing HVDC interconnection between Sardinia, Corse and mainland Italy via 220kV DC subsea cable (358km). The first connection is in operation since 1970. Total capacity of the bipolar link: 500MW. | 500 | 4 | 1 | [6 empty] | 2 | planned | long term | New investment in TYNDP. |  | Reinforcement between Sardinia Corso and mainland Italy.
35 | 35. 137 | Vitkov (CZ) | Mechlenreuth (DE) | New 400kV single circuit tie-line between new (CZ) substation and existing (DE) substation. Length: 70km. | 500 | 5 | 4 | [6 empty] | 3 | under consideration | long term | Progresses as planned |  | This project is required to enable power flows between West and East, enhance the transfer capability between CZ and DE and supports the future generation evacuation.
35 | 35. 138 | tbd (CZ) | tbd (DE) - South-Eastern part of 5 Hertz Transmission control area (Röhrsdorf) | Possible increase of interconnection capacity between CEPS and 50Hertz Transmission is under consideration: either a new 400kV tie-line (OHL on new route) or a reinforcement of the existing 400kV tie-line Hradec (CEPS) – Röhrsdorf (50Hertz Transmission). | [10 empty] | under consideration | long term | Progresses as planned |  | 35
35 | 35. 306 | Vitkov (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA. | [10 empty] | planned | 2017/2018 | It is closely dependent on construction of line investment n°308 |  | 35
35 | 35. 307 | Vernerov (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA. | [10 empty] | planned | 2013/2016 | Commissioning date has been divided into two phases (1. phase - temporary connection of wind plant 180MW, 2. phase finalization of substation construction including connection to the distribution grid (consumption) |  | 35
35 | 35. 308 | Vernerov (CZ) | Vitkov (CZ) | New 400kV double circuit OHL, 1385 MVA. | [10 empty] | planned | long term | Permitting procedure complications are foreseen (line crosses protected area) |  | 35
35 | 35. 309 | Vitkov (CZ) | Prestice (CZ) | New 400kV double circuit OHL, 1385 MVA. | [10 empty] | under consideration | long term | Permitting procedure complications are foreseen (line crosses protected area) |  | 35
35 | 35. 311 | Kocin (CZ) |  | Upgrade of the existing substation 400/110kV; upgrade transformers 2x350MVA. | [10 empty] | design & permitting | long term | Schedule harmonization with market participants |  | 35
35 | 35. 312 | Mirovka (CZ) |  | Upgrade of the existing substation 400/110kV with two transformers 2x250MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 313 | Kocin (CZ) | Mirovka (CZ) | Connection of 2 existing 400kV substations with double circuit OHL having 120.5km length: and a capacity of 2X1385 MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 314 | Mirovka (CZ) | V413 (CZ) | New double circuit OHL with a capacity of 2x1385 MVA and 26.5km length. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 315 | Kocin (CZ) | Prestice (CZ) | Adding second circuit to existing single circuit line OHL upgrade in length of 115.8km. Target capacity 2x1385 MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 316 | Mirovka (CZ) | Cebin (CZ) | Adding second circuit to existing single circuit line (88.5km, 2x1385 MVA). | [10 empty] | under consideration | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 317 | Hradec (CZ) | Reporyje (CZ) | Upgrade of existing 400kV single circuit OHL with length of 116.9km. Target capacity 1385 MVA. | [10 empty] | commissioned | commissioned | Commissioned |  | 35
36 | 36. 141 | Ishøj/Bjæverskov (DK) | Bentwisch/Güstrow (DE) | The Kriegers Flak Combined Grid Solution is the new offshore multiterminal connection between Denmark and Germany used for both grid connection of offshore wind farms Kriegers Flak and interconnection. Technical features still have to be determined. | 600 | 5 | 3 | [6 empty] | 1 | planned | long term | Permission for Danish Wind Farm KF 3 is in pending. Connection to Sweden is withdrawn at present, but can come on a later stage. |  | The Kriegers Flak Combined Grid Solution is the new offshore multiterminal connection between Denmark and Germany used for both grid connection of offshore wind farms Kriegers Flak and interconnection.
37 | 37. 142 | Tonstad (NO) | Wilster (DE) | Nord.Link/NorGer: a new HVDC connection between Southern Norway and Northern Germany. Estimated subsea cable length: 520 - 600km. Capacity: 1000 MW. | up to 1400 | 1 | 4 | [6 empty] | 3 | design & permitting | 2018/2021 | Revised capacity and progress postponed, due to more demanding system operations and time needed to obtain necessary government permits for reinforcing the national grid. |  | The purpose is: Market integration with the continent and facilitating RES integration in southern and western Norway. Will also improve security of supply in southern Norway.
| 37. 408 | Kristiansand, Feda (NO) |  | Reactive compensation due to HVDC links NorNed and Skagerak 4. Reactive power devices in 400kV substations. | [10 empty] | design & permitting | 2012/2014 | Feda is in the planning and permitting stage. Kristiansand is under construction(commissioned expected as planned 2012)
37 | 37. 406 | (Southern part of Norway) (NO) |  | Voltage uprating of existing 300 kV line Sauda/Saurdal - Lyse - Tonstad - Feda - 1&2, Feda - Kristiansand; Sauda-Samnanger in long term. Voltage upgrading of existing single circuit 400kV OHL Tonstad-Solhom-Arendal. Reactive power devices in 400kV substations. | [10 empty] | design & permitting | 2016 (2013-2018) | Revised progress. Due to more demanding system operations and time needed to obtain necessary government permits for reinforcing the national grid. The investment now embed former TYNDP 2010's investments 407 and 409 and the technical description has been updated accordingly. |  | 37
39 | 39. 428 | Kassø (DK) | Tjele (DK) | Rebuilding of a 400kV OHL of 173km from a single-circuit to a double-circuit . This increases the transfer capacity with approx. 1000 MW. | 1000-1550 | 1 | 2 | [6 empty] | 2 | design & permitting | 2012/2014 | Progresses as planned |  | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity.
39 | 39. 144 | Audorf (DE) | Kassö (DK) | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity. It consists of partially an upgrade of existing 400kV line and partially a new 400kV route in Denmark. In Germany new 400kV line mainly in the trace of a existing 220kV line. The total length of this OHL is 114km. | [10 empty] | under consideration | 2017 | Progresses as planned |  | 39
40 | 40. 446 | Bascharage (LU) | Aubange (BE) | As a first step(2016) a PST could be placed in the existing 225kV line between LU and BE. In a second stage, two solutions are currently investigated (4 TSOs - Elia, Amprion, CREOS, RTE are involved). Solutions 1 would be a new interconnection between Creos grid in LU and ELIA grid in BE via a 16km double circuit 225kV underground cable with a capacity of 1000 MVA. Solution 2 would be the interconnection between CREOS grid in LU and ELIA grid in BE via a new 380 kV double circuit. The current study will investigate the impact of this new interconnection on other boundaries (impact of loop flow) and on internal grids . The potential reinforcements of the other boundaries and the internal grids will also be taken into account in the evaluation. | 380-900 | 2 | 5 | Luxemburg area | [5 empty] | 2 | under consideration | 2016/2020 | The commissioning date and status changed as the study to determine the best investment is still ongoing. |  | Increase the transfer capability between LU,DE, BE and FR.
40 | 40. A29 | Bascharage (LU) | tbd (BE, DE, &/o FR) | New interconnection with neighbor(s) either 220kV or 400kV | [10 empty] | under consideration | 2020 | New investment in TYNDP | An ongoing network study (4 TSOs involved) investigates the robustness of the planned 220kV connection between LU and BE and the potentially need for an upgrading to a 400kV interconnector in the South. | 40
40 | 40. 447 | Heisdorf (LU) | Berchem (LU) | New 20km double-circuit mixed (underground cable+OHL) 225kV project with 1000 MVA capacity including substations for in feed in lower voltage levels. | [10 empty] | design & permitting | 2012/2017 | Progresses as planned |  | 40
40 | 40. A30 | Bascharage (LU) | Niederstedem (DE) or tbd (DE) | Upgrading and new construction of an interconnector to DE, in conjunction with the interconnector in the south of LU; Partial upgrading of existing 220kV lines and partial new construction of lines; With power transformer station in LU | [10 empty] | under consideration | 2020 | New investment in TYNDP |  | 40
41 | 41. 149 | Dollern (DE) | Stade (DE) | New 400kV double circuit OHL Dollern - Stade including new 400kV switchgear in Stade. Length:14km. | >3000 | 4 | 5 | [6 empty] | 1 | design & permitting | mid term | This investment depends on the commissioning of a conventional power plant in the area. The additional reason for delay is the long permitting procedure associated with this investment. |  | Evacuation of the new conventional generation in the 50Hz and TenneT area.
41 | 41. 150 | Conneforde (DE) | Maade (DE) | New 400kV double circuit ( underground cable+OHL) Conneforde - Maade including new 400kV switchgear Maade. Length: 37km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 41
41 | 41. A74 | North of Control Area 5 HzT (DE) |  | Construction of new substations/lines for integration of newly build power plants in northern part of 50HzT control area. | [10 empty] | planned | long term | New investment in TYNDP, because of additional need for generation evacuation. Some of the investments are to be commissioned by the mid term and the some by long term. | Support of conventional generation integration in North-Eastern Germany, maintaining of security of supply and support of market development. | 41
42 | 42. 152 | Dörpen/West (DE) |  | New substation for connection of offshore wind farms. | >8000 | 4 | 1 | [6 empty] | 3 | under construction | mid term | Progresses as planned | Commercially sensitive information about this new wind-farm connection cannot be displayed in the TYNDP report | Integration of the offshore wind parks and the onshore grid reinforcements in the Northern DE.
42 | 42. 159 | Cluster BorWin1 (DE) | Diele (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 205km. Line capacity: 400MW. | [10 empty] | under construction | mid term | The commission date of this wind farms connection should be in 2012. Energy transportation is however already enable | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 160 | Offshore- Wind park Nordergründe (DE) | Inhausen (DE) | New AC-cable connection with a total length of 35km. | [10 empty] | design & permitting | mid term | Progresses depend on development of the off shore wind farm |  | 42
42 | 42. 161 | Offshore- Wind park GEOFreE (DE) | Göhl (DE) | New AC-cable connection with a total length of 32km. | [10 empty] | design & permitting | mid term | Progresses depend on development of the off shore wind farm |  | 42
42 | 42. 163 | Cluster HelWin1 (DE) | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 145km. Line capacity: aprox. 690MW. This Project includes also a new substation Büttel and connection of this new substation with the existing OHL Brünsbüttel - Wilster. | [10 empty] | under construction | mid term | Progresses with delay. | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 164 | Cluster SylWin1 (DE) | Büttel (DE) | New line consisting of underground +subsea cable with a total length of 210km. Line capacity: aprox.864MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 165 | Cluster DolWin1 (DE) | Dörpen/West (DE) | New line consisting of underground +subsea cable with a total length of 155km. Line capacity: 800MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 166 | Offshore Wind park Riffgat (DE) | Emden /Borßum(DE) | New AC-cable connection with a total length of 80km. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 167 | Cluster BorWin2 (DE) | Diele (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 205km. Line capacity: 800MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A82 | Cluster DolWin2 (DE) | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 160 km. Line capacity: 900 MW | [10 empty] | under construction | mid term | New investment in TYNDP, for connection of new off-shore wind-farms | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A83 | Cluster DolWin3 (DE) | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 160 km. Line capacity: 900 MW | [10 empty] | design & permitting | mid term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A84 | Cluster BorWin3 | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 180 km. Line capacity: 900 MW | [10 empty] | design & permitting | mid term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A85 | Cluster HelWin2 | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 145km. Line capacity: 690 MW | [10 empty] | under construction | mid term | New investment in TYNDP, for connection of new off-shore wind-farms | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A86 | Cluster BorWin4 (DE) | Emden/Ost (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 185 km. Line capacity: 900 MW | [10 empty] | under consideration | long term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A87 | Cluster SylWin2 (DE) | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 210km. Line capacity: 800 MW | [10 empty] | under consideration | long term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. 211 | Further connections of more offshore wind farms (DE) |  | Further connections in the clusters BorWin, DolWin, SylWin and HelWin. | [10 empty] | under consideration | long term | Progresses depend on development of the off shore wind farm |  | 42
43 | 43. A81 | Osterath (DE) | Philippsburg (DE) | New HVDC-lines from Osterath to Philippsburg to integrate new wind generation especially from North/ Baltic Sea towards Central-South Germany for consumption and storage. | 10000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany |  | Combined DC and AC new infrastructure to accommodate the new RES generation, the associated flows from North to South and also secure the SOS in South Germany.
| 43. A152 | Emden (DE) | Osterath (DE) | New HVDC-lines from Endem to Osterath to integrate new wind generation especially from North/ Baltic Sea towards Central Germany for consumption and storage. | [10 empty] | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany
| 43. A153 | Wehrendorf (DE) | Urberach (DE) | New lines in HVDC technology from the region of Lower Saxony to North Baden-Württemberg to integrate new wind generation especially from North Sea towards Central-South Europe for consumption and storage. The investment is part of the transmission corridor Cloppenburg - North Baden-Württemberg. | [10 empty] | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany
| 43. A154 | Cloppenburg (DE) | Westerkappeln (DE) | New 400-kV double circuit OHL Cloppenburg-Westerkappel (75 km). The investment is part of the transmission corridor Cloppenburg - North Baden-Württemberg. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
43 | 43. A88 | Brunsbüttel (DE), Wilster (DE), Kaltenkirchen (DE) | Großgartach (DE), Goldshöfe (DE), Grafenrheinfeld (DE) | New DC-lines to integrate new wind generation from Northern Germany towards Southern Germany and Southern Europe for consumption and storage. | [10 empty] | under consideration | long term | New Investment. |  | 43
43 | 43. A75 | Lauchstadt (DE) | Meitingen (DE) | New DC- lines to integrate new wind generation from Baltic Sea towards Central/south Europe for consumption and storage. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits |  | 43
43 | 43. A89 | Area of Northern Lower Saxony (DE) |  | New lines for integration of on- and offshore Wind generation incl. 380-kV-lines Halbemond - Emden, Emden-Conneforde and Conneforde - Cloppenburg. Total length: 160 km | [10 empty] | under consideration | long term | New Investment. |  | 43
43 | 43. A90 | Area of Schleswig-Holstein (DE) |  | About 300 km new 380-kV-lines and around 24 new transformers for integration of onshore Wind in Schleswig-Holstein, incl. lines Brunsbüttel-Barlt-Heide-Husum-Niebüll-border of Denmark, Audorf-Kiel-Göhl-Siems-Lübeck-Kaltenkirchen and Kaltenkirchen-Itzehoe-Brunsbüttel | [10 empty] | under consideration | long term | New investment in TYNDP due to new wind generation projects. | The German West-coast line (Brunsbuettel – Niebuel) is planned to be connected to the Danish grid in the 400 kV substation Endrup. The distance from the German/Danish border is approx. 80 km. Bilateral technical/economical investigations are ongoing. Reinforcements in the Danish 400 kV grid are foreseen in order to facilitate the increased power exchange capacity on the Danish-German border. | 43
44 | 44. 147 | Dollern (DE) | Hamburg/Nord (DE) | New 400kV double circuit OHL Dollern - Hamburg/Nord including one new 400/230kV transformer in substation Hamburg/Nord and new 400kV switchgear Kummerfeld. Length:43km. | 5000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 | design & permitting | mid term | Delays due to authorization process. |  | This project helps accommodating the increasing flows coming mainly form RES in NW DE to SW DE and CH.
44 | 44. 148 | Audorf (DE) | Hamburg/Nord (DE) | New 400kV double circuit OHL Audorf - Hamburg/Nord including two new 400/230kV transformers in substation Audorf. Length: 65km. | [10 empty] | design & permitting | mid term | This investment was schedulted for 2015. Presently it is foreseen a delay of around 1 year due to permitting process. |  | 44
44 | 44. 151 | Wehrendorf (DE) | Ganderkesee (DE) | New line (length: ca. 95km), extension of existing and erection of substations, erection of 380/110kV-transformers. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 156 | Niederrhein (DE) | Dörpen/West (DE) | New 400kV double circuit OHL Dörpen - Niederrhein including extension of existing substations. Length: 167km. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 157 | Wahle (DE) | Mecklar (DE) | New 400kV double circuit OHL Wahle - Mecklar including two new substations. Length: 210km. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 90. 170 | Großgartach (DE) | Hüffenhardt (DE) | New 380kV OHL. Length: 23km. Included with the project : 1 new 380kV substation, 2 transformers. | [10 empty] | under construction | 2012 | Progresses as planned |  | 44
44 | 44. 171 | Hüffenhardt (DE) | Neurott (DE) | Upgrade of the line from 220kV to 380kV. Length: 11km. Included with the project : 1 new 380kV substation. | [10 empty] | planned | 2020 | Progresses as planned |  | 44
44 | 44. 90. 172 | Mühlhausen (DE) | Großgartach (DE) | Upgrading line from 220kV to 380kV. Length:-45km. | [10 empty] | design & permitting | 2014 | Progresses as planned |  | 44
44 | 44. 90. 173 | Hoheneck (DE) | Endersbach (DE) | Upgrading line from 220kV to 380kV. Length:20km. | [10 empty] | design & permitting | 2014 | Progresses as planned |  | 44
44 | 44. 174 | Bruchsal Kändelweg (DE) | Ubstadt (DE) | A new 380kV OHL. Length:6km. | [10 empty] | design & permitting | 2014 | Postponed from one year due to permitting procedures |  | 44
44 | 44.90. 176 | Daxlanden | Eichstetten | Upgrade of transmission capacity of existing 380 kV line (120 km) | [10 empty] | under consideration | 2020 | Progresses as planned |  | 44
44 | 44. 178 | Baden-Württemberg, Süden & Nordosten (DE) |  | Installation of 2x250 MVAr 380kV capacitance banks. | [10 empty] | under construction | 2014 | One more bank in addition. Two have already been installed. Projects realised earlier because the need for reactive power compensation became urgent. |  | 44
44 | 44. 179 | Rommerskirchen (DE) | Weißenthurm (DE) | New line, extension of existing and erection of substations, erection of 380/110kV-transformers. Total line length: 100km. | [10 empty] | under construction/design & permitting | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. 181 | Dauersberg (DE) | Limburg (DE) | New 380kV double circuit OHL, extension of existing of substations, Total line length: 20km. | [10 empty] | under construction/design & permitting | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. 182 | Kriftel (DE) | Obererlenbach (DE) | New 400 kV double circuit OHL Kriftel - Obererlebenbach in existing OHL corridor. Length: 11 km | [10 empty] | planned | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. A80 | Area of West Germany (DE) |  | Installation of several 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | under consideration | long term | New investment in TYNDP, because of additional needs for RES integration (combined with SoS) |  | 44
44 | 44. 183 | Wehrendorf (DE) |  | Installation of 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 184 | Bürstadt (DE) |  | Installation of 2 x 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 185 | Area of Muensterland and Westfalia (DE) |  | New lines and installation of additional circuits, extension of existing and erection of several 380/110kV-substations. Total length: ca. 110km. | [10 empty] | design & permitting | long term | Delays due to authorization process. |  | 44
44 | 44. 186 | Gütersloh (DE) | Bechterdissen (DE) | New lines and installation of additional circuits, extension of existing and erection of 380/110kV-substation. Total line length:27km. | [10 empty] | under construction | mid term | Delays due to authorization process. |  | 44
44 | 44. 187 | Area of West-Rhineland (DE) |  | New lines and installation of additional circuits, extension of existing and erection of several 380/110kV-substations. | [10 empty] | under construction | 2013 | Progresses as planned |  | 44
44 | 44. 188 | Kruckel (DE) | Dauersberg (DE) | New lines, extension of existing and erection of several 380/110kV-substations. Total line length: 130km. | [10 empty] | planned | long term | Progresses as planned |  | 44
44 | 44. A78 | Pkt. Metternich (DE) | Niederstedem (DE) | Construction of new 380kV double-circuit OHLs, decommissioning of existing old 220kV double-circuit OHLs, extension of existing and erection of several 380/110kV-substations. Length: 108km. | [10 empty] | planned | long term | New investment in TYNDP | RES integration/ Market integration especially east-west-direction | 44
44 | 44. A77 | Area of South-Wuerttemberg (DE) |  | Construction of new 380kV double-circuit OHLs, decommissioning of existing double-circuit OHLs, extension of existing 380-kV-substations. Length: ca. 60km. | [10 empty] | planned | long term | New investment in TYNDP | RES integration combined with pump storage in the alp region (market) / increasing of the NTC DE-CH/AT | 44
44 | 44. 190 | Saar-Pfalz-Region (DE) |  | New lines, extension of existing and erection of several 380/110kV-substations. Upgrade of an existing line from 220 to 380 kV | [10 empty] | planned | long term | Delays due to authorization process. | SoS (Neub. Frltg Fraulaut-Saarwellingen) combined with RES integration | 44
| 44. A155 | Conneforde (DE) | Unterweser (DE) | Upgrade of 230-kV-circuit Unterweser-Conneforde to 400kV , Line length: 32 km. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A156 | Dollern (DE) | Elsfleht/West (DE) | New 400 kV line in existing OHL corridor Dollern - Elsfleht/West Length:100 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A157 | Dollern (DE) | Landesbergen (DE) | New 400 kV line in existing OHL corridor Dollern-Sottrum-Wechold-Landesbergen (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A158 | Hamm/Uentrop (DE) | Kruckel (DE) | Extension of existing line to a 400 kV single circuit OHL Hamm/Uentrop - Kruckel. Length: 60 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A159 | Pkt. Blatzheim (DE) | Oberzier (DE) | New 400 kV double circuit OHL Pkt. Blatzheim - Oberzier including extension of existing substations. Length 16 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A160 | Urberach (DE) | Daxlanden (DE) | New line and extension of existing line to 400 kV double circuit OHL Urberach - Pfungstadt - Weinheim - Daxlanden including extension of existing substations. Length: 219 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A161 | Bürstadt (DE) | Daxlanden (DE) | New line and extension of existing line to 400 kV double circuit OHL Bürstadt - Lambshein - Daxlanden including extension of existing substastions. Length: 134 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A162 | Großgartach (DE) | Endersbach (DE) | Extension of existing 400-kV-line Großgartach - Endersbach. (Lenght: 32 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
44 | 44. 175 | Birkenfeld (DE) | Ötisheim (DE) | A new 380kV OHL. Length:11km. | [10 empty] | planned | 2020 | New investment in TYNDP |  | 44
44 | 44. 189 | Niederrhein (DE) | Utfort (DE) | New 400 kV double-circuit OHL Niederrhein-Utfort (24 km). | [10 empty] | under consideration | long term | New investment in TYNDP |  | 44
45 | 45. 90. 177 |  |  |  | 5000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 |  |  | 0 | The investment contributes both to project 45 and project 90. For the technical description see project 90. | This project helps accommodating the increasing flows coming mainly form RES in NE DE to South DE and to the Alps.
45 | 45. 191 | Neuenhagen (DE) | Vierraden (DE) | Project of new 380kV double-circuit OHL Neuenhagen-Vierraden-Bertikow with 125km length as prerequisite for the planned upgrading of the existing 220kV double-circuit interconnection Krajnik (PL) – Vierraden (DE Hertz Transmission). | [10 empty] | design & permitting | 2013/2015 | Project in permitting phase, strong local resistance |  | 45
45 | 45. 193 | Halle/Saale (DE) | Schweinfurt (DE) | New 380kV double-circuit OHL between the substations Vieselbach-Altenfeld-Redwitz with 215km length combined with upgrade between Redwitz and Grafenrheinfeld (see project 153). The Section Lauchstedt-Vieselbach has already been commissioned. Support of RES integration in Germany, annual redispatching cost reduction, maintaining of security of supply and support of the market development. The line crosses the former border between Eastern and Western Germany and is right downstream in the main load flow direction. The project will help to avoid loop flows through neighboring grids. | [10 empty] | design & permitting | mid term | Investment partly completed, strong local public resistance- delay due to permitting process |  | 45
45 | 45. 197 | Neuenhagen (DE) | Wustermark (DE) | Construction of new 380kV double-circuit OHL between the substations Wustermark-Neuenhagen with 75km length. Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | under construction | mid term | Investment partly under construction and partly in permitting phase. Expected date of commissioning was adjusted due to long permitting process and strong local public resistance. |  | 45
45 | 45. 199 | Western Pomerania (DE) | Uckermark North (DE) | Construction of new 380kV double-circuit OHLs in North-Eastern part of 50HzT control area and decommissioning of existing old 220kV double-circuit OHLs, incl. 380-kV-line Bertikow-Pasewalk (30 km). Length: 135km.Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015 | Progresses as planned |  | 45
45 | 45. 200 | Lubmin (DE) | Erfurt area (DE) | 380-kV-grid enhancement and structural change area Lubmin-Stralsund and area Magdeburg/Wolmirstedt, incl. 380-kV-line Güstrow-Wolmirsted (195 km) | [10 empty] | planned | long term | Progresses as planned |  | 45
45 | 45. 202 | Area upper Lausitz(DE) | Area Gera(DE) | Upgrading existing double-circuit 380kV OHL in the South-Eastern part of the control area of 50Hertz Transmission. Bärwalde-Schmölln length approx.. 50km. Support of RES and conventional generation integration in North-Eastern Germany, maintaining of security of supply and support of market development. | [10 empty] | design & permitting | 2017 | Progresses as planned |  | 45
45 | 45. 204 | Calbe (DE) |  | Construction of new 380kV double-circuit OHL in substation Calbe for double connection/loop into an existing line. | [10 empty] | planned | mid term / long term | The evolution of this investment depends on the development of the power plant in the area. The date mentioned in the TYNDP 2010 was a typing mistake. |  | 45
45 | 45. 205 | Fördertsedt (DE) | Area Magdeburg(DE) | Construction of new 380kV double-circuit OHL from the substation Förderstedt with 20 km length for double connection/loop in for Förderstedt; Reinforcement of existing switchgear, Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015/2020 | Progresses as planned |  | 45
45 | 45. 206 | Area Leipzig(DE) | Area Chemnitz(DE) | Construction of new double-circuit 380-kV-overhead line in existing corridor Röhrsdorf-Remptendorf (103 km) | [10 empty] | under consideration | 2020 | Progresses as planned |  | 45
45 | 45. 207 | Substations in South-Western part of 5 Hertz Transmission control area (DE) |  | Construction of new 380kV substation in Southern Magdeburg area and restructuring of existing 220kV equipment. total length: aprox .50 km | [10 empty] | planned | long term | Some of the investments are to be commissioned by the mid term and the some by long term. |  | 45
45 | 45. 208 | Lines and Substations in South-Western part of 5 Hertz Transmission control area (DE) |  | Construction of new 380kV double-circuit OHL in existing corridor Pulgar-Vieselbach (103 km) Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015/2020 | Progresses as planned |  | 45
45 | 45. 209 | Substations in 5 Hertz Transmission control area |  | Extension of existing and erection of new 380 kV-substations and several 380/110kV-substations, incl. reactive power compensation devices. | [10 empty] | design & permitting | mid term | This investment includes several substations in the control area of 50Hertz Transmission control area. Present status varies form design & permitting, planning to under consideration and the date of commissioning varies from short/mid to long term. |  | 45
| 45. A163 | Wolmirstedt (DE) | Wahle (DE) | New double circuit OHL 380 kV; Line length 111 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A164 | Vieselbach (DE) | Mecklar (DE) | New double circuit OHL 400 kV line in existing OHL corridor . (129 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A165 | Mecklar (DE) | Grafenrheinfeld (DE) | New double circuit OHL 400-kV-line (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A166 | Altenfeld (DE) | Grafenrheinfeld (DE) | New double circuit OHL 400-kV-line (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A169 | Grafenrheinfeld (DE) | Grossgartach (DE) | Additional 380 Kv circuit on a existing lines. Length: 160 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A167 | Redwitz (DE) | Schwandorf (DE) | New double circuit OHL 400 kV line in existing OHL corridor Redwitz-Mechlenreuth-Etzenricht-Schwandorf (185 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A168 | Raitersaich (DE) | Isar (DE) | New 400 kV line in existing OHL corridor Raitersaich - Ludersheim - Sittling - Isar (160 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
45 | 45. 153 | Redwitz (DE) | Grafenrheinfeld (DE) | Upgrade of 230kV connection Redwitz - Grafenrheinfeld to 400kV, including new 400kV switchgear Eltmann. Line length: 97km. | [10 empty] | design & permitting | mid term | Investment delay due to delay in the implementation of the line Halle-Schweinfurt(investment 45. 193) |  | 45
45 | 45. 154 | Redwitz (DE) |  | New 500 MVAr SVC in substation Redwitz. | [10 empty] | planned | mid term | Progresses as planned |  | 45
45 | 45. 155 | Raitersaich (DE) |  | New 500 MVAr SVC in substation Raitersaich. | [10 empty] | planned | mid term | Progresses as planned |  | 45
45 | 45. 47. 158 | [15 empty] | 0 | The investment contributes both to project 45 and project 47. For the technical description see project 47. | 45
46 | 46. 194 | wind farm cluster Baltic Sea East (DE) | Lüdershagen/ Lubmin (DE) | Offshore wind farm connection project (by AC-cables on transmission voltage level or by clustering with DC connections) has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. | >2000 | 4 | 1 | [6 empty] | 1 | design & permitting | 2012-2020 | This investment includes several connections of offshore wind farms in the eastern part of the Baltic Sea. The present expected date of commissioning varies from 2012 to 2020. |  | The integration of offshore wind generation in the Baltic Sea.
46 | 46. 195 | wind farm cluster Baltic Sea West (DE) | Bentwisch (DE) | Offshore wind farm connection project (by AC-cables on transmission voltage level or by clustering with DC connections) has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. | [10 empty] | design & permitting | 2013-2020 | This investment includes several connections of offshore wind farms in the western part of the Baltic Sea. The present expected date of commissioning varies from 2013 to 2020. |  | 46
47 | 47. A76 | Vöhringen / Leupolz (DE) | Westtirol (AT) | Upgrade of an existing OHL to 380 kV, extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. Transmissions routs Vöhringen - Westtirol and Pkt. Woringen - Memmingen. Length: 114 km. This project will increase the current power exchange capacity between the DE, AT and CH. | >2000 | 1 | 2 | [6 empty] | 3 | planned | long term | New investment in TYNDP |  | The reinforcement of the interconnection between Austria and Germany. Also the support the interaction between the RES in Northern Europe(mainly DE) with the pump storage in the Austrian Alps. The project scheduling is not related only to the network needs, but even to the feasibility and to the authorization process (the possibility to anticipate specific projects could be evaluated in the future considering the three above mentioned elements).
47 | 47. 158 | Irsching (DE) | Ottenhofen (DE) | Upgrade of 230kV connection Irsching - Ottenhofen to 400kV, including new 400kV switchgear Zolling. Length 76km. | [10 empty] | planned | mid term | Progresses as planned | The investment contributes also to project 45. | 47
47 | 47. 212 | Isar / Ottenhofen (DE) | St. Peter (AT) | New 400kV double circuit OHL Isar - St. Peter including new 400kV switchgears Altheim, Simbach and St. Peter, and one new 400/230kV transformer in substation Altheim and fourth circuit on line Isar - Ottenhofen. Line length: 90km. | [10 empty] | design & permitting | 2017 | Progresses as planned |  | 47
47 | 47. 26. 216 | St. Peter (AT) | Tauern (AT) | Completion of the 380kV-line St. Peter - Tauern. This contains an upgrade of the existing 380kV-line St. Peter - Salzburg from 220kV-operation to 380kV-operation and the erection of a new internal double circuit 380kV-line connecting the substations Salzburg and Tauern (replacement of existing 220kV-lines on optimized routes). Moreover the erection of the new substations Wagenham and Pongau and the integration of the substations Salzburg and Kaprun is planned. Line length: 130km. | [10 empty] | design & permitting | 2017/2019 | Preparation for the permitting procedure is ongoing. APG is making efforts to set the 380-kV-Salzburg-line 2017 into service. Depending on possible delays during the permitting procedure the commissioning is expected between 2017 and 2019 | The investment contributes also to project 26. | 47
47 | 47. 26. 218 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 47
47 | 47. 219 | Westtirol (AT) | Zell-Ziller (AT) | Upgrade of the existing 220kV-line Westtirol - Zell-Ziller and erection of additional 220/380kV-Transformers. Line length: 105km. | [10 empty] | partly under construction | 2013-2020 | Project consists of several measures and is on schedule |  | 47
47 | 47. 26. 220 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 47
47 | 47. 221 | St. Peter (AT) | Ernsthofen (AT) | Upgrade from 220kV-operation to 380kV and erection of a 380kV-Substation in Ernsthofen and St. Peter. | [10 empty] | under construction | 2013 | The project is on schedule. Permissions are obtained. Commissioning is expected for 2013 |  | 47
58 | 58. 353 | Krajnik (PL) | Baczyna (PL) | Construction of a new double circuit 400kV OHL Krajnik - Baczyna (2x1870 MVA, 91km); single circuit temporarily working at 220kV on Krajnik - Gorzów part + New substation 400kV Baczyna will be connected by splitting and extending existing line Krajnik-Plewiska + Upgrading of limitations line Krajnik - Plewiska. | >1000 | 1 | 2 | [6 empty] | 2 | planned | 2020 | Progresses as planned |  | Bridge – third interconnection between Poland and Germany.
58 | 58. 355 | Mikułowa (PL) | Świebodzice (PL) | Double circuit line 220kV Mikułowa-Świebodzice will be upgraded to 400kV - single circuit temporarily working at 220kV. | [10 empty] | planned | 2020 | Progresses as planned |  | 58
58 | 58. A67 | Gubin (PL) |  | New 400 kV substation planned near the PL-DE border. The substation will be connected to planned line Eisenhüttenstadt (DE) - Plewiska (PL) creating new lines Eisenhüttenstadt (DE) - Gubin (PL) and Gubin (PL) - Plewiska (PL). | [10 empty] | planned | 2020 | New investment in TYNDP | This new substation on the third DE-PL connection is necessary for future generation connection while ensuring interconnection capability. | 58
58 | 58. 140 | Eisenhüttenstadt (DE) | Plewiska (PL) | New 400kV double circuit OHL Eisenhüttenstadt (DE) - Plewiska (PL) including the construction of new substation Plewiska Bis (PL) | [10 empty] | planned | 2020 | Progresses as planned |  | 58
88 | 88. A23 | offshore wind farms (FR) | several French substations (FR) | Subsea cables and substations works | 3000(MT) 6000 (LT) | 4 | 1 | [6 empty] | 3 | planned | 2015-2020 | New investment in TYNDP, required to connect offshore wind farms as decided by the French government in 2010 | Project development will adapt to the pace of generation installation | Connection of 6 GW offshore wind farms in 2 phases. First 3 GW phase in progress (tender).
89 | 89. A24 | Calan (FR) | Plaine-Haute (FR) | New 80km double circuit 220kV underground cable with 2 phase shifters and T-connection of an existing HV substation; 1150 MVARs of capacitors and SVC; new transformer 400/220kV | 500 MW | 2 | 4 | Brittany area | [5 empty] | 1 | design & permitting | 2017 | New investment in TYNDP, required to secure Brittany's supply, along with DSM management plan and a new CCGT in Finistère area. |  | This project is necessary to security Brittany's supply.
90 | 90. 131 | Bickigen (CH) |  | Addition of a second 400/220kV transformer in an existing substation. | 4000 | 1 | 2 | [6 empty] | 3 | design & permitting | 2012 | Progresses as planned |  | This project increase the transfer capability between FR, DE , AT towards pump storage in CH.
90 | 90. 132 | Mühleberg (CH) |  | Construction of a new 400/220kV substation. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 90
90 | 90. 134 | Bassecourt (CH) | Romanel (CH) | Construction of different new 400kV line sections and voltage upgrade of existing 225kV lines into 400kV lines. Total length: 140km. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 90
90 | 90. 136 | Area of Bodensee (DE, AT, CH) |  | Construction of new lines, extension of existing ones in direction of 400/220/110kV-substation. This project will increase the current power exchange capacity between the DE, AT and CH. The project is expected to increase NTC and Improved the security of supply. | [10 empty] | planned | long term | Progress as planned |  | 90
90 | 90. 129 | Beznau (CH) | Mettlen (CH) | Upgrade of the existing 65km double circuit 220kV OHL to 400kV. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 90
90 | 90. 130 | La Punt (CH) | Pradella / Ova Spin (CH) | Installation of the second circuit on existing towers of a double-circuit 400kV OHL (50km). | [10 empty] | planned | 2017 | Delays due to authorization process. |  | 90
90 | 90. 133 | Bonaduz (CH) | Mettlen (CH) | Upgrade of the existing 180km double circuit 220kV OHL into 400kV. | [10 empty] | under consideration | 2020 | Progresses as planned |  | 90
90 | 90. 44. 170 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 172 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 173 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 176 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 45. 177 | Goldshöfe (DE) | Bünzwangen (DE) | A new 380kV OHL. Length: 45km. | [10 empty] | under consideration | 2020 | Progresses as planned | The investment contributes also to project 45. | 90
91 | 91. 121 | Bickigen (CH) | Romanel (CH) | Construction of different new 400kV OHL sections and voltage upgrade of existing 225kV lines into 400kV lines. Total length: 250km. | >4000 | 4 | 1 | [6 empty] | 2 | design & permitting | 2015 | Delays due to authorization process. |  | The investments help accommodating new pumping storage units which support mainly the increasing RES generation in North Sea area.
91 | 91. 122 | Chippis (CH) | Lavorgo (CH) | Construction of different new 400kV line sections and voltage upgrade of existing 225kV lines into 400kV. Total length: 120km. | [10 empty] | design & permitting | 2017 | Delays due to authorization process. |  | 91
91 | 91. 123 | Mettlen (CH) | Ulrichen (CH) | Construction of different new 400kV line sections and voltage upgrade of existing 225kV lines into 400kV lines. Total length: 90km. | [10 empty] | planned | 2019 | Delays due to authorization process. |  | 91
91 | 91. 125 | Schwanden (CH) | Limmern (CH) | New 400kV double circuit (OHL and underground cable) between Schwanden and Limmern. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 91
91 | 91. 126 | Golbia (CH) | Robbia (CH) | New 2x 400kV cable connection between Golbia and the Bernina line double circuit. | [10 empty] | under consideration | 2019 | Progresses as planned |  | 91
91 | 91. 127 | Magadino (CH) | Verzasca (CH) | Upgrade of existing 150kV line into 220kV line. | [10 empty] | under consideration | 2020 | Progresses as planned |  | 91
91 | 91. 128 | Bâtiaz (CH) | Nant de Drance (CH) | New 400kV double circuit OHL between Bâtiaz and Châtelard. New 2x 400kV cable connection between Châtelard and Nant de Drance. Total length: 22km. | [10 empty] | design & permitting | 2016 | Delays due to authorization process. |  | 91
92 | 92. 146 | Aachen/Düren region (DE) | Lixhe (BE) | Connection between Germany and Belgium including new 100km HVDC underground cable and extension of existing 380kV-substations. On Belgian side, new 380 kV circuit between Lixhe and Herderen and second 380 kV overheadline in/out from Herderen to Lixhe. In Belgium, addition of 2 transformers 380/150 kV in Lixhe and in Limburg part; | 1000 | 3 | 2 | Northern Belgium | [5 empty] | 2 | design & permitting | 2017 | The project entered design and permitting phase in 2011, technical description has been completed and expected date of comissioning is 2017 | Alegro Project | First Belgium-Germany interconnection. This project enhances security of supply of both BE and DE. This HVDC link in an AC grid brings flexibility and bidirectional power control allowing integration of RES in both countries. This project aims to be a demonstration for HVDC link integration in the AC meshed grid.
94 | 94. 139 | Vierraden (DE) | Krajnik (PL) | Upgrade of existing 220 kV line Vierraden-Krajnik to double circuit 400 kV OHL. | >1000 | 1 | 2 | [6 empty] | 1 | design & permitting | long term | Expected date of commissioning was adjusted due to long permitting process and strong local public resistance. |  | PSTs – Control of the transits of power on the polish synchronous profile (increase of import capacity, increase of grid operation safety).
94 | 94. A68 | Krajnik (PL) |  | Upgrade 400 kV | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A69 | Mikułowa (PL) |  | Upgrade 400 kV | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A70 | Krajnik (PL) |  | New PST | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A71 | Mikułowa (PL) |  | New PST | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
103 | 103. 145 | Niederrhein (DE) | Doetinchem (NL) | New 400kV line double circuit DE-NL interconnection line. Length:60km. | 13900 | 3 | 1 | NW part of Netherlands | [5 empty] | 3 | design & permitting | >=2013 | Delays due to authorization process. |  | The project reinforces the Dutch grid to accommodate new conventional and renewable generation, to handle new flow patterns and to increase the interconnection capacity between DE and NL"
103 | 103. 438 | Eemshaven (NL) | Diemen (NL) | New 175-200km AC overhead line with capacity of 2x2650 MVA of 380kV. | [10 empty] | design & permitting | 2018 | Delays due to authorization process. |  | 103
103 | 103. 439 | Borssele (NL) | Geertruidenberg (NL) | New 100-130km double-circuit 380kV OHL with 2x2650 MVA capacity. | [10 empty] | design & permitting | 2016 | Delays due to authorization process. |  | 103
103 | 103. 440 | Maasvlakte (NL) | Beverwijk (NL) | New 380 kV double-circuit mixed project (OHL+ underground cable) including approximately 20km of underground cable for 2650 MVA. The cable sections are a pilot project. The total length of cable at 380kV is frozen until more experience is gained. | [10 empty] | under construction | 2016 | Delays due to authorization process. |  | 103
103 | 103. 441 | Zwolle (NL) | Hengelo (NL) | Upgrade of the capacity of the existing 60km double circuit 380kV OHL to reach a capacity of 2x2650 MVA. | [10 empty] | under consideration | long term | Progresses as planned. |  | 103
103 | 103. 442 | Krimpen aan de Ijssel (NL) | Maasbracht (NL) | Upgrade of the capacity of the existing 150km double circuit 380kV OHL to reach a capacity of 2x2650 MVA. | [10 empty] | under consideration | long term | Progresses as planned. |  | 103
107 | 107. A25 | tbd (IE) | tbd (FR) | A new HVDC subsea connection between Ireland and France | 700-1000 | 3 | 2 | [6 empty] | 3 | under consideration | long term | New investment in TYNDP, conceptual, cost benefit analysis to be confirmed |  | This project will establish interconnection capacity between Ireland and France
112 | 112. 98 | Pordenone (IT) |  | Voltage upgrade of the existing Pordenone 220kV substation up to 400kV. The substation will be connected in and out to the existing Udine O. – Cordignano 400kV line. | 2150 | 2 | 5 | Triveneto area | [5 empty] | 1 | planned | long term | Progresses as planned |  | This projects helps to increase the security of supply in the N-E part of Italy.
112 | 112. 105 | Treviso (IT) |  | New 380/132kV substation in Treviso area, connected in and out to the existing 380kV line “Sandrigo - Cordignano". | [10 empty] | design & permitting | mid term | Project delayed by 2 years due to longer than expected permitting procedure. |  | 112
112 | 112. 106 | Schio (IT) |  | New 220/132kV substation in Schio area, providing the connection in and out to the existing 220kV line "Ala-Vicenza Monte Viale”. | [10 empty] | planned | mid term | Project delayed by 2 years due to longer than expected permitting procedure. |  | 112
112 | 112. 107 | Vicenza Industrial (IT) |  | New 380/132kV substation in the industrial area of Vicenza, connected in and out to the existing Sandrigo-Dugale 400kV line. | [10 empty] | planned | long term | Progresses as planned |  | 112
112 | 112. 108 | North West Padova (IT) |  | New 220/132kV substation in North West Padova area, complying with 400kV standards, providing the connection in and out to the existing Dugale-Marghera Substation1 220kV line. | [10 empty] | planned | long term | Progresses as planned |  | 112
| 40 | Avelin (FR) Mastaing (FR) |  | Installation of a 3rd busbar in Avelin (existing 400-kV substation) & replacement of components to increase the ability to withstand short-circuit power; Connection of Mastaing (existing 400kV substation) to existing 400kV circuit between Avelin (FR) & Lonny (FR) | [10 empty] | commissioned | commissioned | Commissioned
| 41 | Fruges, Sud-Aveyron, Marne-Sud, Somme (FR) |  | New 400-kV substations connected to existing 400-kV network and equipped with transformers to 220 kV or high voltage networks | [10 empty] | design & permitting | mid term | Project progress according to the plan
| 58 | Ensdorf (DE) | St. Avold (FR) | Change of conductors on the German part of this single circuit 220kV line (9 km) and installation of a phase-shifter in Ensdorf (DE) 220kV substation. | [10 empty] | commissioned | commissioned | Commissioned
| 69 | Candia (IT) | Konjsko (HR) | New 1000MW HVDC interconnection line between Italy and Croatia via 280km 500kVDC subsea cable and converters stations at both ending points. | [10 empty] | under consideration | post 2022 | These incestments are very sensitive to the market and still under investigation
| 71 | Brindisi (IT) | Babica (AL) | 500MW single pole HVDC Merchant Line between Italy and Albania via 290km 400kV DC subsea cable and converter stations at both ends. On the Italian side, the new line will be connected to the existing substation of Brindisi South. | [10 empty] | design & permitting | long term | Permitted as a merchant line (it develops according to the plan of the stakeholders)
| 72 | Aetos(GR) | Galatina (IT) | Second 500MW HVDC link between Greece and Italy via 316km 400kVDC subsea cable and converters stations at both ends. | [10 empty] | under consideration | post 2022 | These incestments are very sensitive to the market and still under investigation
| 120 | Lavorgo (CH) | Morbegno (IT) | New 400kV tie line between Italy and Switzerland. | [10 empty] | cancelled | cancelled | It has been replaces by investment n° ITA-4 "New interconnection between CH and IT"- change in the design and complexity of the project
| 135 | 22 kV nodes (CH) |  | Many 220kV reinforcement around the urban areas. | [10 empty] | planned | 2015 | Progress according to the plan
| 168 | Goldshöfe (DE) | Dellmensigen (DE) | Upgrade the line Goldshöfe - Dellmensigen from 220kV to 380kV . Line length:114km. Included with the project : 3x 380kV substations, 2 transformers. | [10 empty] | under construction | 2014 | Investment 168 has been postponed to 2014 due to local resistance against the project in a specific area. The rest of the investment is ready.
| 168a | Region South-West Bavaria (DE) |  | Upgrading the existing 220kV OHL to 380kV,length 100km and the extension of existing substations, erection of 380/110kV-transformers. | [10 empty] | cancelled | cancelled | The project was abandoned - was not seen necessary with the new set of projects in place. Note: in the previous TYNDP the status of the project was under consideration and not planned (printing mistake)
| 192 | Hamburg/Krümmel (DE) | Schwerin (DE) | This 380kV double-circuit OHL project will close the missing gap in North-East German grid infrastructure. Only 65km of new line must be constructed, 22km already exist. | [10 empty] | under construction | 2012/2013 | Commissioning delayed by complex permitting procedure, line is partly constructed, is expected to be commissioned in 2012/2013 short term
| 198 | Wuhlheide (DE) | Thyrow (DE) | Berlin South Ring: replacement of an existing old 220kV double-circuit OHL by a 380kV double-circuit OHL. Length: 50km. | [10 empty] | cancelled | cancelled | Project was depending on the replacement of a CHP power plant based in Berlin, due to a new general CHP-concept the plant size could be adopted and the upgrade of the existing 220-kV connection to 380-kV was not necessary any longer, project was given up with regard to the CHP-Plant investor
| 222 | Silz (AT) | Zell-Ziller (AT) | Upgrade of the existing 220kV-double circuit- OHL Zell-Ziller - Silz. Line length: 42km. | [10 empty] | under construction | 2013/2014 | Progress as planned | This line, due to change in, switched from the TSO environment to the distribution area.
| 267 | Suceava (RO) | Balti (MD) | New 400 kV OHL (139 km) to increase capacity of transfer between Romania and Republic Moldova. The project also implies new substation 400 kV in Moldova (extension of the substation Balti (MD) with 400 kV level). | [10 empty] | design & permitting | 2020 | The project. is associated to the connection of the Rep. Moldova and Ukraine. Delay is associated to the procedure for the connection of UA+MD.
| 268 | Constanta (RO) | Pasakoy (TR) | New DC link (subsea cable) between existing stations in RO and TR. Line length: 400km. | [10 empty] | under consideration | >2020 | The delay in the investment is caused by the lack of financial means.
| 65 | Curon (IT)/ Glorenza (IT) | New substation close to the border in AT | New 380/220kV substation in AT directly located near the border ; erection of a 24km single circuit 220kV-connection via OHL and underground cable till Graun (IT) and upgrade of the existing line Graun (IT) – Glorenza (IT). | [10 empty] | cancelled | cancelled | It has been replaces by investment n° ITA-5 "New interconnection between AT and IT", This project which was depicted in the TYNDP2010 suffered important changes in the design.
| 203 | Area Wolmirstedt(DE) | under consideration | Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | under consideration | 2020 | Included in new investment H3 due to new wind BS generation
| 78 | Palermo area (IT) |  | Restructuring of the network in the Palermo area. The work consists of a new 220/150kV substation, complying with 400kV standards, connected to the Ciminna substation with a new 400kV line and in & out the existing Bellolampo-Caracoli 400kV line, and also the connection of 15 kV lines "Casuzze - Monreale" and "Casuzze - Guadalami" and a repowering of the existing Casuzze 150/MV substation. It is foreseen also large a restructuring of the 150kV network in the palermo area in order to increase the security and the quality of supply. Total length: 49 km. | [10 empty] | design & permitting | 2015 | The project has changed in terms of composition (new refurbishments were added to the initial project). The date of commissioning was advanced due to the faster need of increasing the security of Palormo area.
| 79 | Agrigento (IT) |  | New 220/150kV substation, complying with 400kV standards. The new substation will be connected in and out to the existing Partanna-Favara 400kV line . | [10 empty] | design & permitting | 2015 | The authorization process is faster than expected..
| 80 | Noto (IT) |  | New 220/150kV substation, complying with 400kV standards, connected in and out to the existing Ragusa-Melilli 400kV line. | [10 empty] | design & permitting | 2014/2015 | The authorization process is faster than expected..
| 110 | Restructuring of Sorrento Peninsula network (IT) |  | It is planned a new 380/220/150kV substation in East Vesuvius area (near Naples) connected in and out to the existing 380 and 220kV lines “Montecorvino-S. Sofia” and "Nola-S. Valentino". Related to this project, it has been programmed also some reinforcements and restructuring of the existing 220kV and 150 kV network in the area of Sorrento Peninsula. Total net length: 58km. | [10 empty] | design & permitting | 2014 | Shifted from Long Term to 2014 due to the authorization process which started a little bit before the scheduled time.
| 119 | Capri, Ischia, Procida (IT) |  | New 150kV subsea connection between the Capri, Ischia and Procida islands to the existing substations of Cuma and Torre Annunziata (mainland Italy). Total length : 95km. | [10 empty] | design & permitting | 2014 | Delays due to authorization process.
| 118 | Porto Ferraio (Elba Island) | Cornia (Piombino) | New 40km 132kV connection via subsea cable between the existing substation of Porto Ferraio and the future 400/132kV substation of Cornia that will also be connected in and out to the existing Suvereto-Piombino Termica 400kV line. | [10 empty] | design & permitting | 2012/long term | Delays due to authorization process.
| 180 | Mengede (DE) | Kruckel (DE) | Installation of a second circuit 380kV OHL and extension of existing substations. Line length:16km. | [10 empty] | design & permitting | mid term | project develops according to the plan
| 217 | Dürnrohr (AT) | Sarasdorf (AT) | Installation of the 3rd and 4th circuit on the existing line Dürnrohr - Sarasdorf and restructuring in the area of the substation Bisamberg and the 220kV-Weinviertel-line . Total length: 100km. | [10 empty] | under construction | 2014 | The project is on schedule. Permissions are obtained. Commissioning is expected for 2014
| 52 | Feuillane (FR) | Realtor (FR) | Operation at 400 kV of existing 63km double circuit OHL previously operated at 220kV, creation of a new 400 kV substation and restructuration of the existing 220 kV local network | [10 empty] | under construction | 2012 | To be commissioned by end 2012 - delays due to longer than expected authorization process
| 61 | Moulaine (FR) | Belval (LU) | Connection of SOTEL (industrial grid in LU) to RTE network by mixed (underground cable & OHL) single circuit 220kV line. Parts of the new line use existing ones. | [10 empty] | under construction | short term | Commissioned in 2010 for the French part, the LU part is still pending
| 39 | Avelin (FR) | Warande (FR) | Reconductoring (with ACSS) of both circuits of existing 400kV OHL between Avelin, Weppes & Warande. Total length : 85km | [10 empty] | commissioned | commissioned | Commissioned in 2010
| 43 | Mandarins (FR) |  | Replacement of thyristors in the AC/DC substation (IFA 2000 interconnector, DC voltage 270 kV) | [10 empty] | commissioned | commissioned | Currently under final tests. Will be commissioned in Summer 2012.
| 47 | Tamareau (FR) | Tavel (FR) | Reconductoring with ACCS of both circuits of existing 92km double circuit 400kV OHL to increase its capacity. | [10 empty] | commissioned | commissioned | Commissioned in 2011
| 49 | Cantegrit (FR) | Mouguerre (FR) | Reconductoring (with ACSS) of existing 83km single-circuit 220kV OHL to increase its capacity. | [10 empty] | commissioned | commissioned | Commissioned in 2011
| 50 | Néoules (FR) | Broc-Carros (FR) | The second circuit (formerly operated at 220kV) of a 197km double-circuit 400kV OHL will be operated at 400kV and 400/225 autotransformers installed in relevant substations. | [10 empty] | commissioned | commissioned | Commissioned in 2010
| 56 | Camporosso (IT) |  | New 450 MVA PST in Camporosso (IT) 220kV substation on Camporosso (IT) - Menton (FR) - Trinité-Victor (FR) OHL. | [10 empty] | under construction | 2012 | will be commissioned in 2012
| 59 | Moulaine (FR) | Aubange (BE) | Installation of a second circuit on the existing 220kV cross-border OHL | [10 empty] | commissioned | commissioned | Commissioned in 2010
| 114 | Ittiri (IT) | Codrongianos (IT) | New 18km 400kV OHL between the existing substation of Codrongianos and the future 400kV substation of Ittiri that will be also connected in and out to the existing Fiumesanto-Selargius 400kV line. | [10 empty] | commissioned | commissioned | Commissioned
| 115 | Fiumesanto (IT) | Latina (IT) | Second pole of HVDC link between Sardinia and mainland Italy via 400kV DC subsea cable (420km). The first pole is in operation since 2009. Total capacity of the bipolar link: 1000MW. | [10 empty] | commissioned | commissioned | Commissioned
| 116 | Casellina (IT) | Tavarnuzze (IT) | New 37km 400kV OHL with rearrangement of EHV grid in the area between Casellina and S. Barbara. Voltage upgrade of the existing substations of Casellina400/132kV and S. Barbara400/132kV. | [10 empty] | commissioned | commissioned | Commissioned
| 117 | Castegnero (IT) |  | New 220/132kV substation connected in and out to the existing 220kV line “Cittadella – Este” and “Dugale – Stazione 1”, providing a restructuring of HV grid. | [10 empty] | commissioned | commissioned | Commissioned
| 169 | Großgartach (DE) |  | Upgrade the substation for a higher short circuit capacity. New installation includes 10 gas insulated bays, 63 kA, 3 bus-bar and 2 transformers. | [10 empty] | commissioned | commissioned | Commissioned
| 201 | Bärwalde (DE) | Schmölln (DE) | New internal double circuit 380kV-line connecting the substations St. Peter and Salzach new (replacement of the existing 220kV-line). Length: 46km. | [10 empty] | design & permitting | 2014 | Delays due to authorization process.
| 196 | wind farm Baltic 1 (DE) | Bentwisch (DE) | Connection of the offshore wind farm Baltic 1 (AC-cables on transmission voltage level). | [10 empty] | commissioned | commissioned | Commissioned
| 210 | Substations in 5 Hertz Transmission control area |  | Construction of new 380/110kV substations. | [10 empty] | commissioned | commissioned | Freiberg and Stendal/West are commissioned. The remaining substations were transferred to the 44. 209 investment.
| 213 | Wien SO (AT) | Szombathely (HU) | Installation of the 2nd circuit on the existing interconnection from Wien SO (AT, APG) to the border (both circuits have already been installed on the Hungarian side, one is connected to Györ and the 2nd circuit to Szombathely). Line length: 63km. | [10 empty] | commissioned | commissioned | 2011->2010: Completed earlier. It was due to scheduling of the field work.
| 215 | St. Peter (AT) | Salzach neu (AT) | New internal double circuit 380kV-line connecting the substations St. Peter and Salzach neu (replacement of the existing 220kV-line). Length: 46km. | [10 empty] | commissioned | commissioned | Commissioned
| 226 | Ernestinovo (HR) | Pecs (HU) | New 400kV double circuit interconnection line between existing stations. Line length: 86km. | [10 empty] | commissioned | commissioned | Commissioned
| 67 | Divaca (SI) |  | Installation of a new 400kV PST to assist control of power flows to Italy on secure level and secure the operation of Slovenian grid enabling full utilization of regional market. | [10 empty] | commissioned | commissioned | This is PST in SS Divaca and it has been is in operation since 2011.
| 82 | Chignolo Po (IT) | Maleo (IT) | A new 380kV double circuit OHL between the new 380kV substations of Chignolo Po and Maleo in Lodi area. Restructuring of HV network. Total line length: 22km. | [10 empty] | commissioned | commissioned | Commissioned
| A104 | Castelbello (IT) | Naturno (IT) | New 220 kV (insulated at 400 kV level) OHL connection between existing stations of Naturno and Castelbello. | [10 empty] | planned | long term | Overcoming the constrains in operation, due the renewable generation in the area of Trentino Alto Adige region.

## CSE report
5 July 2012
TYDNP 2012 package - Table of projects Continental South East Regional Group Investment Plan
Project identification |  |  |  |  | Project assessment
Project number | Investment number | Substation 1 | Substation 2 | Brief technical description | Grid Transfer Capability Increase [MW] | Socio-economic Welfare | RES integration | Improved Security of Supply | Losses variation | CO2 mitigation | Technical resilience | Flexibility | Social and environmental Impact | Project costs | Present status | Expected date of commissioning | Evolution compared to the TYNDP 2010 situation | Investment comment | Project comment
21 | 21. 54 | Cornier (FR) | Piossasco (IT) | Replacement of conductors (by ACCS) on Albertville (FR) - Montagny (FR) - Cornier (FR) and Albertville (FR) - La Coche (FR) - La Praz (FR) - Villarodin (FR) - Venaus (IT) - Piossasco (IT) single circuit 400kV OHLs. In addition, change of conductors and operation at 400kV of an existing single circuit OHL between Grande Ile and Albertville (FR) currently operated at lower voltage, and associated works in Albertville (FR) 400kV substation. (Total length of lines : 257 km) | 1800 from FR to IT, (600 in the MT) | 1 | 5 | [6 empty] | 3 | under construction | 2012/2013 | Mainly progresses as planned although the works on existing lines take slightly longer than initially thought |  | Planned France-Italy interconnection development
21 | 21. 55 | Grande Ile (FR) | Piossasco (IT) | "Savoie - Piémont" Project : New 190km HVDC (VSC) interconnection FR-IT via underground cable and converter stations at both ends (two poles, each of them with 600MW capacity). The cables will be laid in the security gallery of the Frejus motorway tunnel and possibly also along the existing motorways' right-of-way. | [10 empty] | design & permitting | 2017/2018 | Progresses as planned |  | 21
21 | 21. 81 | Trino (IT) | Lacchiarella (IT) | A new 380kV double circuit OHL between the existing 380kV substations of Trino and Lacchiarella in North West Italy area. Total line length: 95km, Voltage upgrade of the existing Magenta 220/132kV substation up to 380kV. | [10 empty] | under construction | 2013 | Authorization process ended, construction phase on going |  | 21
21 | 21. 84 | Casanova (IT) | Vignole (IT) | Voltage upgrade of the existing 100km Casanova-Vignole 220kV OHL to 400kV and new 400/220/150kV substation in Asti area. | [10 empty] | design & permitting | long term | Delays due to authorization process. |  | 21
21 | 21. 101 | Turin (IT) |  | Restructuring of the 220kV network in the urban area of Turin. Some new 220kV cables, some new 220/132kV substations and some reinforcements of existing assets are planned. Total length: 63km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 21
26 | 26. 63 | Lienz (AT) | Veneto region (IT) | The project foresees the reconstruction of the existing 220kV-interconnection line as 380kV-line on an optimized route to minimize the environmental impact. Total length should be in the range of 100-150km. | 750 | 3 | 2 | [6 empty] | 3 | planned | long term | Progresses as planned |  | Reinforcement of the interconnection between Italy and Austria. Also the support the interaction between the RES in mainly Italy with the pump storage in the Austrian Alps.
26 | 26. 220 | Lienz (AT) |  | Erection of a new 220/220kV- PST in the substation Lienz (AT). | [10 empty] | under construction | 2012 | Project is in errecion and expected to be commissioned 2012 according to the schedule | The investment contributes also to project 47. | 26
26 | 26. 47. 216 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 26
26 | 26. 64 | Bressanone (IT) | New substation near Innsbruck (AT) | New double circuit 400kV interconnection through the pilot tunnel of the planned Brenner Base Tunnel. Total line length: 65km. | [10 empty] | under consideration | >2022 | Progresses as planned |  | 26
26 | 26. 66 | Prati di Vizze (IT) | Steinach (AT) | Upgrade of the existing 44km Prati di Vizze (IT) – Steinach (AT) single circuit 110/132kV OHL, currently operated at medium voltage and installing a 110kV/132kV PST. | [10 empty] | design & permitting | mid term | Investment delayed with 2 years due to the permitting process |  | 26
26 | 26. 83 | Volpago (IT) | North Venezia (IT) | Realization of a new 380kV line between the existing substation of North Venezia and the future 380kV substation of Volpago, connected in and out to the 380kV "Sandrigo - Cordignano” . Total line length: 31km. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 26
26 | 26. 93 | Dolo (IT) | Camin (IT) | New 15km double circuit 400kV OHL between existing Dolo and Camin 400kV substations, to be built in parallel with the existing line. | [10 empty] | under construction | 2014 | Authorization process ended, construction phase on going |  | 26
26 | 26. 97 | Polpet (IT) |  | Voltage upgrade of the existing Polpet 150kV/medium voltage substation up to 220kV, complying with 400kV standards. The substation will be connected by two shorts links to the existing Soverzene-Lienz 220kV line. | [10 empty] | design & permitting | 2015 | Authorization process started, project phase on going |  | 26
26 | 26. 218 | Obersielach (AT) | Lienz (AT) | New 190km 380kV OHL connecting the substations Lienz (AT) and Obersielach (AT) to close the Austrian 380kV-Ring in the southern grid area. Line length: 190km. | [10 empty] | under consideration | long term | Progresses as planned | The investment contributes also to project 47. | 26
26 | 26. A102 | New interconnection between Italy and Austria |  | New possible interconnection line between Italy and Austria | [10 empty] | under consideration | long term | This investment replaces investment n°65 mentioned on TYNDP 2010. The previous investment evolved so much that it is substituted by a new project. Feasibility studies ongoing including internal reinforcements. |  | 26
27 | 27. 68 | Okroglo (SI) | Udine (IT) | New 120km double circuit 400kV OHL with installation of a PST in Okroglo. The thermal rating will be 1870 MVA per circuit. | >1800 | 1 | 3 | [6 empty] | 2 | planned | long term | Progresses as planned |  | This project increases the capacity between Slovenia - Italy and Slovenia - Hungary. Project will remove congestion and strengthen connection on North-South and East-West axis.
27 | 27. 92 | West Udine (IT) | Redipuglia (IT) | New 40km double circuit 400kV OHL between the existing substations of West Udine and Redipuglia, providing in and out connection to the future 400kV substation of South Udine. | [10 empty] | design & permitting | 2015 | The investment is delayed due to longer than expected authorization procedures. |  | 27
27 | 27. A96 | New interconnection between Italy and Slovenia |  | New interconnection between Italy and Slovenia | [10 empty] | under consideration | long term | Feasibility studies ongoing including the internal reinforcements. | Need for strengthening the connection between Slovenia and Italy and increasing of power exchange capability | 27
27 | 27. 223 | Cirkovce (SI) | Heviz (HU) Zerjavenec (HR) | The existing substation of Cirkovce (SI) will be connected to one circuit of the existing Heviz (HU) -Zerjavinec (HR) double circuit 400kV OHL by erecting a new 80km double circuit 400kV OHL in Slovenia. The project will result in two new cross-border circuits: Heviz (HU) - Cirkovce (SI) and Cirkovce (SI) - Žerjavenec (HR). | [10 empty] | design & permitting | 2016 | Presently in the authorization process. This investment was delayed due to permitting process. |  | 27
27 | 27. 224 | Krsko (SI) | Bericevo (SI) | New 400kV double circuit OHL. This project will strengthen connection between East and Central part of Slovenia and connect an internal loop. Line length: 80km. | [10 empty] | under construction | 2015 | Authorization process ended, construction phase is on going. This investment was delayed due to permitting process. |  | 27
27 | 27. 225 | Divaca (SI) | Cirkovce (SI) | Upgrading 220kV lines to 400kV in corridor Divaca-Klece-Bericevo-Podlog-Cirkovce. Line length: 193km. | [10 empty] | planned | long term | Progresses as planned |  | 27
27 | 27. A105 | Lika(HR) | Brinje(HR) | New 55km single circuit 400 kV OHL replacing aging 220 kV overhead line | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. A106 | Lika(HR) | Velebit(HR) | New 60km single circuit 400 kV OHL replacing aging 220 kV overhead line | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. A107 | Lika (HR) |  | New 400/110 kV substation, 2x300 MVA | [10 empty] | planned | 2017 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. A108 | Brinje (HR) |  | New 400/220 kV substation, 1x400 MVA | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. 229 | Plomin (HR) | Melina(HR) | New 90 km double circuit OHL, with two connecting substations and transformer 400/220 kV, 400 MVA | [10 empty] | design & permitting | >2016 | Project moved to long term, due to postponed commissioning date of thermal power plant Plomin |  | 27
27 | 27. 227 | Banja Luka (BA) | Lika (HR) | New 400kV interconnection line between BA and HR | [10 empty] | under consideration | 2020 | End points of OHL and commissioning date defined after bilateral HR-BA agreement |  | 27
28 | 28. 70 | Villanova (IT) | Lastva (ME) | New 1000MW HVDC interconnection line between Italy and Montenegro via 375km 500kV DC subsea cable and converter stations at both ending points. | 1000 | 1 | 2 | [6 empty] | 3 | under construction | 2015 | Authorization process ended, construction phase on going. The substations on the ME side has been changed. |  | It contributes significantly to the increase of GTC between the West Balkans and IT such contributing to market integration; complements the ME - IT cable
28 | 28. 86 | Foggia (IT) | Villanova (IT) | New 178km double circuit 400kV OHL between existing Foggia and Villanova 400kV substations, also connected in and out to the Larino and Gissi substations. A PST will be installed on the new 400kV line. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 28
28 | 28. 89 | Fano (IT) | Teramo (IT) | New 200km single circuit 400kV OHL between the existing 400kV substations of Fano and Teramo, providing the connection in and out to the future substation to be built in Macerata area. | [10 empty] | design & permitting | long term | The investment is delayed due to longer than expected authorization procedures. |  | 28
28 | 28. 232 | Visegrad (BA) | Pljevlja (ME) | New 70km single circuit 400kV OHL between Visegrad and Pljevlja | [10 empty] | planned | 2015 | Feasibility study for 400kV interconnections RS-ME-BA proposed under Infrastructure Projects Facility for Western Balkans |  | 28
28 | 28. 233a | Lastva (ME) |  | A new substation will be connected to the existing line 400kV Podgorica 2(ME)-Trebinje(BA), with two transformers 2X300MVA 400/110kV, and convertor station for the DC cable Lastva(Tivat)-Villanova (see 70). | [10 empty] | design & permitting | 2015 | Feasibility study covering the aspects of route planning, substation location, environmental and social issues and equipment selection is due to end in second half of 2011 |  | 28
28 | 28. 233b | Lastva (ME) | Pljevlja (ME) | New 160 km double circuit 400kV OHL existing substation Pljevlja and new substation Tivat. | [10 empty] | design & permitting | 2016 | Feasibility study covering the aspects of route planning, substation location, environmental and social issues and equipment selection is due to end in second half of 2011 |  | 28
28 | 28. A109 | Bajina Basta (RS) | Visegrad (BA) | New 400kV interconnection OHL between Serbia and BiH, and reconstruction of existing two OHL 220 kV between BiH and Serbia. | [10 empty] | planned | >2016 | New investment in TYNDP | New 400 kV overhead line between Serbia and BIH. It will eliminate constraints in the region for electric energy transits and exchange. | 28
28 | 28. A110 | Bajina Basta (RS) | TPP Obrenovac (RS) | New double circuit 400 kV OHL between new substation Bajina Basta (see infra), and substation Obrenovac | [10 empty] | design & permitting | >2016 | New investment in TYNDP | Obrenovac is the "strongest" 400 kV node in Serbia, thus providing significant upgrade for evacuation and energy transfer from north to south, and further down in Montenegro, through the new line between Bajina Basta and Pljevlja (ME) | 28
28 | 28. A111 | Bajina Basta (RS) | Pljevlja (ME) | New 86 km single circuit 400kV OHL connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS). | [10 empty] | planned | >2016 | New investment in TYNDP |  | 28
28 | 28. A112 | Bajina Basta (RS) |  | New 400/110 kV substation in Bajina Basta, upgrading an existing 220/110 kV substation. | [10 empty] | planned | >2016 | New investment in TYNDP |  | 28
28 | 28. A113 | Bistrica (RS) |  | New 220/110 kV substation | [10 empty] | design & permitting | 2015 | New investment in TYNDP | After a topology change in the area, the investment will eliminate firm connection in "Vardiste" (secure and stable operation in Serbian network and systems of Bosnia and Herzegovina and Montenegro), to eliminate constraints in the region for electric energy transits and exchange. | 28
28 | 28. A114 | Konjsko(HR) | Velebit(HR) | New 100km single circuit 400 kV OHL replacing ageing 220 kV overhead line | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 28
28 | 28. 231 | Konjsko(HR) |  | Installation of a 150MVAr reactive power device | [10 empty] | design & permitting | 2014 | Investment postponed 1 year due to permitting process |  | 28
28 | 28. A115 | Plat (HR) |  | New 220/110 kV substation | [10 empty] | under construction | 2013 | New investment in TYNDP, contributing to mesh the network surrounding HVDC link IT-ME and to increase the reliability of the EHV system |  | 28
28 | 28. 228 | Trebinhe(BA) | Plat(HR) | Re-establishment of two previously existing 220kV single circuit interconnection Trebinje(BA)-Plat(HR); Total length 10km. | [10 empty] | planned | 2014 | Progresses as planned |  | 28
29 | 29. 73 | El Aouaria (TU) | Partanna (IT) | New 350km 1000 MW HVDC line between Tunisia and Italy via Sicily with 400kV DC subsea cable and converters stations at both ends. | 1500 | 3 | 5 | [6 empty] | 2 | design & permitting | long term | The investment is delayed due to longer than expected authorization procedures. | This project will be realized in 2 steps. In the previous TYNDP just the first part of the investment was mentioned (500MW). | Interconnection between Italy and North Africa. Other interconnection projects between North Africa and Italy are still under investigation and under study
29 | 29. 76 | Partanna (IT) | Ciminna (IT) | New 65km single circuit 400kV OHL in Sicily between existing Partanna and Ciminna substations. | [10 empty] | planned | long term | Progresses as planned |  | 29
29 | 29. A97 | unknown (IT) | unknown (AL) | New interconnection between Italy and Algeria -new DC submarine cable | [10 empty] | under consideration | long term | New investment in TYNDP | Need for a new interconnection between Algeria and Italy and increasing of power exchange capability with North Africa frontier. feasibility study on going | 29
30 | 30. 74 | Chiaramonte Gulfi (IT) | Sorgente (IT) | Realization of 380kV ring grid, trough the construction of 3 new 380kV line: "Chiaramonte Gulfi - Ciminna", "Sorgente - Ciminna" and "Paternò - Priolo". It will be realized a new 380/150kV substation in Caltanissetta area and the voltage upgrade of the existing Ciminna substation up to 380kV. Total line length: 365km. New 380/150 kV substation in Sorgente area will be temporally connected in and out to the existing 400 line kV "Paterno - Sorgente" and to the local 220 kV and 150 kV network. | 1000 | 4 | 1 | Palermo, Catania, Agrigento and Messina area | [5 empty] | 3 | planned | 2016/long term | Feasibility studies carried out have led to adapt the schedule. |  | Sicilian 400kV transmission ring.
30 | 30. 75 | Sorgente (IT) | Rizziconi (IT) | New 90km double circuit 400kV line, partly via subsea cable and partly via OHL. This line is part of a larger project that foresees the creation of the future 400kV ring grid of Sicily. | [10 empty] | under construction | 2014 | Delays on construction phase |  | 30
30 | 30. 77 | Partinico (IT) | Fulgatore (IT) | New 45km single circuit 400kV OHL between Partinico and Fulgatore in Western Sicily. | [10 empty] | planned | 2016 | Feasibility studies carried out have led to adapt the schedule. |  | 30
30 | 30. 87 | Feroleto (IT) | Maida (IT) | New 400kV OHL across Calabria between the existing substation of Feroleto and the future substation of Maida, while restructuring the existing grid in North Calabria. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 30
30 | 30. A98 | Mineo (IT) |  | New 380/150 kV substation in Mineo area connected in and out to the existing 400 line kV "Chiaramonte Gulfi - Paterno" and to the local HV network. | [10 empty] | planned | long term | New investment in TYNDP | needed to overcome the expected congestions on the central-east HV network of Sicily affected by the flows of consistent production from renewable plants | 30
31 | 31. 85 | Pavia area (IT) | Piacenza area (IT) | New 45km double circuit 400kV OHL between 2 substations in the Pavia area and Piacenza. | >1000 | 3 | [7 empty] | 2 | planned | long term | Initial design partially changed, with new reinforcements and rearrangements activities on the neighboring areas resulting from further studies |  | Increase interconnection capability between IT and CH.
31 | 31. 95 | Mese (IT) |  | Voltage upgrade of the existing 220/132kV Mese substation up to 400kV. | [10 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 31
31 | 31. 99 | Avise (IT) | Chatillon (IT) | Voltage upgrade of the existing 40km Avise-Villeneuve-Chatillon single circuit 220kV OHL up to 400kV. | [10 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 31
31 | 31. 100 | Milan (IT) |  | Restructuring of the 220kV network in the urban area of Milan. Some new 220kV cables (33km), a new 220kV substation (Musocco) and some reinforcements of existing assets (35km) are planned. | [10 empty] | design & permitting | mid term | The cables in the Milan area are in operation, the appropriate substations are under construction and the reinforcements are under design and permitting. |  | 31
31 | 31. 103 | Brescia (IT) |  | New 400/132kV substation in South East area of Brescia, connected in and out to the existing Flero-Nave 400kVOHL, while restructuring the 132kV network. | [10 empty] | planned | mid term | Progresses as planned |  | 31
31 | 31. 112 | Tirano (IT) | Verderio(IT) | New 140km single circuit 400kV OHL between Tirano and Verderio substations connecting also the new 400kV substation Grosio/Piateda. | [10 empty] | planned | long term | Progresses as planned |  | 31
31 | 31. 124 | Mettlen (CH) | Airolo (CH) | Upgrade of existing 225kV OHL into 400kV. Line length: 90km. | [10 empty] | under consideration | 2020 | Progresses as planned |  | 31
31 | 31. A101 | New interconnections between Italy and Switzerland |  | Up to 4 interconnection projects are under discussion, one or two probably will be implemented | [10 empty] | under consideration | long term | This investment replaces investment n° 120 mentioned on TYNDP 2010. The previous investment evolved so much that it is substituted by a new project. Feasibility studies ongoing including the internal reinforcements. |  | 31
32 | 32. 88 | Montecorvino (IT) | Benevento (IT) | New 70km double circuit 400kV OHL between the existing 400kV substations of Montecorvino and Benevento II, providing in and out connection to the future substation to be build in Avellino North area, which will be also connected to the existing "Matera-S. Sofia" 400kV line. | 1900 | 4 | 1 | Naple urban area, Sorrento Penninsul, minor Campania islands and Tirrenic South coast Italy | [5 empty] | 3 | design & permitting | mid term | The Avelino substation is under construction, the line is in delay due to authorization process. |  | Reinforcement between South and Central-South of Italy to accommodate increasing market flows.
32 | 32. 91 | Foggia (IT) | Benevento II (IT) | Upgrade of the existing 85km Foggia-Benevento II 400kV OHL and installation of a PST on this line. | [10 empty] | under construction | 2013-2014 | Authorization process ended, construction phase on going |  | 32
32 | 32. 96 | Deliceto (IT) | Bisaccia (IT) | New 30km single circuit 400kV OHL between the future substations of Deliceto and Bisaccia, in the Candela area. | [10 empty] | design & permitting | mid term | The 2 substations are in operation from 2011. The connecting line is still in design and permitting. This delay is due to authorization process. |  | 32
32 | 32. 96a | Several new 38 kV substations in Central / South of Italy for RES (IT) |  | It will be realized few new 380/150kV substations. The new substations will be connected to the wind power plants in order to avoid the congestions on the 150kV network and to dispatch the renewable energy produced. | [10 empty] | under construction | mid term | The realization of the substations is delayed. These investments are highly sensitive to the construction of the wind/solar plants that are meant to connect. |  | 32
32 | 32. 102 | Naples (IT) |  | Restructuring of the 220kV network in the urban area of Naples. Some new 220kV cables and some reinforcements of existing assets are planned. Total length: 36km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 32
32 | 32. 110a | Aliano (IT) | Montecorvino (IT) | New connection OHL 400 kV between north Basilicata and Campania region. | [10 empty] | planned | long term | Progresses as planned |  | 32
32 | 32. A99 | Restructuring of North Calabria (IT) |  | New 400kV OHL between the existing substations of Laino and Altomonte in Calabria and a new 380/150 kV substation in Aliano connected in and out to the existing 400 line kV "Matera - Laino" and to the local HV network. Related to this project will be acted a great restructuring of the local HV network, downgrading the existing 220 kV lines to 150 kV level and the demolition of great part of existing 150 kV lines inside the Pollino Park. | [10 empty] | partly under construction, design & permitting | 2012/mid term | New investment in TYNDP (initial design partially changed, evolution including new reinforcements and rearrangements activities on the neighboring areas resulting from further studies) |  | 32
33 | 33. 90 | Calenzano (IT) | Colunga (IT) | Voltage upgrade of the existing 80km Calenzano-Colunga 220kV OHL to 400kV, providing in and out connection to the existing 220/150kV substation of S. Benedetto del Querceto (which already complies with 400kV standards). | 500 | 2 | 5 | central part of Italy | [5 empty] | 2 | design & permitting | mid term | Delays due to authorization process. |  | Reinforcement between Northern and Central part of Italy to accommodate increasing market flows.
33 | 33. 94 | Mantova area (IT) | Modena area (IT) | New 35km 400kV OHL between the 2 substations in Modena and Mantova area. | [10 empty] | planned | long term | During the preliminary consultation process the substations have became uncertain. |  | 33
33 | 33. 104 | Rome (IT) |  | Restructuring of the network in the Rome area. The work consists of : a new 380/150kV substation in south-West area of Rome, connected in and out to the existing 380kV line "Rome West-Rome South", a voltage upgrade of the existing Flaminia substation up to 380kV to be connected in and out to the foreseen 380kV line "Rome West - Rome North" and a restructuring of the 150kV network. | [10 empty] | design & permitting | 2013/long term | Progresses as planned |  | 33
33 | 33. 109 | North Bologna (IT) |  | New 400/132kV substation in North Bologna area connected in and out to the existing Sermide–Martignone 400kV line. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 33
33 | 33. 111 | Lucca (IT) |  | New 380/132kV substation in Lucca area connected in and out to the existing 380kV line “La Spezia-Acciaiolo”. | [10 empty] | planned | long term | Progresses as planned |  | 33
33 | 33. 113 | Monte S. Savino (IT) |  | New 400/220/132kV substation in Monte S. Savino area connected to the existing S. Barbara 400kV substation by upgrading an existing 220kV line. | [10 empty] | design & permitting | 2015/long term | Delays due to authorization process. |  | 33
34 | 34. A100 | Codrongianos (IT) | Suvereto (IT) | Repowering of existing HVDC interconnection between Sardinia, Corse and mainland Italy via 220kV DC subsea cable (358km). The first connection is in operation since 1970. Total capacity of the bipolar link: 500MW. | 500 | 4 | 1 | [6 empty] | 2 | planned | long term | New investment in TYNDP. |  | Reinforcement between Sardinia Corso and mainland Italy.
48 | 48. 214 | Gabcikovo (SK) | Gőnyü area (HU) | New interconnection (new 2x400 kV tie-line) between SK and HU starting from Gabčíkovo substation (SK) to the Gőnyü substation on Hungarian side ( preliminary decision). Project also includes the erection of new switching station Gabčíkovo next to the existing one. | 1100 SK -> HU; HU -> SK 400 | 3 | 2 | (North-West Hungary) | [5 empty] | 1 | under consideration | 2016 | The commissioning date has been moved to earlier term due to earlier erection of new 400 kV line Veľký Ďur - Gabčíkovo that help to evacuate power from new NPP. | Negotiations still in progress. This project is closely connected with the project of erection of new line between Rimavska Sobota substation (SK) and Sajoivanka substation (HU); see below. | This cluster will increase the transfer capacity between Slovak and Hungarian network systems and increase security of supply. The internal interconnections in Slovakia are necessary for the same objective. Also this cluster is important for support of North - South flow from RES in North of EU.
48 | 48. 298 | Veľký Ďur (SK) | Gabčíkovo (SK) | Erection of new 2x400kV line between two important substations and extension of the substation Veľký Ďur (SK) Line length:93km. | [10 empty] | planned | 2016 | The commissioning date has been moved to earlier term due to ensure security of power evacuation from new NPP in V.ĎUR area. |  | 48
48 | 48. A125 | Veľký Ďur (SK) | Levice (SK) | The erection of new 1x400 kV line between two important Veľký Ďur and Levice substations, including extension of the V.Ďur and Levice substation. The driver for this project is expected connection of to new generation units in Veľký Ďur area. | [10 empty] | under consideration | 2018 | New investment in TYNDP, which will significantly increase of the security and reliability of the power evacuation from new NPP. |  | 48
48 | 48. A126 | Rimavská Sobota (SK) | Sajóivánka (HU) | Connection of the two existing substations (R.Sobota (SK) - Sajoóivánka (HU)) by the new 2x400 kV line (preliminary armed only with one circuit). | [10 empty] | under consideration | 2016 | New investment in TYNDP | Negotiations/bilateral studies in progress. This project is closely connected with the project 2x400kV line Gabčíkovo (SK) - Hungary (see above). | 48
48 | 48. A127 | Sajóivánka (HU) |  | Second 400/120 kV transformer and 2x70 Mvar shunt reactors in station Sajóivánka | [10 empty] | under consideration | 2016 | New investment in TYNDP |  | 48
48 | 48. A128 | Győr (HU) |  | Third 400/120 kV transformer and 70 Mvar shunt reactor in station Győr | [10 empty] | under consideration | 2016 | New investment in TYNDP |  | 48
49 | 49. 235 | Tirana(AL) | Pristina (RS) | New 238km 400kV OHL; on 78km the circuit will be installed on the same towers as the Tirana-Podgorica OHL currently in construction (see project 233); the rest will be built as single circuit line. | 600 | 2 | 5 | [6 empty] | 1 | design & permitting | 2013 | Line in Albania is already constructed. The rest of the lines develops according to the schedule. |  | It increases significantly the North to South GTC thus accommodating bulk transports to GR, FYROM and AL
49 | 49. 236 | Leskovac(RS) | Stip (MK) | New 220km 400kV single circuit overhead interconnection between Serbia and FYR of Macedonia. A new 400/110 substation will be built in Serbia between connection nodes. | [10 empty] | under construction | Serbian part commissioned, Macedonian part : 2013 | Serbian part is completed. Regarding the Macedonian part, the design is finished; the land acquisition is ongoing and the construction tender is in preparation. |  | 49
49 | 49. 237 | TPP Kosovo (RS) | Skopje (MK) | A new 400kV OHL relevant to planning investment of 2000MW of TPP in the area of Kosovo and Metohija. Line length: 85km. | [10 empty] | under consideration | 2020 | Progresses as planned |  | 49
49 | 49. 252 | Melliti (GR) | Kardia (GR) | New 400kV double circuit OHL. Length:40km. | [10 empty] | design & permitting | long term | Due to new thermal generation in South Greece the investment is no more needed urgently and postponed to the longer term. (This investment mainly was initially designed to solve voltage problems in South Greece.) |  | 49
49 | 49. 253 | Kardia (GR) | Trikala (GR) | New 400kV double circuit OHL. Length:80km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 49
49 | 49. 254 | Larissa(GR) | Trikala (GR) | New 400kV double circuit OHL. Length:57km. | [10 empty] | under consideration | long term | Progresses as planned |  | 49
50 | 50. 238 | Pancevo (RS) | Resita (RO) | New 131 km double circuit 400kV OHL between existing substations in Romania and Serbia (63 km on Romanian side and 68 km on Serbian side). | 1000 | 1 | 3 | Area BeLgrade and south Banat region | [5 empty] | 1 | design & permitting | 2015 (2019?) | Due to financing gap, the commissioning deadline was postponed to 2019. RO intends to apply for funding through the Operational Programme 'Increase of Economic Competitiveness' - Priority Axis 4. This would ensure realization of the project and allow for faster finalization (2015 instead of estimated 2019). Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | This project increases the transfer capability between Serbia, Romania and accommodates new RES generation on the West/East part of Romanian, respectively Serbia. It also increases the transfer capability on the interface between RO+BG/RS+BA+ME.
50 | 50. 269 | Portile de Fier (RO) | Resita (RO) | New 400kV OHL between existing substation 400 kV Portile de Fier and new 400 kV substation Resita. Line length: 116km. New 400 kV substation Resita, with 400/220 kV and 400/110 kV transformers, as development of the existing 220/110 kV substation. | [10 empty] | design & permitting | 2016 | Constructive characteristics were updated as a result of progress of feasibility and design studies. Commissioning date has been slightly shifted. |  | 50
50 | 50. A116 | Beograd 2 (RS) |  | New 400/110 kV substation on the Belgrade territory | [10 empty] | under construction | 2012 | New investment in TYNDP | By taking large amount of load from other Belgrade substations, the investment will both in/ improve the local SoS significantly, and ii/ relieve the constraints on the EHV local network and enable greater inter-area transits. | 50
50 | 50. A117 | Kraljevo 3 (RS) |  | Upgrade of the existing 220/110kV substation Kraljevo 3 by constructing the 400 kV level. | [10 empty] | design & permitting | 2015 | New investment in TYNDP |  | 50
50 | 50. A118 | Kraljevo 3 (RS) | Bajina Basta (RS) | New 140km double circuit 400kV OHL between substation Kraljevo 3 and substation Bajina Basta. Kraljevo 3 (400kV) will be connected to Kragujevac 2 (400 kV) substation, which is connected to a Sofia (Bulgaria) through a 400 kV line. | [10 empty] | planned | >2015 | New investment in TYNDP | New axis for transits from East to the West, typically from Bulgaria to Bosnia and Montenegro, and further to the west. | 50
50 | 50. 270 | Resita( RO) | Timisoara-Sacalaz-Arad (RO) | Upgrade of an existing 220kV double circuit line to 400kV double circuit line and replacement of 220 kV substations Timisoara and Sacalaz with 400 kV substations. Line length: 156km. | [10 empty] | design & permitting | 2022 | Due to financing gap, the commissioning deadline was postponed to 2022. Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 50
51 | 51. 239 | Bitola (MK) | Elbasan (AL) | New 200km cross-border single circuit 400kV OHL between existing substations. New 400/110 kV substation in Ohrid area connected in/out to the new 400 kV line Bitola-Elbasan. | 1255 MW BG - AL ,>1000 BG-TR | 3 | 2 | [6 empty] | 1 | planned | 2015 | Change of date of commissioning due to : resolving the problems in the 110KV in S-W Macedonia; facilitate the market integration; increased interest of potential investors. | Selection of consultant for preparation of feasibility study | East-West corridor from Bulgaria to Italy. Investments 257, 258 and 262 can build up an independent sub-project, as they will both in/ develop altogether, specifically, grid transfer capability with Turkey; ii/ contributes with all other investments clustered in the project to developing GTC East-West from Bulgaria to BiH and Montenegro.
51 | 51. 244 | Filippi(GR) | Lagadas (GR) | New 400kV substation in Lagadas in Thessaloniki area and connection to the existing substation of Filippi via a new 110km double circuit 400kV OHL. | [10 empty] | under construction | 2013 | Initial delays due to authorization process.The project is now under construction |  | 51
51 | 51. 256 | Maritsa East 1 (BG) | N.Santa (GR) | New interconnection line BG-GR by a 130km single circuit 400kV OHL. | [10 empty] | design & permitting | long term | After the interconnection with Turkey, the project can be delayed to LT as it is mainly connected to further RES development. The final commissioning date is subject to change depending of the evolution in the area. |  | 51
51 | 51. 257 | Maritsa East 1 (BG) | Plovdiv (BG) | New 100km single circuit 400kV OHL in parallel to the existing one. | [10 empty] | design & permitting | 2014 | Investments 257,258 and 262 are postponed because the permitting procedures (environmental requirements) with the land owners induced delays . |  | 51
51 | 51. 258 | Maritsa East 1 (BG) | Maritsa East 3 (BG) | New 13km single circuit 400kV OHL in parallel to the existing one. | [10 empty] | design & permitting | 2014 |  |  | 51
51 | 51. 262 | Maritsa East 1 (BG) | Burgas (BG) | New 400kV OHL. Line length: 150km. | [10 empty] | design & permitting | 2014 |  |  | 51
52 | 52. 240 | Patras (GR) | 4 kV Continental System (GR) | New 400kV substation in Patras (GIS Technology) and in&out connection to the existing Axeloos - Distomo 400kV OHL via a new 15km double circuit line, part of which will consist of subsea cable. The project shall constitute the first 400kV corridor to Peloponnese. | 600-700 | 4 | 1 | Peloponnese area | [5 empty] | 1 | design & permitting | 2013 | The project is likely to be delayed mainly due to the environmental concerns; strong opposition by the local communities resulted in the delay in permitting procedures and subsequent delay in the expected date of commissioning |  | It increases significantly the GTC to/from the peninsula of Peloponnese, thus allowing the accommodation of large amount of RES in the peninsula and also contributes to market integration
52 | 52. 241 | Patras (GR) | Megalopolis (GR) | New 400kV substation in Megalopolis and connection to Patras 400kV substation via a 110km double circuit OHL. 2nd corridor to Peloponnese. | [10 empty] | design & permitting | 2013 |  |  | 52
52 | 52. 242 | Megalopolis (GR) | Korinthos (GR) | Construction of a new 400kV substation in Korinthos (GIS Technology) and connection to the Megalopolis substation via a 110km double circuit 400kV OHL. | [10 empty] | design & permitting | 2014 |  |  | 52
52 | 52. 243 | Korinthos (GR) | Koymoyndoyros (GR) | Replacement of the existing 150kV double circuit line by a 87km double circuit 400kV OHL. | [10 empty] | design & permitting | 2014 |  |  | 52
53 | 53. 276 | Suceava(RO) | Gadalin(RO) | New 400kV OHL between existing stations. Line length: 260km. | 2000-2500 | 4 | 1 | [6 empty] | 2 | planned | 2021 | Constructive design characteristics and time schedule were updated as a result of progress of feasibility and design studies. |  | The project will help evacuate important amount of new generation (wind +nuclear generation) in Eastern part of Romania
53 | 53. A131 | Stejaru(RO) | Gheorghieni(RO) | Reconductoring (with HTLS) of existing simple circuit 220kV line. | [10 empty] | under consideration | 2015 | New investment in the TYNDP, required to integrate new RES generation and maintain the GTC for the entire project. |  | 53
53 | 53. 273 | Cernavoda (RO) | Stalpu | New 400kV double circuit OHL between existing stations. Line length:145km. | [10 empty] | planned | 2017 | Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 53
53 | 53. 274 | Constanta (RO) | Medgidia(RO) | New 400kV double circuit (one circuit wired) OHL between existing stations. Line length:75km. | [10 empty] | planned | 2020 | As for other investments, the commissioning date was postponed due to financing gap. Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 53
53 | 53. 275 | Smardan(RO) | Gutinas(RO) | New 400kV double circuit OHL between existing stations. Line length:140km. | [10 empty] | planned | 2020 | As for other investments, the commissioning date was postponed due to financing gap. Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 53
53 | 53. 271 | connection IN-OUT in Medgidia(RO) of actual 4 kV OHL Isaccea(RO)-Varna (BG) |  | The 400kV Isaccea (RO) - Varna (BG) is passing near 400 kV substation Medgidia S. The line shall be connected in Medgidia S, through a double circuit OHL. New wind farms shall be connected to the 400 kV OHL Isaccea - Medgidia S section . Substation Medgidia S, 400 kV, shall be refurbished with GIS technology in order to provide necessary space for new connections. | [10 empty] | design & permitting | 2015 | As for other investments, the commissioning date was postponed due to financing gap. Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 53
53 | 53. A132 | Stalpu (RO) | Teleajen (RO) - Brazi (RO) | Upgrade of an existing 220kV single circuit line to 400kV. New 400 kV substations: Stalpu (400/110kV, 1x250 MVA), Teleajen (400/110kV, 1x400 MVA) | [10 empty] | planned | 2018 | New investment in TYNDP | This investment was merged with investment 273 in TYNDP 2010. They are now presented as separate investments in TYNDP 2012, according to internal project organization. The network development is still the same. | 53
53 | 53. A133 | Fantanele (RO) | Ungheni (RO) | Reconductoring (with HTLS) of existing simple circuit 220kV line. | [10 empty] | under consideration | long term | New investment in the TYNDP, required to accommodate new RES generation not foreseen in the TYNDP 2010, by increasing the GTC for the entire project. |  | 53
53 | 53. 272 | connection IN-OUT in Medgidia(RO) of actual 4 kV OHL Isaccea(RO)-Dobrudja(BG) |  | Connection IN-OUT in Medgidia (RO) of existing 400kV OHL Isaccea (RO)-Dobrudja (BG), passing nearby. The line shall be connected in Medgidia S, through a double circuit OHL. Substation Medgidia S, 400 kV, shall be refurbished with GIS technology in order to provide necessary space for new connections. | [10 empty] | design & permitting | 2015 | As for other investments, the commissioning date was postponed due to financing gap. Constructive characteristics were updated as a result of progress of feasibility and design studies. | New wind farms shall be connected to the 400 kV OHL Isaccea - Medgidia S section. | 53
53 | 53. A134 | Gheorghieni(RO) | Fantanele (RO) | Reconductoring (with HTLS) of existing simple circuit 220kV line. | [10 empty] | under consideration | 2015 | New investment in the TYNDP, required to accommodate new RES generation not foreseen in the TYNDP 2010, by increasing the GTC for the entire project. |  | 53
54 | 54. 293 | Voľa (SK) | point of splitting (SK) | Splitting of the existing single 400kV line between Lemešany and Veľké Kapušany substations to connect the new 400kV substation Voľa with transformation 400/110kV (replacing existing 220kV substation). New 400kV double circuit OHL. Length: 23km | 500 | 2 | 2 | [6 empty] | 1 | design & permitting | 2013 | Progresses as planned |  | This cluster will increase the transfer capacity between Slovak and Hungarian network systems and increase security of supply. The internal interconnections in Slovakia are necessary for the same objective. Also this cluster is important for support of North - South flow from RES in North of EU.
54 | 54. 294 | Lemešany (SK) | Veľké Kapušany (SK) | Erection of new 400 kV line between Lemešany and Veľké Kapušany substations. The project includes the extension both substations Lemešany and V.Kapušany. Line length:100 (including the loop erected under the Investment 54.293). | [10 empty] | planned | 2018 | Progresses as planned |  | 54
54 | 54. A127 | Veľké Kapušany (SK) | tbd (HU) | Erection of new 2x400 line between SK and Hungary (substation on Hungarian side still to be defined) | [10 empty] | under consideration | 2021 | New investment in TYNDP |  | 54
95 | 95. A119 | Dobrudja(BG) | Burgas (BG) | New 140km single circuit 400kV OHL in parallel to the existing one. | 1500 | 4 | 3 | [6 empty] | 1 | planned | 2016 | New investment in TYNDP, required to accommodate 2000MW RES in Dobrudja region |  | It contributes to the accommodation of large amount of RES in Dobrudja region (2000 MW). It also contributes to North-South transfers and increases the SoS in Burgas region.
95 | 95. 265 | Vidno (BG) | Svoboda (BG) | New 400kV double circuit OHL to accommodate 2000 MW RES generation in N-E Bulgaria (Dobruja region). Line length: 2x70km. | [10 empty] | planned | 2015 | Moved from LT(TYNDP 2010) to MT due to high interest for very fast implementation of about 2000MW RES generation in Dobrudja region |  | 95
95 | 95. 263 | SS 4 /11 kV Svoboda(Krusari) |  | New 400/110kV substation to accommodate the expected RES generation(2000MW) in N-E Bulgaria (Dobruja region) | [10 empty] | planned | 2015 |  |  | 95
95 | 95. 264 | SS 4 /11 kV Vidno |  | New 400/110kV substation to accommodate the expected RES generation(2000MW) in N-E Bulgaria (Dobruja region) | [10 empty] | planned | 2015 |  |  | 95
95 | 95. 266 | IN-OUT in Svoboda on actual 4 kV OHL Isaccea(RO)-Varna (BG) |  | New 400kV double circuit OHL to accommodate the expected RES generation(2000MW) in N-E Bulgaria (Dobruja region). Line length: 2x10km. | [10 empty] | planned | 2015 |  |  | 95
108 | 108. A134 | Tarnita (RO) | Mintia (RO) | New 145km double circuit 400kV OHL | 1000 | 4 | 1 | [6 empty] | 1 | planned | 2018 | New investment in TYNDP | Connection of pumped storage hydro plant Tarnita Lapustesti to the grid. The plant has an installed capacity of 1000 MW and will support system balancing, especially in order to face the intermittent RES output. | The project will connect to the grid 1000MW hydro pump storage.
108 | 108. A135 | Tarnita (RO) | Cluj E - Gadalin (RO) | New 40km double circuit 400kV OHL | [10 empty] | planned | 2018 | New investment in TYNDP |  | 108
108 | 108. A136 | Tarnita (RO) |  | New 400kV substation | [10 empty] | planned | 2018 | New investment in TYNDP |  | 108
112 | 112. 98 | Pordenone (IT) |  | Voltage upgrade of the existing Pordenone 220kV substation up to 400kV. The substation will be connected in and out to the existing Udine O. – Cordignano 400kV line. | 2150 | 2 | 5 | Triveneto area | [5 empty] | 1 | planned | long term | Progresses as planned |  | This projects helps to increase the security of supply in the N-E part of Italy.
112 | 112. 105 | Treviso (IT) |  | New 380/132kV substation in Treviso area, connected in and out to the existing 380kV line “Sandrigo - Cordignano". | [10 empty] | design & permitting | mid term | Project delayed by 2 years due to longer than expected permitting procedure. |  | 112
112 | 112. 106 | Schio (IT) |  | New 220/132kV substation in Schio area, providing the connection in and out to the existing 220kV line "Ala-Vicenza Monte Viale”. | [10 empty] | planned | mid term | Project delayed by 2 years due to longer than expected permitting procedure. |  | 112
112 | 112. 107 | Vicenza Industrial (IT) |  | New 380/132kV substation in the industrial area of Vicenza, connected in and out to the existing Sandrigo-Dugale 400kV line. | [10 empty] | planned | long term | Progresses as planned |  | 112
112 | 112. 108 | North West Padova (IT) |  | New 220/132kV substation in North West Padova area, complying with 400kV standards, providing the connection in and out to the existing Dugale-Marghera Substation1 220kV line. | [10 empty] | planned | long term | Progresses as planned |  | 112
| 69 | Candia (IT) | Konjsko (HR) | New 1000MW HVDC interconnection line between Italy and Croatia via 280km 500kVDC subsea cable and converters stations at both ending points. | [10 empty] | under consideration | post 2022 | These incestments are very sensitive to the market and still under investigation
| 71 | Brindisi (IT) | Babica (AL) | 500MW single pole HVDC Merchant Line between Italy and Albania via 290km 400kV DC subsea cable and converter stations at both ends. On the Italian side, the new line will be connected to the existing substation of Brindisi South. | [10 empty] | design & permitting | long term | Permitted as a merchant line (it develops according to the plan of the stakeholders)
| 72 | Aetos(GR) | Galatina (IT) | Second 500MW HVDC link between Greece and Italy via 316km 400kVDC subsea cable and converters stations at both ends. | [10 empty] | under consideration | post 2022 | These incestments are very sensitive to the market and still under investigation
| 120 | Lavorgo (CH) | Morbegno (IT) | New 400kV tie line between Italy and Switzerland. | [10 empty] | cancelled | cancelled | It has been replaces by investment n° ITA-4 "New interconnection between CH and IT"- change in the design and complexity of the project
| 230 | TPP Sisak (HR) | Mraclin(HR)/Prijedor(BA) | Connection of new generator on existing line 220kV Mraclin (HR) - Prijedor (BA) via a new double circuit OHL. Line length: 12km. | [10 empty] | design & permitting | 2012-2013 | The commissioning date is postponed due to the prolonged permitting procedures and due to the harmonization with installation of new generating unit in TPP Sisak.
| 245 | N.Santa (GR) |  | Construction of the new 400kV S/S N.Santa in North Greece. This S/S will serve as the interface for the new line GR-TR, as well as for the interconnection of new wind farms and conventional generation. | [10 empty] | commissioned | commissioned | Commissioned
| 247 | Aliveri(GR) | Larimna (GR) | Construction of the new 400kV S/S Aliveri in Eviai area and a new 400kV double circuit line Aliveri-System. Line length: 128km. | [10 empty] | design & permitting | Long term | Delays in the permitting procedures and uncertainties in the commission of new generation in Evia island.
| 250 | Lavrion (GR) | Syros (GR) | New 150kV subsea cable DC connection. There is also the possibility to use AC if proved technically and economically feasible. | [10 empty] | design & permitting | 2015 | Due to the technical complexity of the projects and environmental problems, the project is delayed. Most of the problems have been solved; the tender for the construction released in 2011. Now the date of commissioning is identified.
| 251 | Syros (GR) | Cyclades (GR) | New 150kV subsea cables and 4x150kV Substations to islands of Mykonos,Paros, Naxos and Tinos | [10 empty] | design & permitting | 2015 | Project going according to the plan
| 255 | Lamia (GR) |  | Construction of a new 400kV EHV SS in Lamia and connection to the two circuits of the existing 400kV lines Trikala-Distomo and Larisa-Larymna. | [10 empty] | planned | Long term | No change
| 260 | Plovdiv (BG) | Aleko(BG) | Reconstruction of the existing 220kV OHL and the building of a new second one. Line length: 40km. | [10 empty] | cancelled | cancelled | The project is abandoned, as building the 400kV line "M.East1-Plovdiv"(Pr.139, boundary 40b, inv.index257) will eliminate the need of building the line
| 261 | Karnobat (BG) | Dobrudja (BG) | This project concerns the reconstruction of the existing 220kV OHL. Line length: 95km. | [10 empty] | cancelled | cancelled | "The project is abandoned, as building the 400kV line "Dobrudja-Burgas"(PR 136 boundary 43, inv.index BG NEW) will eliminate the need of building the line
| 267 | Suceava (RO) | Balti (MD) | New 400 kV OHL (139 km) to increase capacity of transfer between Romania and Republic Moldova. The project also implies new substation 400 kV in Moldova (extension of the substation Balti (MD) with 400 kV level). | [10 empty] | design & permitting | 2020 | The project. is associated to the connection of the Rep. Moldova and Ukraine. Delay is associated to the procedure for the connection of UA+MD.
| 268 | Constanta (RO) | Pasakoy (TR) | New DC link (subsea cable) between existing stations in RO and TR. Line length: 400km. | [10 empty] | under consideration | >2020 | The delay in the investment is caused by the lack of financial means.
| 279 | Gyor (HU) | Martonvasar (HU) | Upgrade of an existing 220kV single circuit line to 400kV double circuit. Line length:84km. | [10 empty] | under construction | 2012 | It will be commissioned by the end of 2012
| 282 | Sajoszoged / God (HU) | Detk (HU) | New substation Detk with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Sajoszoged-God. | [10 empty] | design & permitting | 2017 | The project was delayed due to a change in the generation(decommissioning of units connected to 120 kV deferred) which led to a delay in investment need
| 284 | Martonvasar / Paks (HU) | Dunaujvaros (HU) | New substation Dunaujvaros with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Martonvasar-Paks. | [10 empty] | design & permitting | 2015 | 2012->2015: Delayed due to delay in investment need, according to National Plan 2010 (load growth in the specific area will be lower than previously forecasted)
| 285 | Debrecen (HU) |  | New substation Debrecen with 2*250 MVA 400/120kV transformation is connected by changing the operating voltage of line Sajoszoged-Debrecen from 220kV to 400kV, this line being already designed for 400kV. | [10 empty] | design & permitting | 2013 | Progress as planned.
| 286 | Martonvasar / Liter (HU) | Szekesfehervar (HU) | New substation Szekesfehervar with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Martonvasar-Liter. | [10 empty] | planned | 2016 | 2014->2016: Delayed due to delay in investment need, according to National Plan 2010 (load growth in the specific area will be lower than previously forecasted)
| 287 | Albertirsa / God (HU) | Godollo (HU) | New substation Godollo with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Albertirsa-God. | [10 empty] | planned | 2015 | progress as planned
| 288 | Albertirsa / Martonvasar (HU) | Szazhalombatta (HU) | New substation Szazhalombatta is connected by splitting and extending existing line Albertirsa-Martonvasar. | [10 empty] | planned | 2015 | progress as planned
| 289 | Felsozsolca (HU) | Sajoivanka (HU) | Reconstruction of line to double circuit, installation of the 2nd transformer in substation Sajoivanka. Line length: 29km. | [10 empty] | cancelled | cancelled | Cancelled: new cluster #53 makes this investment unnecessary.
| 290 | Oroszlany (HU) |  | New substation Oroszlany with 2*250 MVA 400/120kV transformation is connected by splitting and extending the second circuit of line Martonvasar-Gyor. | [10 empty] | under consideration | 2016 | 2017->2016: Earlier completion is foreseen for financing and organization reasons.
| 291 | Sajoszoged (HU) |  | New 400/120kV 250MVA transformer with PST. | [10 empty] | cancelled | cancelled | Cancelled according to National Plan 2010; generation pattern in the specific area will change significantly thus this investment is no longer necessary.
| 292 | Debrecen (HU) |  | Reconstruction of 750kV substation. | [10 empty] | design & permitting | 2013 | progress as planned
| 65 | Curon (IT)/ Glorenza (IT) | New substation close to the border in AT | New 380/220kV substation in AT directly located near the border ; erection of a 24km single circuit 220kV-connection via OHL and underground cable till Graun (IT) and upgrade of the existing line Graun (IT) – Glorenza (IT). | [10 empty] | cancelled | cancelled | It has been replaces by investment n° ITA-5 "New interconnection between AT and IT", This project which was depicted in the TYNDP2010 suffered important changes in the design.
| 78 | Palermo area (IT) |  | Restructuring of the network in the Palermo area. The work consists of a new 220/150kV substation, complying with 400kV standards, connected to the Ciminna substation with a new 400kV line and in & out the existing Bellolampo-Caracoli 400kV line, and also the connection of 15 kV lines "Casuzze - Monreale" and "Casuzze - Guadalami" and a repowering of the existing Casuzze 150/MV substation. It is foreseen also large a restructuring of the 150kV network in the palermo area in order to increase the security and the quality of supply. Total length: 49 km. | [10 empty] | design & permitting | 2015 | The project has changed in terms of composition (new refurbishments were added to the initial project). The date of commissioning was advanced due to the faster need of increasing the security of Palormo area.
| 79 | Agrigento (IT) |  | New 220/150kV substation, complying with 400kV standards. The new substation will be connected in and out to the existing Partanna-Favara 400kV line . | [10 empty] | design & permitting | 2015 | The authorization process is faster than expected..
| 80 | Noto (IT) |  | New 220/150kV substation, complying with 400kV standards, connected in and out to the existing Ragusa-Melilli 400kV line. | [10 empty] | design & permitting | 2014/2015 | The authorization process is faster than expected..
| 248 | Polypotamo (GR) | N. Makri (GR) | New 150kV double circuit subsea cable. Line length:33km. | [10 empty] | under construction | 2013 | Delays due to authorization process.
| 110 | Restructuring of Sorrento Peninsula network (IT) |  | It is planned a new 380/220/150kV substation in East Vesuvius area (near Naples) connected in and out to the existing 380 and 220kV lines “Montecorvino-S. Sofia” and "Nola-S. Valentino". Related to this project, it has been programmed also some reinforcements and restructuring of the existing 220kV and 150 kV network in the area of Sorrento Peninsula. Total net length: 58km. | [10 empty] | design & permitting | 2014 | Shifted from Long Term to 2014 due to the authorization process which started a little bit before the scheduled time.
| 119 | Capri, Ischia, Procida (IT) |  | New 150kV subsea connection between the Capri, Ischia and Procida islands to the existing substations of Cuma and Torre Annunziata (mainland Italy). Total length : 95km. | [10 empty] | design & permitting | 2014 | Delays due to authorization process.
| 118 | Porto Ferraio (Elba Island) | Cornia (Piombino) | New 40km 132kV connection via subsea cable between the existing substation of Porto Ferraio and the future 400/132kV substation of Cornia that will also be connected in and out to the existing Suvereto-Piombino Termica 400kV line. | [10 empty] | design & permitting | 2012/long term | Delays due to authorization process.
| 114 | Ittiri (IT) | Codrongianos (IT) | New 18km 400kV OHL between the existing substation of Codrongianos and the future 400kV substation of Ittiri that will be also connected in and out to the existing Fiumesanto-Selargius 400kV line. | [10 empty] | commissioned | commissioned | Commissioned
| 115 | Fiumesanto (IT) | Latina (IT) | Second pole of HVDC link between Sardinia and mainland Italy via 400kV DC subsea cable (420km). The first pole is in operation since 2009. Total capacity of the bipolar link: 1000MW. | [10 empty] | commissioned | commissioned | Commissioned
| 116 | Casellina (IT) | Tavarnuzze (IT) | New 37km 400kV OHL with rearrangement of EHV grid in the area between Casellina and S. Barbara. Voltage upgrade of the existing substations of Casellina400/132kV and S. Barbara400/132kV. | [10 empty] | commissioned | commissioned | Commissioned
| 117 | Castegnero (IT) |  | New 220/132kV substation connected in and out to the existing 220kV line “Cittadella – Este” and “Dugale – Stazione 1”, providing a restructuring of HV grid. | [10 empty] | commissioned | commissioned | Commissioned
| 213 | Wien SO (AT) | Szombathely (HU) | Installation of the 2nd circuit on the existing interconnection from Wien SO (AT, APG) to the border (both circuits have already been installed on the Hungarian side, one is connected to Györ and the 2nd circuit to Szombathely). Line length: 63km. | [10 empty] | commissioned | commissioned | 2011->2010: Completed earlier. It was due to scheduling of the field work.
| 226 | Ernestinovo (HR) | Pecs (HU) | New 400kV double circuit interconnection line between existing stations. Line length: 86km. | [10 empty] | commissioned | commissioned | Commissioned
| 246 | Aliveri(GR) | System (GR) | Construction of the new 400kV S/S Aliveri in Eviai area and a new 400kV double circuit line Aliveri-System. Line length: 72km. | [10 empty] | under construction | 2012 | Under construction; some minor design and permitting issues are pending. The investment has been removed from projects of European significance because it doesn't fit to the criteria set in TYNDP 2012
| 249 | Polypotamo (GR) | N. Evia (GR) | New 150kV double circuit OHL. Line length: 40km. Along the new transmission line, 4 new 150/20kV substation shall be build for the interconnection of new wind farms in Evia island. | [10 empty] | under construction | 2013 | This line will be utilized mainly for the connection of new wind farms. The final locations of the private substations are not defined yet. In addition public opposition to the construction of the overhead line created additional time delays. The investments has been removed from projects of European significance because it doesn't fit to the criteria set in TYNDP 2012
| 259 | Plovdiv (BG) | Zlatica (BG) | New 75km single circuit 400kV OHL. | [10 empty] | commissioned | commissioned | "Completed and in normal operation since October 2010
| 277 | Heviz (HU) | Szombathely (HU) | New 400kV transmission line between existing stations. Line length: 78km. | [10 empty] | commissioned | commissioned | Commissioned
| 278 | Gyor / Liter (HU) | Gonyu (HU) | New substation Gonyu (generator connection point) is connected by splitting and extending existing line Gyor-Liter. | [10 empty] | commissioned | commissioned | Commissioned
| 233 | Tirana (AL) | Podgorica (ME) | New 400kV line Tirana (AL)-Podgorica (ME) with length 157km (128.5km on Albanian side, 76km of which with double circuit and 28.5km on the Montenegrin side). | [10 empty] | commissioned | commissioned | Commissioned
| 234 | Elbasan (AL) | Tirana(AL) | New 400kV AC OHL. Length: 48km. | [10 empty] | commissioned | commissioned | Commissioned
| 280 | Gyor / Martonvasar (HU) | Bicske (HU) | New substation Bicske with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Gyor-Martonvasar line. | [10 empty] | commissioned | commissioned | 2012->2010: Completed earlier. It was due to financing and field organization issues.
| 283 | Albertirsa / Bekescsaba (HU) | Szolnok (HU) | New substation Szolnok with 2*250 MVA 400/120kV transformers is connected by splitting and extending existing line Albertirsa-Bekescsaba. | [10 empty] | commissioned | commissioned | 2012->2011: Earlier completion due to scheduling of the field work.
| 281 | Albertirsa (HU) | Martonvasar (HU) | Adding second circuit to existing 400kV single circuit OHL. Line length: 45km. | [10 empty] | commissioned | commissioned | Commissioned earlier due to scheduling of the field work.
| 67 | Divaca (SI) |  | Installation of a new 400kV PST to assist control of power flows to Italy on secure level and secure the operation of Slovenian grid enabling full utilization of regional market. | [10 empty] | commissioned | commissioned | This is PST in SS Divaca and it has been is in operation since 2011.
| 82 | Chignolo Po (IT) | Maleo (IT) | A new 380kV double circuit OHL between the new 380kV substations of Chignolo Po and Maleo in Lodi area. Restructuring of HV network. Total line length: 22km. | [10 empty] | commissioned | commissioned | Commissioned
| A121 | Brezna (ME) |  | A new substation will be connected to the planned line 400kV Lastva-Pljevlja(ME), with two transformers 2X300MVA 400/110kV | [10 empty] | design & permitting | 2016 | New project
| A122 | Maoce (ME) |  | A new TPP substation will be connected to the existing line 400kV Ribarevine-Pljevlja(ME) | [10 empty] | design & permitting | 2018 | New project
| A123 | Andrijevo (ME) |  | A new HPP substation will be connected to the existing line 400kV Ribarevine-Pljevlja(ME) | [10 empty] | design & permitting | 2016 | New project
| A130 | Albertfalva (HU) |  | New 220/120kV 160MVA transformer. | [10 empty] | planned | 2020 | Appeared in National Plan 2010, transformer capacity extension on 220/120 kV is needed for maintaining SoS.
| A138 | Filippoi EHV (GR) | Limnos (GR) | A new substation in Limnos will be connected to the mainland grid to the existing EHV substation in Filippoi. | [10 empty] | Under consideration | long term | New project
| A137 | Larymna EHV (GR) | Chios (GR) | A new substation in Chios will be connected to the mainland grid to the existing EHV substation in Larymna. | [10 empty] | Under consideration | long term | New project
| A140 | Chios (GR) | Lesvos (GR) | A new substation in Lesvos will be connected to Chios substation. | [10 empty] | Under consideration | long term | New project
| A141 | Limnos (GR) | Lesvos (GR) | A new submarine DC link will connect Limnos and Lesvos substations. | [10 empty] | Under consideration | long term | New project
| A142 | Megalopoli EHV (GR) | Crete 1 (GR) | A new substation in Crete will be connected to the mainland grid in Peloponese to the new EHV substation in Megalopoli | [10 empty] | Under consideration | 2018-2019 | New project
| A143 | Acharnes EHV (GR) | Crete 2 (GR) | A new substation in Crete will be connected to the mainland grid of the capital to the existing EHV substation in Acharnes | [10 empty] | Under consideration | 2030 | New project
| A104 | Castelbello (IT) | Naturno (IT) | New 220 kV (insulated at 400 kV level) OHL connection between existing stations of Naturno and Castelbello. | [10 empty] | planned | long term | Overcoming the constrains in operation, due the renewable generation in the area of Trentino Alto Adige region.

## BS report
5 July 2012
TYDNP 2012 package - Table of projects Baltic Sea Regional Group Investment Plan
Project identification |  |  |  |  | Project assessment
Project number | Investment number | Substation 1 | Substation 2 | Brief technical description | Grid Transfer Capability Increase [MW] | Socio-economic Welfare | RES integration | Improved Security of Supply | Losses variation | CO2 mitigation | Technical resilience | Flexibility | Social and environmental Impact | Project costs | Present status | Expected date of commissioning | Evolution compared to the TYNDP 2010 situation | Investment comment | Project comment
35 | 35. 137 | Vitkov (CZ) | Mechlenreuth (DE) | New 400kV single circuit tie-line between new (CZ) substation and existing (DE) substation. Length: 70km. | 500 | 5 | 4 | [6 empty] | 3 | under consideration | long term | Progresses as planned |  | This project is required to enable power flows between West and East, enhance the transfer capability between CZ and DE and supports the future generation evacuation.
35 | 35. 138 | tbd (CZ) | tbd (DE) - South-Eastern part of 5 Hertz Transmission control area (Röhrsdorf) | Possible increase of interconnection capacity between CEPS and 50Hertz Transmission is under consideration: either a new 400kV tie-line (OHL on new route) or a reinforcement of the existing 400kV tie-line Hradec (CEPS) – Röhrsdorf (50Hertz Transmission). | [10 empty] | under consideration | long term | Progresses as planned |  | 35
35 | 35. 306 | Vitkov (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA. | [10 empty] | planned | 2017/2018 | It is closely dependent on construction of line investment n°308 |  | 35
35 | 35. 307 | Vernerov (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA. | [10 empty] | planned | 2013/2016 | Commissioning date has been divided into two phases (1. phase - temporary connection of wind plant 180MW, 2. phase finalization of substation construction including connection to the distribution grid (consumption) |  | 35
35 | 35. 308 | Vernerov (CZ) | Vitkov (CZ) | New 400kV double circuit OHL, 1385 MVA. | [10 empty] | planned | long term | Permitting procedure complications are foreseen (line crosses protected area) |  | 35
35 | 35. 309 | Vitkov (CZ) | Prestice (CZ) | New 400kV double circuit OHL, 1385 MVA. | [10 empty] | under consideration | long term | Permitting procedure complications are foreseen (line crosses protected area) |  | 35
35 | 35. 311 | Kocin (CZ) |  | Upgrade of the existing substation 400/110kV; upgrade transformers 2x350MVA. | [10 empty] | design & permitting | long term | Schedule harmonization with market participants |  | 35
35 | 35. 312 | Mirovka (CZ) |  | Upgrade of the existing substation 400/110kV with two transformers 2x250MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 313 | Kocin (CZ) | Mirovka (CZ) | Connection of 2 existing 400kV substations with double circuit OHL having 120.5km length: and a capacity of 2X1385 MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 314 | Mirovka (CZ) | V413 (CZ) | New double circuit OHL with a capacity of 2x1385 MVA and 26.5km length. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 315 | Kocin (CZ) | Prestice (CZ) | Adding second circuit to existing single circuit line OHL upgrade in length of 115.8km. Target capacity 2x1385 MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 316 | Mirovka (CZ) | Cebin (CZ) | Adding second circuit to existing single circuit line (88.5km, 2x1385 MVA). | [10 empty] | under consideration | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 317 | Hradec (CZ) | Reporyje (CZ) | Upgrade of existing 400kV single circuit OHL with length of 116.9km. Target capacity 1385 MVA. | [10 empty] | commissioned | commissioned | Commissioned |  | 35
36 | 36. 141 | Ishøj/Bjæverskov (DK) | Bentwisch/Güstrow (DE) | The Kriegers Flak Combined Grid Solution is the new offshore multiterminal connection between Denmark and Germany used for both grid connection of offshore wind farms Kriegers Flak and interconnection. Technical features still have to be determined. | 600 | 5 | 3 | [6 empty] | 1 | planned | long term | Permission for Danish Wind Farm KF 3 is in pending. Connection to Sweden is withdrawn at present, but can come on a later stage. |  | The Kriegers Flak Combined Grid Solution is the new offshore multiterminal connection between Denmark and Germany used for both grid connection of offshore wind farms Kriegers Flak and interconnection.
37 | 37. 142 | Tonstad (NO) | Wilster (DE) | Nord.Link/NorGer: a new HVDC connection between Southern Norway and Northern Germany. Estimated subsea cable length: 520 - 600km. Capacity: 1000 MW. | up to 1400 | 1 | 4 | [6 empty] | 3 | design & permitting | 2018/2021 | Revised capacity and progress postponed, due to more demanding system operations and time needed to obtain necessary government permits for reinforcing the national grid. |  | The purpose is: Market integration with the continent and facilitating RES integration in southern and western Norway. Will also improve security of supply in southern Norway.
| 37. 408 | Kristiansand, Feda (NO) |  | Reactive compensation due to HVDC links NorNed and Skagerak 4. Reactive power devices in 400kV substations. | [10 empty] | design & permitting | 2012/2014 | Feda is in the planning and permitting stage. Kristiansand is under construction(commissioned expected as planned 2012)
37 | 37. 406 | (Southern part of Norway) (NO) |  | Voltage uprating of existing 300 kV line Sauda/Saurdal - Lyse - Tonstad - Feda - 1&2, Feda - Kristiansand; Sauda-Samnanger in long term. Voltage upgrading of existing single circuit 400kV OHL Tonstad-Solhom-Arendal. Reactive power devices in 400kV substations. | [10 empty] | design & permitting | 2016 (2013-2018) | Revised progress. Due to more demanding system operations and time needed to obtain necessary government permits for reinforcing the national grid. The investment now embed former TYNDP 2010's investments 407 and 409 and the technical description has been updated accordingly. |  | 37
38 | 38. 425 | Feda (NO) | tbd (NL) | NorNed 2: a second HVDC connection between Norway and The Netherlands via 570km 450kV DC subsea cable with 700 - 1400MW capacity. | 700 | 5 | 2 | [6 empty] | 2 | under consideration | Long term | NorNed 2 is now not likely be realised during this planning period but is included in the TYNDP calculations and therefore on the project list. NorNed 2 is not included in the current Norwegian national grid development plan. |  | Additional interconnection between NO and NL under consideration
39 | 39. 428 | Kassø (DK) | Tjele (DK) | Rebuilding of a 400kV OHL of 173km from a single-circuit to a double-circuit . This increases the transfer capacity with approx. 1000 MW. | 1000-1550 | 1 | 2 | [6 empty] | 2 | design & permitting | 2012/2014 | Progresses as planned |  | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity.
39 | 39. 144 | Audorf (DE) | Kassö (DK) | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity. It consists of partially an upgrade of existing 400kV line and partially a new 400kV route in Denmark. In Germany new 400kV line mainly in the trace of a existing 220kV line. The total length of this OHL is 114km. | [10 empty] | under consideration | 2017 | Progresses as planned |  | 39
40 | 40. 446 | Bascharage (LU) | Aubange (BE) | As a first step(2016) a PST could be placed in the existing 225kV line between LU and BE. In a second stage, two solutions are currently investigated (4 TSOs - Elia, Amprion, CREOS, RTE are involved). Solutions 1 would be a new interconnection between Creos grid in LU and ELIA grid in BE via a 16km double circuit 225kV underground cable with a capacity of 1000 MVA. Solution 2 would be the interconnection between CREOS grid in LU and ELIA grid in BE via a new 380 kV double circuit. The current study will investigate the impact of this new interconnection on other boundaries (impact of loop flow) and on internal grids . The potential reinforcements of the other boundaries and the internal grids will also be taken into account in the evaluation. | 380-900 | 2 | 5 | Luxemburg area | [5 empty] | 2 | under consideration | 2016/2020 | The commissioning date and status changed as the study to determine the best investment is still ongoing. |  | Increase the transfer capability between LU,DE, BE and FR.
40 | 40. A29 | Bascharage (LU) | tbd (BE, DE, &/o FR) | New interconnection with neighbor(s) either 220kV or 400kV | [10 empty] | under consideration | 2020 | New investment in TYNDP | An ongoing network study (4 TSOs involved) investigates the robustness of the planned 220kV connection between LU and BE and the potentially need for an upgrading to a 400kV interconnector in the South. | 40
40 | 40. 447 | Heisdorf (LU) | Berchem (LU) | New 20km double-circuit mixed (underground cable+OHL) 225kV project with 1000 MVA capacity including substations for in feed in lower voltage levels. | [10 empty] | design & permitting | 2012/2017 | Progresses as planned |  | 40
40 | 40. A30 | Bascharage (LU) | Niederstedem (DE) or tbd (DE) | Upgrading and new construction of an interconnector to DE, in conjunction with the interconnector in the south of LU; Partial upgrading of existing 220kV lines and partial new construction of lines; With power transformer station in LU | [10 empty] | under consideration | 2020 | New investment in TYNDP |  | 40
41 | 41. 149 | Dollern (DE) | Stade (DE) | New 400kV double circuit OHL Dollern - Stade including new 400kV switchgear in Stade. Length:14km. | >3000 | 4 | 5 | [6 empty] | 1 | design & permitting | mid term | This investment depends on the commissioning of a conventional power plant in the area. The additional reason for delay is the long permitting procedure associated with this investment. |  | Evacuation of the new conventional generation in the 50Hz and TenneT area.
41 | 41. 150 | Conneforde (DE) | Maade (DE) | New 400kV double circuit ( underground cable+OHL) Conneforde - Maade including new 400kV switchgear Maade. Length: 37km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 41
41 | 41. A74 | North of Control Area 5 HzT (DE) |  | Construction of new substations/lines for integration of newly build power plants in northern part of 50HzT control area. | [10 empty] | planned | long term | New investment in TYNDP, because of additional need for generation evacuation. Some of the investments are to be commissioned by the mid term and the some by long term. | Support of conventional generation integration in North-Eastern Germany, maintaining of security of supply and support of market development. | 41
42 | 42. 152 | Dörpen/West (DE) |  | New substation for connection of offshore wind farms. | >8000 | 4 | 1 | [6 empty] | 3 | under construction | mid term | Progresses as planned | Commercially sensitive information about this new wind-farm connection cannot be displayed in the TYNDP report | Integration of the offshore wind parks and the onshore grid reinforcements in the Northern DE.
42 | 42. 159 | Cluster BorWin1 (DE) | Diele (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 205km. Line capacity: 400MW. | [10 empty] | under construction | mid term | The commission date of this wind farms connection should be in 2012. Energy transportation is however already enable | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 160 | Offshore- Wind park Nordergründe (DE) | Inhausen (DE) | New AC-cable connection with a total length of 35km. | [10 empty] | design & permitting | mid term | Progresses depend on development of the off shore wind farm |  | 42
42 | 42. 161 | Offshore- Wind park GEOFreE (DE) | Göhl (DE) | New AC-cable connection with a total length of 32km. | [10 empty] | design & permitting | mid term | Progresses depend on development of the off shore wind farm |  | 42
42 | 42. 163 | Cluster HelWin1 (DE) | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 145km. Line capacity: aprox. 690MW. This Project includes also a new substation Büttel and connection of this new substation with the existing OHL Brünsbüttel - Wilster. | [10 empty] | under construction | mid term | Progresses with delay. | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 164 | Cluster SylWin1 (DE) | Büttel (DE) | New line consisting of underground +subsea cable with a total length of 210km. Line capacity: aprox.864MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 165 | Cluster DolWin1 (DE) | Dörpen/West (DE) | New line consisting of underground +subsea cable with a total length of 155km. Line capacity: 800MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 166 | Offshore Wind park Riffgat (DE) | Emden /Borßum(DE) | New AC-cable connection with a total length of 80km. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 167 | Cluster BorWin2 (DE) | Diele (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 205km. Line capacity: 800MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A82 | Cluster DolWin2 (DE) | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 160 km. Line capacity: 900 MW | [10 empty] | under construction | mid term | New investment in TYNDP, for connection of new off-shore wind-farms | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A83 | Cluster DolWin3 (DE) | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 160 km. Line capacity: 900 MW | [10 empty] | design & permitting | mid term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A84 | Cluster BorWin3 | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 180 km. Line capacity: 900 MW | [10 empty] | design & permitting | mid term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A85 | Cluster HelWin2 | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 145km. Line capacity: 690 MW | [10 empty] | under construction | mid term | New investment in TYNDP, for connection of new off-shore wind-farms | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A86 | Cluster BorWin4 (DE) | Emden/Ost (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 185 km. Line capacity: 900 MW | [10 empty] | under consideration | long term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A87 | Cluster SylWin2 (DE) | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 210km. Line capacity: 800 MW | [10 empty] | under consideration | long term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. 211 | Further connections of more offshore wind farms (DE) |  | Further connections in the clusters BorWin, DolWin, SylWin and HelWin. | [10 empty] | under consideration | long term | Progresses depend on development of the off shore wind farm |  | 42
43 | 43. A81 | Osterath (DE) | Philippsburg (DE) | New HVDC-lines from Osterath to Philippsburg to integrate new wind generation especially from North/ Baltic Sea towards Central-South Germany for consumption and storage. | 10000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany |  | Combined DC and AC new infrastructure to accommodate the new RES generation, the associated flows from North to South and also secure the SOS in South Germany.
| 43. A152 | Emden (DE) | Osterath (DE) | New HVDC-lines from Endem to Osterath to integrate new wind generation especially from North/ Baltic Sea towards Central Germany for consumption and storage. | [10 empty] | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany
| 43. A153 | Wehrendorf (DE) | Urberach (DE) | New lines in HVDC technology from the region of Lower Saxony to North Baden-Württemberg to integrate new wind generation especially from North Sea towards Central-South Europe for consumption and storage. The investment is part of the transmission corridor Cloppenburg - North Baden-Württemberg. | [10 empty] | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany
| 43. A154 | Cloppenburg (DE) | Westerkappeln (DE) | New 400-kV double circuit OHL Cloppenburg-Westerkappel (75 km). The investment is part of the transmission corridor Cloppenburg - North Baden-Württemberg. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
43 | 43. A88 | Brunsbüttel (DE), Wilster (DE), Kaltenkirchen (DE) | Großgartach (DE), Goldshöfe (DE), Grafenrheinfeld (DE) | New DC-lines to integrate new wind generation from Northern Germany towards Southern Germany and Southern Europe for consumption and storage. | [10 empty] | under consideration | long term | New Investment. |  | 43
43 | 43. A75 | Lauchstadt (DE) | Meitingen (DE) | New DC- lines to integrate new wind generation from Baltic Sea towards Central/south Europe for consumption and storage. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits |  | 43
43 | 43. A89 | Area of Northern Lower Saxony (DE) |  | New lines for integration of on- and offshore Wind generation incl. 380-kV-lines Halbemond - Emden, Emden-Conneforde and Conneforde - Cloppenburg. Total length: 160 km | [10 empty] | under consideration | long term | New Investment. |  | 43
43 | 43. A90 | Area of Schleswig-Holstein (DE) |  | About 300 km new 380-kV-lines and around 24 new transformers for integration of onshore Wind in Schleswig-Holstein, incl. lines Brunsbüttel-Barlt-Heide-Husum-Niebüll-border of Denmark, Audorf-Kiel-Göhl-Siems-Lübeck-Kaltenkirchen and Kaltenkirchen-Itzehoe-Brunsbüttel | [10 empty] | under consideration | long term | New investment in TYNDP due to new wind generation projects. | The German West-coast line (Brunsbuettel – Niebuel) is planned to be connected to the Danish grid in the 400 kV substation Endrup. The distance from the German/Danish border is approx. 80 km. Bilateral technical/economical investigations are ongoing. Reinforcements in the Danish 400 kV grid are foreseen in order to facilitate the increased power exchange capacity on the Danish-German border. | 43
44 | 44. 147 | Dollern (DE) | Hamburg/Nord (DE) | New 400kV double circuit OHL Dollern - Hamburg/Nord including one new 400/230kV transformer in substation Hamburg/Nord and new 400kV switchgear Kummerfeld. Length:43km. | 5000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 | design & permitting | mid term | Delays due to authorization process. |  | This project helps accommodating the increasing flows coming mainly form RES in NW DE to SW DE and CH.
44 | 44. 148 | Audorf (DE) | Hamburg/Nord (DE) | New 400kV double circuit OHL Audorf - Hamburg/Nord including two new 400/230kV transformers in substation Audorf. Length: 65km. | [10 empty] | design & permitting | mid term | This investment was schedulted for 2015. Presently it is foreseen a delay of around 1 year due to permitting process. |  | 44
44 | 44. 151 | Wehrendorf (DE) | Ganderkesee (DE) | New line (length: ca. 95km), extension of existing and erection of substations, erection of 380/110kV-transformers. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 156 | Niederrhein (DE) | Dörpen/West (DE) | New 400kV double circuit OHL Dörpen - Niederrhein including extension of existing substations. Length: 167km. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 157 | Wahle (DE) | Mecklar (DE) | New 400kV double circuit OHL Wahle - Mecklar including two new substations. Length: 210km. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 90. 170 | Großgartach (DE) | Hüffenhardt (DE) | New 380kV OHL. Length: 23km. Included with the project : 1 new 380kV substation, 2 transformers. | [10 empty] | under construction | 2012 | Progresses as planned |  | 44
44 | 44. 171 | Hüffenhardt (DE) | Neurott (DE) | Upgrade of the line from 220kV to 380kV. Length: 11km. Included with the project : 1 new 380kV substation. | [10 empty] | planned | 2020 | Progresses as planned |  | 44
44 | 44. 90. 172 | Mühlhausen (DE) | Großgartach (DE) | Upgrading line from 220kV to 380kV. Length:-45km. | [10 empty] | design & permitting | 2014 | Progresses as planned |  | 44
44 | 44. 90. 173 | Hoheneck (DE) | Endersbach (DE) | Upgrading line from 220kV to 380kV. Length:20km. | [10 empty] | design & permitting | 2014 | Progresses as planned |  | 44
44 | 44. 174 | Bruchsal Kändelweg (DE) | Ubstadt (DE) | A new 380kV OHL. Length:6km. | [10 empty] | design & permitting | 2014 | Postponed from one year due to permitting procedures |  | 44
44 | 44.90. 176 | Daxlanden | Eichstetten | Upgrade of transmission capacity of existing 380 kV line (120 km) | [10 empty] | under consideration | 2020 | Progresses as planned |  | 44
44 | 44. 178 | Baden-Württemberg, Süden & Nordosten (DE) |  | Installation of 2x250 MVAr 380kV capacitance banks. | [10 empty] | under construction | 2014 | One more bank in addition. Two have already been installed. Projects realised earlier because the need for reactive power compensation became urgent. |  | 44
44 | 44. 179 | Rommerskirchen (DE) | Weißenthurm (DE) | New line, extension of existing and erection of substations, erection of 380/110kV-transformers. Total line length: 100km. | [10 empty] | under construction/design & permitting | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. 181 | Dauersberg (DE) | Limburg (DE) | New 380kV double circuit OHL, extension of existing of substations, Total line length: 20km. | [10 empty] | under construction/design & permitting | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. 182 | Kriftel (DE) | Obererlenbach (DE) | New 400 kV double circuit OHL Kriftel - Obererlebenbach in existing OHL corridor. Length: 11 km | [10 empty] | planned | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. A80 | Area of West Germany (DE) |  | Installation of several 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | under consideration | long term | New investment in TYNDP, because of additional needs for RES integration (combined with SoS) |  | 44
44 | 44. 183 | Wehrendorf (DE) |  | Installation of 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 184 | Bürstadt (DE) |  | Installation of 2 x 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 185 | Area of Muensterland and Westfalia (DE) |  | New lines and installation of additional circuits, extension of existing and erection of several 380/110kV-substations. Total length: ca. 110km. | [10 empty] | design & permitting | long term | Delays due to authorization process. |  | 44
44 | 44. 186 | Gütersloh (DE) | Bechterdissen (DE) | New lines and installation of additional circuits, extension of existing and erection of 380/110kV-substation. Total line length:27km. | [10 empty] | under construction | mid term | Delays due to authorization process. |  | 44
44 | 44. 187 | Area of West-Rhineland (DE) |  | New lines and installation of additional circuits, extension of existing and erection of several 380/110kV-substations. | [10 empty] | under construction | 2013 | Progresses as planned |  | 44
44 | 44. 188 | Kruckel (DE) | Dauersberg (DE) | New lines, extension of existing and erection of several 380/110kV-substations. Total line length: 130km. | [10 empty] | planned | long term | Progresses as planned |  | 44
44 | 44. A78 | Pkt. Metternich (DE) | Niederstedem (DE) | Construction of new 380kV double-circuit OHLs, decommissioning of existing old 220kV double-circuit OHLs, extension of existing and erection of several 380/110kV-substations. Length: 108km. | [10 empty] | planned | long term | New investment in TYNDP | RES integration/ Market integration especially east-west-direction | 44
44 | 44. A77 | Area of South-Wuerttemberg (DE) |  | Construction of new 380kV double-circuit OHLs, decommissioning of existing double-circuit OHLs, extension of existing 380-kV-substations. Length: ca. 60km. | [10 empty] | planned | long term | New investment in TYNDP | RES integration combined with pump storage in the alp region (market) / increasing of the NTC DE-CH/AT | 44
44 | 44. 190 | Saar-Pfalz-Region (DE) |  | New lines, extension of existing and erection of several 380/110kV-substations. Upgrade of an existing line from 220 to 380 kV | [10 empty] | planned | long term | Delays due to authorization process. | SoS (Neub. Frltg Fraulaut-Saarwellingen) combined with RES integration | 44
| 44. A155 | Conneforde (DE) | Unterweser (DE) | Upgrade of 230-kV-circuit Unterweser-Conneforde to 400kV , Line length: 32 km. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A156 | Dollern (DE) | Elsfleht/West (DE) | New 400 kV line in existing OHL corridor Dollern - Elsfleht/West Length:100 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A157 | Dollern (DE) | Landesbergen (DE) | New 400 kV line in existing OHL corridor Dollern-Sottrum-Wechold-Landesbergen (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A158 | Hamm/Uentrop (DE) | Kruckel (DE) | Extension of existing line to a 400 kV single circuit OHL Hamm/Uentrop - Kruckel. Length: 60 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A159 | Pkt. Blatzheim (DE) | Oberzier (DE) | New 400 kV double circuit OHL Pkt. Blatzheim - Oberzier including extension of existing substations. Length 16 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A160 | Urberach (DE) | Daxlanden (DE) | New line and extension of existing line to 400 kV double circuit OHL Urberach - Pfungstadt - Weinheim - Daxlanden including extension of existing substations. Length: 219 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A161 | Bürstadt (DE) | Daxlanden (DE) | New line and extension of existing line to 400 kV double circuit OHL Bürstadt - Lambshein - Daxlanden including extension of existing substastions. Length: 134 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A162 | Großgartach (DE) | Endersbach (DE) | Extension of existing 400-kV-line Großgartach - Endersbach. (Lenght: 32 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
44 | 44. 175 | Birkenfeld (DE) | Ötisheim (DE) | A new 380kV OHL. Length:11km. | [10 empty] | planned | 2020 | New investment in TYNDP |  | 44
44 | 44. 189 | Niederrhein (DE) | Utfort (DE) | New 400 kV double-circuit OHL Niederrhein-Utfort (24 km). | [10 empty] | under consideration | long term | New investment in TYNDP |  | 44
45 | 45. 90. 177 |  |  |  | 5000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 |  |  | 0 | The investment contributes both to project 45 and project 90. For the technical description see project 90. | This project helps accommodating the increasing flows coming mainly form RES in NE DE to South DE and to the Alps.
45 | 45. 191 | Neuenhagen (DE) | Vierraden (DE) | Project of new 380kV double-circuit OHL Neuenhagen-Vierraden-Bertikow with 125km length as prerequisite for the planned upgrading of the existing 220kV double-circuit interconnection Krajnik (PL) – Vierraden (DE Hertz Transmission). | [10 empty] | design & permitting | 2013/2015 | Project in permitting phase, strong local resistance |  | 45
45 | 45. 193 | Halle/Saale (DE) | Schweinfurt (DE) | New 380kV double-circuit OHL between the substations Vieselbach-Altenfeld-Redwitz with 215km length combined with upgrade between Redwitz and Grafenrheinfeld (see project 153). The Section Lauchstedt-Vieselbach has already been commissioned. Support of RES integration in Germany, annual redispatching cost reduction, maintaining of security of supply and support of the market development. The line crosses the former border between Eastern and Western Germany and is right downstream in the main load flow direction. The project will help to avoid loop flows through neighboring grids. | [10 empty] | design & permitting | mid term | Investment partly completed, strong local public resistance- delay due to permitting process |  | 45
45 | 45. 197 | Neuenhagen (DE) | Wustermark (DE) | Construction of new 380kV double-circuit OHL between the substations Wustermark-Neuenhagen with 75km length. Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | under construction | mid term | Investment partly under construction and partly in permitting phase. Expected date of commissioning was adjusted due to long permitting process and strong local public resistance. |  | 45
45 | 45. 199 | Western Pomerania (DE) | Uckermark North (DE) | Construction of new 380kV double-circuit OHLs in North-Eastern part of 50HzT control area and decommissioning of existing old 220kV double-circuit OHLs, incl. 380-kV-line Bertikow-Pasewalk (30 km). Length: 135km.Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015 | Progresses as planned |  | 45
45 | 45. 200 | Lubmin (DE) | Erfurt area (DE) | 380-kV-grid enhancement and structural change area Lubmin-Stralsund and area Magdeburg/Wolmirstedt, incl. 380-kV-line Güstrow-Wolmirsted (195 km) | [10 empty] | planned | long term | Progresses as planned |  | 45
45 | 45. 202 | Area upper Lausitz(DE) | Area Gera(DE) | Upgrading existing double-circuit 380kV OHL in the South-Eastern part of the control area of 50Hertz Transmission. Bärwalde-Schmölln length approx.. 50km. Support of RES and conventional generation integration in North-Eastern Germany, maintaining of security of supply and support of market development. | [10 empty] | design & permitting | 2017 | Progresses as planned |  | 45
45 | 45. 204 | Calbe (DE) |  | Construction of new 380kV double-circuit OHL in substation Calbe for double connection/loop into an existing line. | [10 empty] | planned | mid term / long term | The evolution of this investment depends on the development of the power plant in the area. The date mentioned in the TYNDP 2010 was a typing mistake. |  | 45
45 | 45. 205 | Fördertsedt (DE) | Area Magdeburg(DE) | Construction of new 380kV double-circuit OHL from the substation Förderstedt with 20 km length for double connection/loop in for Förderstedt; Reinforcement of existing switchgear, Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015/2020 | Progresses as planned |  | 45
45 | 45. 206 | Area Leipzig(DE) | Area Chemnitz(DE) | Construction of new double-circuit 380-kV-overhead line in existing corridor Röhrsdorf-Remptendorf (103 km) | [10 empty] | under consideration | 2020 | Progresses as planned |  | 45
45 | 45. 207 | Substations in South-Western part of 5 Hertz Transmission control area (DE) |  | Construction of new 380kV substation in Southern Magdeburg area and restructuring of existing 220kV equipment. total length: aprox .50 km | [10 empty] | planned | long term | Some of the investments are to be commissioned by the mid term and the some by long term. |  | 45
45 | 45. 208 | Lines and Substations in South-Western part of 5 Hertz Transmission control area (DE) |  | Construction of new 380kV double-circuit OHL in existing corridor Pulgar-Vieselbach (103 km) Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015/2020 | Progresses as planned |  | 45
45 | 45. 209 | Substations in 5 Hertz Transmission control area |  | Extension of existing and erection of new 380 kV-substations and several 380/110kV-substations, incl. reactive power compensation devices. | [10 empty] | design & permitting | mid term | This investment includes several substations in the control area of 50Hertz Transmission control area. Present status varies form design & permitting, planning to under consideration and the date of commissioning varies from short/mid to long term. |  | 45
| 45. A163 | Wolmirstedt (DE) | Wahle (DE) | New double circuit OHL 380 kV; Line length 111 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A164 | Vieselbach (DE) | Mecklar (DE) | New double circuit OHL 400 kV line in existing OHL corridor . (129 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A165 | Mecklar (DE) | Grafenrheinfeld (DE) | New double circuit OHL 400-kV-line (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A166 | Altenfeld (DE) | Grafenrheinfeld (DE) | New double circuit OHL 400-kV-line (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A169 | Grafenrheinfeld (DE) | Grossgartach (DE) | Additional 380 Kv circuit on a existing lines. Length: 160 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A167 | Redwitz (DE) | Schwandorf (DE) | New double circuit OHL 400 kV line in existing OHL corridor Redwitz-Mechlenreuth-Etzenricht-Schwandorf (185 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A168 | Raitersaich (DE) | Isar (DE) | New 400 kV line in existing OHL corridor Raitersaich - Ludersheim - Sittling - Isar (160 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
45 | 45. 153 | Redwitz (DE) | Grafenrheinfeld (DE) | Upgrade of 230kV connection Redwitz - Grafenrheinfeld to 400kV, including new 400kV switchgear Eltmann. Line length: 97km. | [10 empty] | design & permitting | mid term | Investment delay due to delay in the implementation of the line Halle-Schweinfurt(investment 45. 193) |  | 45
45 | 45. 154 | Redwitz (DE) |  | New 500 MVAr SVC in substation Redwitz. | [10 empty] | planned | mid term | Progresses as planned |  | 45
45 | 45. 155 | Raitersaich (DE) |  | New 500 MVAr SVC in substation Raitersaich. | [10 empty] | planned | mid term | Progresses as planned |  | 45
45 | 45. 47. 158 | [15 empty] | 0 | The investment contributes both to project 45 and project 47. For the technical description see project 47. | 45
46 | 46. 194 | wind farm cluster Baltic Sea East (DE) | Lüdershagen/ Lubmin (DE) | Offshore wind farm connection project (by AC-cables on transmission voltage level or by clustering with DC connections) has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. | >2000 | 4 | 1 | [6 empty] | 1 | design & permitting | 2012-2020 | This investment includes several connections of offshore wind farms in the eastern part of the Baltic Sea. The present expected date of commissioning varies from 2012 to 2020. |  | The integration of offshore wind generation in the Baltic Sea.
46 | 46. 195 | wind farm cluster Baltic Sea West (DE) | Bentwisch (DE) | Offshore wind farm connection project (by AC-cables on transmission voltage level or by clustering with DC connections) has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. | [10 empty] | design & permitting | 2013-2020 | This investment includes several connections of offshore wind farms in the western part of the Baltic Sea. The present expected date of commissioning varies from 2013 to 2020. |  | 46
47 | 47. A76 | Vöhringen / Leupolz (DE) | Westtirol (AT) | Upgrade of an existing OHL to 380 kV, extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. Transmissions routs Vöhringen - Westtirol and Pkt. Woringen - Memmingen. Length: 114 km. This project will increase the current power exchange capacity between the DE, AT and CH. | >2000 | 1 | 2 | [6 empty] | 3 | planned | long term | New investment in TYNDP |  | The reinforcement of the interconnection between Austria and Germany. Also the support the interaction between the RES in Northern Europe(mainly DE) with the pump storage in the Austrian Alps. The project scheduling is not related only to the network needs, but even to the feasibility and to the authorization process (the possibility to anticipate specific projects could be evaluated in the future considering the three above mentioned elements).
47 | 47. 158 | Irsching (DE) | Ottenhofen (DE) | Upgrade of 230kV connection Irsching - Ottenhofen to 400kV, including new 400kV switchgear Zolling. Length 76km. | [10 empty] | planned | mid term | Progresses as planned | The investment contributes also to project 45. | 47
47 | 47. 212 | Isar / Ottenhofen (DE) | St. Peter (AT) | New 400kV double circuit OHL Isar - St. Peter including new 400kV switchgears Altheim, Simbach and St. Peter, and one new 400/230kV transformer in substation Altheim and fourth circuit on line Isar - Ottenhofen. Line length: 90km. | [10 empty] | design & permitting | 2017 | Progresses as planned |  | 47
47 | 47. 26. 216 | St. Peter (AT) | Tauern (AT) | Completion of the 380kV-line St. Peter - Tauern. This contains an upgrade of the existing 380kV-line St. Peter - Salzburg from 220kV-operation to 380kV-operation and the erection of a new internal double circuit 380kV-line connecting the substations Salzburg and Tauern (replacement of existing 220kV-lines on optimized routes). Moreover the erection of the new substations Wagenham and Pongau and the integration of the substations Salzburg and Kaprun is planned. Line length: 130km. | [10 empty] | design & permitting | 2017/2019 | Preparation for the permitting procedure is ongoing. APG is making efforts to set the 380-kV-Salzburg-line 2017 into service. Depending on possible delays during the permitting procedure the commissioning is expected between 2017 and 2019 | The investment contributes also to project 26. | 47
47 | 47. 26. 218 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 47
47 | 47. 219 | Westtirol (AT) | Zell-Ziller (AT) | Upgrade of the existing 220kV-line Westtirol - Zell-Ziller and erection of additional 220/380kV-Transformers. Line length: 105km. | [10 empty] | partly under construction | 2013-2020 | Project consists of several measures and is on schedule |  | 47
47 | 47. 26. 220 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 47
47 | 47. 221 | St. Peter (AT) | Ernsthofen (AT) | Upgrade from 220kV-operation to 380kV and erection of a 380kV-Substation in Ernsthofen and St. Peter. | [10 empty] | under construction | 2013 | The project is on schedule. Permissions are obtained. Commissioning is expected for 2013 |  | 47
57 | 57. 320 | Dargoleza (PL) |  | A new AC 400/110kV (450 MVA) substation between existing substations Słupsk and Żarnowiec in Northern Poland. New substation Dargoleza is connected by splitting and extending of existing 400kV line Słupsk - Dargoleza. | 3000 | 4 | 1 | [6 empty] | 2 | planned | 2020 | The new substation Dargoleza is required for the connection new wind generation in Northern Poland. The time horizon for comissioning of this investment has been changed due to change in wind farms connection schedule in the region. |  | Wind – the infrastructure in this project assures reliable connection of 3000 MW of wind generation in northern Poland. It also allows the evacuation of power in the southern direction.
57 | 57. 328 | Piła Krzewina (PL) | Bydgoszcz Zachód (PL) | New 84km 400kV double circuit 2x1870 MVA OHL interconnection line Piła Krzewina - Bydgoszcz Zachód temporarily on 220kV. | [10 empty] | design & permitting | 2016 | The time schedule of the project was shifted to meet the schedule of the RES (wind) generation connection. This one year delay in the plans appeared after updating of the NDP. The change in the NDP introduced a double circuit. |  | 57
57 | 57. 329 | Żydowo (PL) | Słupsk (PL) | A new AC 400/110kV substation next to existing 220/110kV substation in Northern Poland with transformation 400/110kV 450 MVA. New substation Żydowo is connected by new 70km 400kV 2x1870 MVA OHL double circuit lines Żydowo - Słupsk and Żydowo - Gdańsk Przyjaźń. Dismantling of existing 220/110kV transformers + Upgrade of substation SŁupsk | [10 empty] | planned | 2020 | The date of commissioning evolved due to regulatory, social and environmental issues. The investment also foresee upgrade works in substation Słupsk. |  | 57
57 | 57. 330 | Żydowo (PL) | Gdańsk Przyjaźń (PL) | A new AC substation in Gdańsk Agglomeration Area. New substation Gdańsk Przyjaźń is connected by splitting and extending of one circuit of existing line Żarnowiec - Gdańsk Błonia and new 150km 400kV 2x1870 MVA double circuit OHL line Żydowo - Gdańsk Przyjaźń with one circuit from Żydowo to Gdańsk temporarily on 220kV after dismantling of 220kV line Żydowo - Gdańsk. | [10 empty] | planned | 2020 | The date of commissioning evolved due to regulatory, social and environmental issues. |  | 57
57 | 57. 352 | Dunowo (PL) | Plewiska (PL) | Construction of a new double circuit 400kV OHL Dunowo - Żydowo (2x1870 MVA) partly using existing 220kV line + Construction of a new 400kV OHL Plewiska - Piła Krzewina - Żydowo (2x1870 MVA); single circuit temporarily working as a 220kV + A new AC 400kV switchgear in existing substation Pila Krzewina + upgrade of substation Dunowo | [10 empty] | design & permitting | 2020 | Progressed as planned. The investment also foresee upgrade works in substation Dunowo. |  | 57
58 | 58. 353 | Krajnik (PL) | Baczyna (PL) | Construction of a new double circuit 400kV OHL Krajnik - Baczyna (2x1870 MVA, 91km); single circuit temporarily working at 220kV on Krajnik - Gorzów part + New substation 400kV Baczyna will be connected by splitting and extending existing line Krajnik-Plewiska + Upgrading of limitations line Krajnik - Plewiska. | >1000 | 1 | 2 | [6 empty] | 2 | planned | 2020 | Progresses as planned |  | Bridge – third interconnection between Poland and Germany.
58 | 58. 355 | Mikułowa (PL) | Świebodzice (PL) | Double circuit line 220kV Mikułowa-Świebodzice will be upgraded to 400kV - single circuit temporarily working at 220kV. | [10 empty] | planned | 2020 | Progresses as planned |  | 58
58 | 58. A67 | Gubin (PL) |  | New 400 kV substation planned near the PL-DE border. The substation will be connected to planned line Eisenhüttenstadt (DE) - Plewiska (PL) creating new lines Eisenhüttenstadt (DE) - Gubin (PL) and Gubin (PL) - Plewiska (PL). | [10 empty] | planned | 2020 | New investment in TYNDP | This new substation on the third DE-PL connection is necessary for future generation connection while ensuring interconnection capability. | 58
58 | 58. 140 | Eisenhüttenstadt (DE) | Plewiska (PL) | New 400kV double circuit OHL Eisenhüttenstadt (DE) - Plewiska (PL) including the construction of new substation Plewiska Bis (PL) | [10 empty] | planned | 2020 | Progresses as planned |  | 58
59 | 59. 368 | Ełk (PL) | PL-LT border (LT) | Construction of a new 400kV OHL Ełk to PL-LT border. (2x1870 MVA, 108km). | 1000 | 1 | 5 | South LT and NE/central PL | [5 empty] | 3 | design & permitting | 2015 | Progresses as planned |  | “LitPol Link” project. Interconnection of Lithuanian power system with Polish power system via Back to Back station. This project allows integration of Baltics to the internal European power market,
59 | 59. 369 | Siedlce Ujrzanów (PL) | Miłosna (PL) | Construction of a new 400kV OHL Siedlce Ujrzanów - Miłosna (1870 MVA, 84km) + A new AC 400kV switchgear in existing substation Siedlce Ujrzanow with transformation 400/110kV 400 MVA. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 59
59 | 59. 370 | Ełk (PL) | Łomża (PL) | Construction of a new 400kV double circuit OHL Ełk - Łomża (2x1870 MVA, 95km) + A new AC 400kV switchgear in existing substation Elk + A new 400 kV AC substation Łomża | [10 empty] | design & permitting | 2015 | Łomża has been elected as end substation for the project and the technical description is adapted accordingly. Progresses as planned otherwise. |  | 59
59 | 59. 371 | Ostrołęka (PL) | Narew (PL) | Construction of a new 400kV OHL Ostrołęka-Łomża-Narew (1870 MVA, 120km) + A new AC 400kV switchgear in existing substation Ostroleka (in two stages) with transformation 400/220kV 500 MVA and with transformation 400/110kV 400 MVA + extension of 400 switchgear in substation Narew. | [10 empty] | design & permitting | 2015 | Progressed as planned. The investment also foresee extension works in substation Narew. |  | 59
59 | 59. 372 | Oltarzew (PL) |  | A new AC substation with two transformers 400/220kV 2x500 MVA and one 400/110kV 330 MVA will be connected by splitting 400kV line Rogowiec-Miłosna and Miłosna-Płock and 220kV line Mory-Sochaczew and Mory-Janów. | [10 empty] | under construction | 2015 | Progresses as planned |  | 59
59 | 59. 373 | Ostrołęka (PL) | Stanisławów (PL) | Single circuit line 220kV Ostrołęka-Miłosna will be partly upgraded to double circuit line 400kV (2x1870 MVA, 106km) with development of Ostrołęka 400kV substation + New substation 400kV Stanisławów will be connected by splitting and extending existing line Miłosna-Narew and Miłosna-Siedlce. | [10 empty] | design & permitting | 2020 | Progresses as planned |  | 59
59 | 59. 374 | Kozienice (PL) | Siedlce Ujrzanów (PL) | Existing single circuit line will be upgraded to 400kV line in the same direction (1870 MVA, 90km) + upgrade of Kozienice substation to connect the new line | [10 empty] | design & permitting | 2020 | Progressed as planned. The investment also foresee extension works in substation Kozienice |  | 59
59 | 59. 375 | Płock (PL) | Olsztyn Mątki (PL) | New single circuit line 400kV (1870 MVA, 180km) with development of Olsztyn Mątki 400kV substation. | [10 empty] | design & permitting | 2020 | Progresses as planned |  | 59
59 | 59. 376 | Alytus (LT) | PL-LT border (PL) | Construction of Back-to-Back convertor station near Alytus 330kV substation. Construction of double circuit 400 kV OHL between Alytus and PL – LT border (2 x 1,870 MVA, 51 km). | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 59
59 | 59. 379 | Kruonis (LT) | Alytus (LT) | New double circuit 330kV OHL (2x1080 MVA, 53km). | [10 empty] | planned | 2015 | Progresses faster than intially planned to support the LitPol project |  | 59
60 | 60. 377 | Klaipeda (LT) | Telsiai (LT) | New single circuit 330kV OHL (943 MVA, 85km). | 700 | 3 | 3 | West LV region | [5 empty] | 2 | under construction | 2014 | Project delayed because of land renting issues. |  | “Nordbalt“ project. Planned DC connection between Lithuania and Sweden. The project will connect the Baltic grid to the Nordic and integrate the Baltic countries with the Nordic electricity market, increases security of supply. Possibility to connect offshore wind farms as well.
60 | 60. 378 | Panevezys (LT) | Musa (LT) | New single circuit 330kV OHL (1080 MVA, 80km). | [10 empty] | planned | 2018 | Project postponed after investment portfolio optimization |  | 60
60 | 60. 383 | Klaipeda (LT) | Nybro (SE) | (NordBalt) A new 300kV HVDC VSC partly subsea and partly underground cable between Lithuania and Sweden. (440km). | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 60
60 | 60. 62. 384 | RigaCHP1 (LV) | Imanta (LV) | A new 12.5km AC 330kV cable will be built from RigaCHP1 substation to Imanta substation. Both substations will be reconstructed, according new line connecting. New cable will be underground and one part will be underwater (under Daugava river). Expected capacity: 880MW. | [10 empty] | under construction | 2012 | Progresses as planned | The investment contributes also to project 62 | 60
60 | 60. A52 | Ekhyddan (SE) | Nybro/Hemsjö (SE) | New single circuit 400 kV OHL | [10 empty] | under consideration | 2019 | New investment in TYNDP |  | 60
60 | 60. 62. 385 | Grobina (LV) | Imanta (LV) | Kurzeme roject a Latvian grid reinforcement roject with new 330kV OHL construction and connection to the Riga node. New 330kV OHL construction mainly instead of the existing 110kV double circuit line route, 110kV line will be renovated at the same time and both will be assembled on the same towers. Length 380km, Capacity 800MW | [10 empty] | design & permitting | 2018 | Investment delays due to authorization process and the extensive works. | The investment contributes also to project 62 | 60
61 | 61. 380 | Visaginas (LT) | Kruonis (LT) | New single circuit 330kV OHL (1080 MVA, 200km). | 1400 | 4 | 5 | [6 empty] | 1 | planned | 2020 | Progresses as planned |  | “New NPP” project. Grid development for connection of new Lithuanian nuclear power plant planned in Visaginas to the power system. This project allows safe and reliable integration of new NPP to the power system.
61 | 61. 382 | Vilnius (LT) | Neris (LT) | New single circuit 330kV OHL (943 MVA, 50km). | [10 empty] | planned | 2020 | Progresses as planned |  | 61
62 | 62. 60. 384 |  |  |  | 450-600 | 1 | 1 | Riga region | [5 empty] | 1 |  |  | 0 | The investment contributes both to project 62 and project 64. For the technical description see project 62 | This project will increase the transfer capability between Estonia and Latvia and will accommodate RES generation in the Baltic Sea. This will be the 3rd corridor between these countries.
62 | 62. 60. 385 | [15 empty] | 0 | The investment contributes both to project 62 and project 64. For the technical description see project 62 | 62
62 | 62. 386 | Kilingi-Nomme(EE) | RigaCHP2(LV) | Estonia-Latvia third interconnection will consist of 330 kV AC OHL Harku-Lihula-Sindi in Estonian part and OHL between Kilingi-Nõmme substation in Estonia and TEC2 substation in Latvia. The third interconnection allows to increase the NTC between Estonia and Latvia additionally in the range of 450 to 600 MW . | [10 empty] | planned | 2020 | Progresses as planned |  | 62
62 | 62. 387 | Tartu (EE) | Sindi (EE) | A new 162km internal connection will be established on existing route resulting in double circuit line with 2 different voltages (330kV / 110kV). | [10 empty] | under construction | 2014 | Progresses as planned |  | 62
62 | 62. 388 | Harku (EE) | Sindi (EE) | New double circuit OHL with 2 different voltages 330 kV and 110 kV and with capacity 1200 MVA/240 MVA and a length 140 km. Major part of new internal connection will be established on existing right of way on the Western part of Estonian mainland. | [10 empty] | design & permitting | 2018 | Progresses as planned |  | 62
63 | 63. 389 | Eesti (EE) | Püssi (EE) | Reinforcement of existing 57km single circuit 330kV OHL. Expected capacity:1200 MVA. | 650 | 3 | 2 | NW Estonia | [5 empty] | 2 | commissioned | commissioned | Commissioned |  | Estlink2 ; The main driver for this cluster is integration need of Electricity Market. This project will increase the transfer capability between Estonia and Finland and will accommodate RES generation in the North of Estonia and will increase the SOS in the Baltics.
63 | 63. 390 | Balti (EE) | Püssi (EE) | Reconstruction of 68km single circuit 330kV OHL. | [10 empty] | commissioned | commissioned | Commissioned |  | 63
63 | 63. 391 | Püssi (EE) | Anttila (FI) | A new HVDC (450kV) connection will be built between Estonia and Finland. On the Finnish side, a 14km DC overhead line will be built to a new substation Anttila where the converter station will be placed. On the Estonian side, a 11km DC cable line will be built to a existing substation Püssi where the converter station will be placed. length of marine cable is 140km. Expected capacity: 650MW. | [10 empty] | under construction | 2014 | The expected date of commissioning is beginning of 2014, postponed a few months compared to the preliminary estimate end of 2013. |  | 63
64 | 64. 392 | Yllikkälä (FI) | Huutokoski (FI) | New 155km single circuit 400kV OHL and renovation of 400kV substations in Yllikkälä and Huutokoski. Expected capacity: 1850 MVA. | 700-1400 | 3 | 2 | West coast Finland | [5 empty] | 1 | under construction | 2013 | Progresses as planned. Expected date of commission is beginning of 2013. |  | Several 400 kV AC lines are planned in Finland to be built to increase the North-South transmission capacity thus enabling the integration of new renewable and conventional generation in northern Finland and to compensate the dismantling of the obsolescent exiting 220 kV lines. The commissioning of the lines is scheduled to take place in segments both in mid and long term.
64 | 64. 393 | Seinäjoki Ulvila Ventusneva (FI) | Tuovila (FI) Kristinestad (FI) Pyhänselkä (FI) | Four new single circuit 400kV OHL are part of project in upgrading Ostrobothnian 220kV system into 400kV, and strengthening the 400 kV grid in Northern Finland. Commissioning of first section in year 2011, second in 2014 third in ca. 2018 and fourth ca. 2020. total length of lines: 520 km. Expected capacity: 1850 MVA. | [10 empty] | under construction | 2011/2020 | Project has progressed as planned. Since TYNDP 2010 Seinäjoki-Tuovila has been constructed and Ulvila-Kristinestad has progressed to design and permitting phase. Keminmaa-Pyhänselkä is now presented as a separate investment item. |  | 64
64 | 64. A62 | Pyhänselkä (FI) | Petäjävesi or Vihtavuori (FI) | New single circuit 400 kV OHLs will be built from middle Finland to Oulujoki Area to increase the capacity between North and South Finland. | [10 empty] | design & permitting | 2020 | New investment in TYNDP |  | 64
65 | 65. 394 | Hikiä (FI) | Forssa (FI) | New 80km single circuit 400kV OHL and building of 400 kV substation in Forssa. | 800 | 2 | 4 | SW Finland | [5 empty] | 1 | design & permitting | 2015 | Progresses as planned |  | Reinforcements due to changed exchange patterns and reliable grid operation of South-West Finland.
65 | 65. A63 | Forssa (FI) | Lieto (FI) | New 67km single circuit 400 kV OHL. | [10 empty] | under consideration | 2017 | New investment in TYNDP
66 | 66. 400 | Ekhyddan (SE) | Barkeryd (SE) | New single circuit 400kV OHL. | 1250 | 4 | 1 | [6 empty] | 2 | design & permitting | 2017 | Progresses as planned |  | The new subsea connection to the island of Gotland will be two connections with a capacity of 500 MW for each cable.
66 | 66. 401 | Västervik (SE) | Gotland (SE) | New DC subsea cable interconnection ±300kV (2*500 MW). | [10 empty] | design & permitting | 2017 -2021 | The first cable is progressing as planned but the second cable is planned to be in commission after 2017 due to adjustments to RES. | The new subsea connection to the island of Gotland will be two connections with a capacity of 500 MW for each cable. The first cable is planned to be in commission 2017 and the second is planned to be in commission between 2020 and 2021. | 66
67 | 67. 402 | Barkeryd (SE) Hallsberg (SE) | Tveiten (NO) Hurva (SE) | "South West link" consisting of three main parts: 1) New 400kV line between Hallsberg and Barkeryd (SE) 2) New double HVDC VSC underground cable and OHL between Barkeryd and Hurva (SE) 3) New double HVDC VSC line between Barkeryd (SE) and Tveiten (NO). The project also include new substations and converter stations in the connection points line double circuit new OHL Hallsberg - Barkeryd 170km, underground VSC Barkeryd - Hurva 250km and VSC Barkeryd - Tveiten with 103km on the Norwegian side. Expected capacity: 1200MW. | 1400 (E-W), 1200 (N-S) | 3 | 2 | [6 empty] | 3 | design & permitting | 2014-2019 | Commissioning date updated after bilateral negotiations between the two countries. Hallsberg-Barkeryd-Hurva expected in 2014; Barkeryd-Tveiten in 2019 |  | 5 investments of HVDC and AC lines in Sweden and Norway as well as between the countries, resulting in increased GTC and market integration
67 | 67. 411 | Rød (NO) | Sylling (NO) | Voltage upgrading of existing single circuit 300kV OHL Rød-Tveiten-Flesaker-Sylling in connection with the new HVDC line to Sweden, the Syd Vest link. | [10 empty] | design & permitting | 2018/2020 | Investment postponed, especially because of long permitting processes. |  | 67
67 | 67. 412 | Rød (NO) - Sylling (NO) - Flesaker (NO) - | Hasle (NO) Tegneby (NO) Tegneby (NO) | Reinvestment and capacity increase Oslofjord 400kV subsea cables. Three cables: Filtvedt - Brenntangen, Solberg - Brenntangen, and Teigen - Evje. | [10 empty] | design & permitting | 2015 | Investment delayed, especially because of long permitting processes. One cable is under construction. |  | 67
68 | 68. 421 | Ofoten (NO) | Balsfjord (NO) | New 160km single circuit 400kV OHL. | 350-1500 | 2 | 1 | Northern Norway | [5 empty] | 2 | design & permitting | 2016 | Investment delayed, especially because of long permitting processes. |  | The main purpose of this project is to secure the northern part of NO.
68 | 68. 422 | Balsfjord (NO) | Hammerfest (NO) | New 360 km single circuit 400kV OHL. | [10 empty] | design & permitting | 2018 | Investment delayed, especially because of long permitting processes.
68 | 68. 423 | Skaidi (NO) | Varangerbotn (NO) | New 230 km single circuit 400kV OHL. | [10 empty] | planned | 2022 | Investment postponed, especially because of long permitting processes.
70 | 70. 405 | Kristiansand (NO) | Rød (NO) | Voltage upgrading of an existing single circuit 300kV OHL and a new section of OHL between Rød and Bamle. Total length: 175km. | 700 | 5 | 2 | [6 empty] | 2 | design & permitting | 2014 | Progresses as planned |  | Market integration and RES integration.
70 | 70. 426 | Kristiansand (NO) | Tjele (DK) | Skagerak 4: 4th HVDC connection between Southern Norway and Western Denmark, built in parallel with the existing 3 HVDC cables; new 700MW including 230km 500kV DC subsea cable. | [10 empty] | Under construction | 2014 | Progresses as planned |  | 70
71 | 71. 427 | Endrup (DK) | Eemshaven (NL) | COBRA: New single circuit HVDC connection between Jutland and the Netherlands via 350km subsea cable; the DC voltage will be up to 320kVand the capacity 600-700MW. | 700 MW | 5 | 2 | [6 empty] | 2 | design & permitting | 2016 | Progresses as planned |  | Cobra
72 | 72. 430 | Revsing (DK) | Landerupgård (DK) | New 18km single circuit 400kV line via cable with capacity of approx. 1200 MW. | 950 | 4 | 1 | DK west and north DE | [5 empty] | 2 | Planned | 2017 | Progresses as planned |  | The main purpose of the project is to integrate and transmit large scale wind power in DK west.
72 | 72. 435 | Endrup (DK) | Revsing(DK) | Upgrade of 50km double-circuit 400kV OHL to reach a capacity of approx. 2000MW. | [10 empty] | design & permitting | 2015 | Earlier date of commissioning than initially expected caused by reprioritization of project. Also one of the substations has been changed: Endrup was replaced by Tjele. |  | 72
72 | 72. 436 | Idomlund (DK) | Endrup (DK) | New 74km single circuit 400kV line via cable with capacity of approx. 1200MW. | [10 empty] | under consideration | 2018/2020 | Envisaged route changed from Idomlund-Tjele to Idomlund-Endrup |  | 72
73 | 73. 432 | Asvæsværket (DK) | Kyndbyværket (DK) | New 60km single circuit 400kV line via cable with capacity of approx. 1200 MW. | >1000 | 4 | 4 | [6 empty] | 1 | design & permitting | 2014 | Progresses as planned |  | The project will increase the stability of the DK eastern power system and allow for larger transmission and transit.
73 | 73. 433 | Glentegård (DK) | Amagerværket & H.C. Ørstedværket (DK) | New 22km single circuit 400kV line via cable with capacity of approx. 1200MW. | [10 empty] | planned | 2016 | Progresses as planned |  | 73
87 | 87. A53 | Forsmark (SE) | Råsten (SE) | New 50km single circuit 400kV OHL | 1215 | 2 | 4 | [6 empty] | 2 | design & permitting | 2019 | New investment in TYNDP |  | Several 400 kV AC lines and stations due to increase of nuclear power and RES, result in increased GTC
87 | 87. A54 | Råsten (SE) | Hamra (SE) | New 85km single circuit 400kV OHL | [10 empty] | design & permitting | 2019 | New investment in TYNDP |  | 87
87 | 87. A55 | Forsmark (SE) | Stackbo (SE) | New 70km single circuit 400kV OHL | [10 empty] | design & permitting | 2018 | New investment in TYNDP |  | 87
87 | 87. A56 | Ängsberg (SE) | Horndal (SE) | New 55km single circuit 400kV OHL | [10 empty] | under consideration | 2020 | New investment in TYNDP |  | 87
87 | 87. A57 | Horndal (SE) | Lindbacka (SE) | New 145km single circuit 400kV OHL | [10 empty] | under consideration | 2020 | New investment in TYNDP |  | 87
87 | 87. A58 | Hamra (SE) | Västerås (SE) | New 50km single circuit 400kV OHL | [10 empty] | planned | 2021 | New investment in TYNDP |  | 87
87 | 87. 399 | Vasteras (SE) | Lindbaka (SE) | Upgrade/Replacement of existing single circuit 220kV lines to 400kV. | [10 empty] | under consideration | 2021 | All investments in project 87 has been prioritized and result in new commissioning dates |  | 87
90 | 90. 131 | Bickigen (CH) |  | Addition of a second 400/220kV transformer in an existing substation. | 4000 | 1 | 2 | [6 empty] | 3 | design & permitting | 2012 | Progresses as planned |  | This project increase the transfer capability between FR, DE , AT towards pump storage in CH.
90 | 90. 132 | Mühleberg (CH) |  | Construction of a new 400/220kV substation. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 90
90 | 90. 134 | Bassecourt (CH) | Romanel (CH) | Construction of different new 400kV line sections and voltage upgrade of existing 225kV lines into 400kV lines. Total length: 140km. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 90
90 | 90. 136 | Area of Bodensee (DE, AT, CH) |  | Construction of new lines, extension of existing ones in direction of 400/220/110kV-substation. This project will increase the current power exchange capacity between the DE, AT and CH. The project is expected to increase NTC and Improved the security of supply. | [10 empty] | planned | long term | Progress as planned |  | 90
90 | 90. 129 | Beznau (CH) | Mettlen (CH) | Upgrade of the existing 65km double circuit 220kV OHL to 400kV. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 90
90 | 90. 130 | La Punt (CH) | Pradella / Ova Spin (CH) | Installation of the second circuit on existing towers of a double-circuit 400kV OHL (50km). | [10 empty] | planned | 2017 | Delays due to authorization process. |  | 90
90 | 90. 133 | Bonaduz (CH) | Mettlen (CH) | Upgrade of the existing 180km double circuit 220kV OHL into 400kV. | [10 empty] | under consideration | 2020 | Progresses as planned |  | 90
90 | 90. 44. 170 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 172 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 173 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 176 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 45. 177 | Goldshöfe (DE) | Bünzwangen (DE) | A new 380kV OHL. Length: 45km. | [10 empty] | under consideration | 2020 | Progresses as planned | The investment contributes also to project 45. | 90
92 | 92. 146 | Aachen/Düren region (DE) | Lixhe (BE) | Connection between Germany and Belgium including new 100km HVDC underground cable and extension of existing 380kV-substations. On Belgian side, new 380 kV circuit between Lixhe and Herderen and second 380 kV overheadline in/out from Herderen to Lixhe. In Belgium, addition of 2 transformers 380/150 kV in Lixhe and in Limburg part; | 1000 | 3 | 2 | Northern Belgium | [5 empty] | 2 | design & permitting | 2017 | The project entered design and permitting phase in 2011, technical description has been completed and expected date of comissioning is 2017 | Alegro Project | First Belgium-Germany interconnection. This project enhances security of supply of both BE and DE. This HVDC link in an AC grid brings flexibility and bidirectional power control allowing integration of RES in both countries. This project aims to be a demonstration for HVDC link integration in the AC meshed grid.
93 | 93. 413 | Ørskog (NO) | Fardal (NO) | New 285 km single circuit 400kV OHL. | 2250 | 3 | 3 | South west of Trondheim (county Møre and Romsdal) | [5 empty] | 3 | under construction | 2015 | Investment delayed due to due to long permitting procedure. | The project is key to improve SoS in Mid-Norway: presently, for several N-1 contingencies, load might be disconnected. The project is also the pre-requisite to lift the ban on RES development in the whole area covered by the new line Ørskog - Fardal. | Security of supply for mid-Norway (Møre and Romsdal mainly) and RES integration in western Norway.
93 | 93. 398A | Under consideration (SE) |  | New shunt compensation of OHL. | [10 empty] | under consideration | 2015 | New part of investment 398 in TYNDP 2010 | Investment 398 in TYNDP 2010 have been divided into 398A and 398B. 398B is described in project 104. | 93
93 | 93. 403 | Scandinavia north (SE) | Scandinavia South (SE) | A joint Stattnett & Svenska Kraftnat study north - south reinforcement (AC or VSC), expected length: 400 - 500km under study. | [10 empty] | under consideration | 2025 | Postponed after reprioritization of the project portfolio |  | 93
93 | 93. 414 | Fardal (NO) | Aurland (NO) | Voltage upgrading of existing single circuit 300kV OHL Fardal-Aurland Extension of 413 - Ørskog - Fardal. | [10 empty] | planned | 2020 | Investment postponed, especially because of long permitting processes. |  | 93
93 | 93. 417 | Aura/Viklandet (NO) | Fåberg (NO) | Voltage upgrading of existing single circuit 300kV OHL Aura/Viklandet-Fåberg. | [10 empty] | under consideration | long term | Investment postponed, especially because of long permitting processes. |  | 93
93 | 93. 416 | Klæbu (NO) | Aura/ Viklandet (NO) | Voltage upgrading of existing single circuit 300kV OHL Klæbu-Aura. | [10 empty] | design & permitting | 2018 (2016-2020) | Investment postponed, especially because of long permitting processes. |  | 93
94 | 94. 139 | Vierraden (DE) | Krajnik (PL) | Upgrade of existing 220 kV line Vierraden-Krajnik to double circuit 400 kV OHL. | >1000 | 1 | 2 | [6 empty] | 1 | design & permitting | long term | Expected date of commissioning was adjusted due to long permitting process and strong local public resistance. |  | PSTs – Control of the transits of power on the polish synchronous profile (increase of import capacity, increase of grid operation safety).
94 | 94. A68 | Krajnik (PL) |  | Upgrade 400 kV | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A69 | Mikułowa (PL) |  | Upgrade 400 kV | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A70 | Krajnik (PL) |  | New PST | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A71 | Mikułowa (PL) |  | New PST | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
96 | 96. A64 | Keminmaa (FI) | Pyhänselkä (FI) | Integration of new generation + increased transmission capacity demand. | 1000 | 4 | 1 | [6 empty] | 1 | under consideration | 2019 | New investment in TYNDP, split out from investment 393, and now been moved as a stand-alone project cluster because of his specific benefits. |  | Integration of new generation and increased transmission capacity demand.
97 | 97. A65 | Uusnivala (FI) | Pyhäjoki (FI) | New double circuit 400 kV OHLs | 1600 | 4 | 5 | [6 empty] | 1 | under consideration | 2020 | New investment in TYNDP, required to connect Fennovoimas new 1 250-1 700 MW nuclear power plant that will be built in Pyhäjoki |  | New investment in TYNDP, required to connect Fennovoimas new 1 250-1 700 MW nuclear power plant that will be built in Pyhäjoki
98 | 98. A66 | Rauma (FI) | Forssa (FI) Lieto (FI) Ulvila (FI) | New single circuit 400 kV OHLs | 1600 | 4 | 5 | [6 empty] | 1 | under consideration | 2020 | New investment in TYNDP, required to connect TVO's new 1 000-1 800 MW nuclear power plant that will be built in Olkiluoto. |  | New investment in TYNDP, required to connect TVO's new 1 000-1 800 MW nuclear power plant that will be built in Olkiluoto
99 | 99. 324 | Dobrzeń (PL) | Wrocław/ Pasikurowice (PL) | New 76 km 400kV 2x1870 MVA OHL double circuit line from Dobrzeń to splitted Pasikurowice - Wrocław line + upgrade and extension of 400 kV switchgear in substation Dobrzeń. | 1800 | 4 | 5 | Warsaw and lower Silesia area | [5 empty] | 1 | design & permitting | 2017 | Progresses globally as planned. Technical description and commissioning date have been updated so as to deliver full benefit as from 2017 |  | Dobrzeń - the project introduces new infrastructure (2x400 kV line) to allow power evacuation from two (2x9000 MW) conventional units to be installed in existing power plant Opole. The new line provides power supply for agglomeration Wroclaw, it increases the SoS for this area.
100 | 100. 335 | Ostrołęka (PL) | Olsztyn Mątki (PL) | New 138km 400kV 2x1870 MVA double circuit OHL line Ostrołęka - Olsztyn Mątki after dismantling of 220kV line Ostrołęka - Olsztyn with one circuit from Ostrołęka to Olsztyn temporarily on 220kV. | 1000 | 4 | 5 | [6 empty] | 1 | design & permitting | 2017 | The time schedule of the project was shifted to meet the schedule of the generation connection. |  | Ostrołęka - the new 400 kV line allows power evacuation from new 1000 MW conventional unit to be installed in existing power plant Ostroleka.
101 | 101. 327 | Kozienice (PL) | Ołtarzew (PL) | New 130km 400kV 2x1870 MVA OHL double circuit line Kozienice - Ołtarzew + upgrade and extension of 400 kV switchgear in substation Kozienice for the connection of new line | 1000 | 4 | 5 | Warsaw area | [5 empty] | 1 | design & permitting | 2017 | The time schedule of the project was shifted to meet the schedule of the generation connection. |  | Kozienice - the new 2x400 kV line allows power evacuation from new 1000 MW conventional unit to be installed in existing power plant Kozienice. The new unit is foreseen to supply Warsaw agglomeration area. The project also allows to close the 400 kV ring around Warsaw agglomeration are increasing the SoS significantly.
101 | 101. 338 | Kozienice (PL) | Mory/ Piaseczno (PL) | Replacement of conductors (high temperature conductors). | [10 empty] | under construction | 2014 | Progresses as planned, with commissioning now expected in 2014 |  | 101
102 | 102. A72 | Gdańsk Błonia (PL) |  | Extension and upgrade of an existing 400/110 kV substation Gdańsk Błonia for connection of planned 900 MW power plant. | 2900 | 4 | 5 | [6 empty] | 2 | planned | 2020 | New investment in TYNDP | Power Evacuation North. The upgraded substation will connect a planned 900 MW CCPP. | North - the North-South corridor provides necessary capacity to evacuate the power from new 2900 MW of conventional generation planned to be installed in northern Poland.
102 | 102. 334 | Pątnów (PL) | Grudziądz (PL) | New 174km 400kV 2x1870 MVA double circuit OHL line Pątnów - Grudziądz after dismantling of 220kV line Pątnów - Jasiniec (two parallel lines) and Jasiniec - Grudziądz. One circuit from Pątnów to Grudziądz via Jasiniec temporarily on 220kV. | [10 empty] | design & permitting | 2020 | The time schedule of the project was shifted to meet the schedule of the generation connection. | Power Evacuation North | 102
102 | 102. 326 | Grudziądz (PL) | Gdańsk Przyjaźń (PL) | A new AC 400/110kV substation between existing substation Grudziądz and planned substation Gdańsk Przyjaźń. New substation Pelplin is connected by new 110km 400kV 2x1870 MVA OHL double circuit lines Grudziądz - Pelplin and Pelplin - Gdańsk Przyjaźń after dismantling of 220kV line Jasiniec - Gdańsk. | [10 empty] | planned | 2020 | The time schedule of the project was shifted to meet the schedule of the generation connection. | Power Evacuation North | 102
103 | 103. 145 | Niederrhein (DE) | Doetinchem (NL) | New 400kV line double circuit DE-NL interconnection line. Length:60km. | 13900 | 3 | 1 | NW part of Netherlands | [5 empty] | 3 | design & permitting | >=2013 | Delays due to authorization process. |  | The project reinforces the Dutch grid to accommodate new conventional and renewable generation, to handle new flow patterns and to increase the interconnection capacity between DE and NL"
103 | 103. 438 | Eemshaven (NL) | Diemen (NL) | New 175-200km AC overhead line with capacity of 2x2650 MVA of 380kV. | [10 empty] | design & permitting | 2018 | Delays due to authorization process. |  | 103
103 | 103. 439 | Borssele (NL) | Geertruidenberg (NL) | New 100-130km double-circuit 380kV OHL with 2x2650 MVA capacity. | [10 empty] | design & permitting | 2016 | Delays due to authorization process. |  | 103
103 | 103. 440 | Maasvlakte (NL) | Beverwijk (NL) | New 380 kV double-circuit mixed project (OHL+ underground cable) including approximately 20km of underground cable for 2650 MVA. The cable sections are a pilot project. The total length of cable at 380kV is frozen until more experience is gained. | [10 empty] | under construction | 2016 | Delays due to authorization process. |  | 103
103 | 103. 441 | Zwolle (NL) | Hengelo (NL) | Upgrade of the capacity of the existing 60km double circuit 380kV OHL to reach a capacity of 2x2650 MVA. | [10 empty] | under consideration | long term | Progresses as planned. |  | 103
103 | 103. 442 | Krimpen aan de Ijssel (NL) | Maasbracht (NL) | Upgrade of the capacity of the existing 150km double circuit 380kV OHL to reach a capacity of 2x2650 MVA. | [10 empty] | under consideration | long term | Progresses as planned. |  | 103
104 | 104. 398B | Under consideration (SE) |  | New series compensation of OHL. | 1200 | 2 | 1 | [6 empty] | 2 | under consideration | 2015 | Reprioritization of projects. | Investment 398 in TYNDP 2010 have been divided into 398A and 398B. 398A is described in project 93. | RES integration in mid-Norway (Trøndelag and Nordland) and reinforcement of Swedish internal interconnections in order to facilitate wind power integration in northern Sweden
104 | 104. 415 | Namsos (NO) | Klæbu and Storeheia (NO) | New line and voltage upgrade of 286km single circuit 400kV OHL | [10 empty] | design & permitting | 2015 | Delays due to authorization process. | New line and voltage upgrade to facilitate new wind power generation | 104
104 | 104. 418 | Nedre Røssåga (NO) | Namsos (NO) | Upgrade of 70km single circuit 400kV OHL | [10 empty] | design & permitting | 2019 | Investment postponed, especially because of long permitting processes. | Increased capacity between north and mid Norway. Facilitates RES integration | 104
104 | 104. 420 | Storheia (NO) | Orkdal / Trollheim (NO) | New 130km single circuit 400kV OHL | [10 empty] | design & permitting | 2017-2020 | Investment postponed due to long permitting procedure. | New line to facilitate wind power generation | 104
104 | 104. A59 | Råbäcken (SE) | Letsi - Betåsen (SE) | New 55km single circuit 400kV OHL | [10 empty] | under consideration | 2017 | New investment in TYNDP. Will probably be postponed after 2020 due to later development of wind power in the area |  | 104
104 | 104. A51 | Svartisen (NO) | Nedre Røssåga (NO) | New 116km 400kV OHL | [10 empty] | planned | 2020 | New investment in TYNDP | New line to facilitate wind power generation | 104
105 | 105. A60 | Skogssäter (SE) | Stenungsund/Stenkullen (SE) | New 80km single circuit 400kV OHL | 600 | 2 | 1 | [6 empty] | 1 | under consideration | 2019 | New investment in TYNDP |  | This project facilitates the connection of wind power along the Swedish west coast
110 | 110. 424 | Kvilldal (NO) | tbd (GB) | A new 1000MW HVDC bipolar installation connecting Western Norway and Great Britain via 800km subsea cable; DC voltage is to be determined. | 1000-1400 | 1 | 2 | [6 empty] | 3 | design & permitting | 2018/2021 | Capacity revised. Investment postponed, especially because of long permitting processes. |  | Market integration. Facilitate RES integration in southern and western Norway and improve security of supply.
111 | 111. 396 | Finland North (FI) | Sweden North (SE) | Third single circuit 400kV AC OHL between Sweden and Finland. Expected capacity: 1850 MVA. | 700 | 3 | 2 | [6 empty] | 1 | under consideration | 2021 | The projects reinforcing the North-South transmission in the Scandinavia have been prioritized ahead of this project. Based on common estimation project can be delayed to 2021. SvK will evaluate the project and the timetable in ongoing studies |  | Third AC 400 kV cross border line between North-Sweden and North-Finland is under consideration. Strengthening the AC connection between Finland and Sweden is necessary due to new wind power generation, larger conventional units and decommissioning of the existing 220 kV interconnector.
| 58 | Ensdorf (DE) | St. Avold (FR) | Change of conductors on the German part of this single circuit 220kV line (9 km) and installation of a phase-shifter in Ensdorf (DE) 220kV substation. | [10 empty] | commissioned | commissioned | Commissioned
| 168 | Goldshöfe (DE) | Dellmensigen (DE) | Upgrade the line Goldshöfe - Dellmensigen from 220kV to 380kV . Line length:114km. Included with the project : 3x 380kV substations, 2 transformers. | [10 empty] | under construction | 2014 | Investment 168 has been postponed to 2014 due to local resistance against the project in a specific area. The rest of the investment is ready.
| 168a | Region South-West Bavaria (DE) |  | Upgrading the existing 220kV OHL to 380kV,length 100km and the extension of existing substations, erection of 380/110kV-transformers. | [10 empty] | cancelled | cancelled | The project was abandoned - was not seen necessary with the new set of projects in place. Note: in the previous TYNDP the status of the project was under consideration and not planned (printing mistake)
| 192 | Hamburg/Krümmel (DE) | Schwerin (DE) | This 380kV double-circuit OHL project will close the missing gap in North-East German grid infrastructure. Only 65km of new line must be constructed, 22km already exist. | [10 empty] | under construction | 2012/2013 | Commissioning delayed by complex permitting procedure, line is partly constructed, is expected to be commissioned in 2012/2013 short term
| 198 | Wuhlheide (DE) | Thyrow (DE) | Berlin South Ring: replacement of an existing old 220kV double-circuit OHL by a 380kV double-circuit OHL. Length: 50km. | [10 empty] | cancelled | cancelled | Project was depending on the replacement of a CHP power plant based in Berlin, due to a new general CHP-concept the plant size could be adopted and the upgrade of the existing 220-kV connection to 380-kV was not necessary any longer, project was given up with regard to the CHP-Plant investor
| 322 | Kromolice (PL) |  | A new AC substation between existing substations Plewiska and Ostrów and Pątnów in Poznań Agglomeration Area with transformation 400/110kV 400 MVA. New substation Kromolice is connected by splitting and extending existing line Ostrów-Plewiska and Pątnów - Plewiska. | [10 empty] | under construction | 2012 | The investment process ongoing according to plan. Faster commissioning date reported after update of NDP. The project will be commissioned by the end on 2012,
| 331 | Gorzów (PL) | Leśniow (PL) | Upgrading of sag limitations (new capacity 461 MVA). | [10 empty] | planned | 2015 | The investment process ongoing according to plan
| 336 | Warszawa Praga (PL) |  | A new AC substation with 2x275 MVA 220/110kV transformation between existing substations Miłosna and Mory in Warszawa Agglomeration Area, New substation Warszawa Praga is connected by splitting and extending existing line Miłosna-Mory. | [10 empty] | planned | >2015 | The project is in the plans for generation connection purpose. Planned comissioning is dependent upon generation investment (the investor has withdrawn a new gen. unit from the plans). There is an existing combined heat power plant in this area; possible new generation in the future.
| 344 | Lublin Systemowa (PL) | Abramowice (PL) | New 220kV cable/OHL interconnection line Lublin Systemowa - Abramowice, in Lublin agglomeration area (522 MVA, 18km). | [10 empty] | design & permitting | >2020 | Investment postponed due to change in generation sector plans.
| 346 | Halemba (PL) |  | Halemba substation is connected by splitting and extending of existing 220kV lines Kopanina - Katowice. | [10 empty] | cancelled | cancelled | Project withdrawn from TSO plans because of cancellation of construction of new generation unit.
| 348 | several substations in PSE O control area |  | Installation additional and exchange existing transformers (400/110kV and 220/110kV), capacitors and SVC in substations, upgrading of substations. | [10 empty] | design & permitting | 2015 | The investment process ongoing according to plan.
| 349 | Puławy (PL) |  | A new AC 400kV switchgear in existing substation Pulawy (with transformation 400/220kV 500 MVA) will be connected by splitting and extending existing 400kV lines: Kozienice- Lublin Systemowa and Kozienice - Ostrowiec. | [10 empty] | planned | 2020 | The investment process ongoing according to plan. This investment is connected to the construction of a new power plant.
| 350 | Chełm (PL) | Lublin Systemowa (PL) | Construction of a new 400 kV OHL Lublin Systemowa-Chełm with single circuit (1870 MVA). A new AC 400kV switchgear in existing substation Chelm with transformation 400/220kV 500 MVA. | [10 empty] | planned | 2020 | Upon withdrawal of new conventional power plant from the plans the content of the project in the area has changed. Initially the project was foreseen to accommodate a conventional generator.
| 351 | Blachownia (PL) |  | A new AC 400kV switchgear in existing substation Blachownia (with transformation 400/220kV 500 MVA and 400/110kV 400 MVA) will be connected by splitting and extending existing 400kV line Joachimów - Wielopole and 220kV line Kedzierzyn - Groszowice. | [10 empty] | planned | 2020 | The project is in the plans for generation connection purpose. Planned comissioning is dependent upon generation investment (the investor has withdrawn a new gen. unit from the plans). There is an existing heat power plant in this area; possible new generation in the future.
| 354 | Byczyna (PL) | Podborze (PL) | Double line 400kV Byczyna-Czeczott-Podborze (2x1870 MVA, 155km) will be built in parallel with 220kV line Byczyna-Bieruń-Poręba-Podborze in the same road + New substation 400 and 220kV Podborze (with transformation 400/220kV 500 MVA) will be connected by splitting and extending existing lines Wielopole-Nosovice, Kopanina-Liskovec, Bujaków-Liskovec, Komorowice-Bieruń, Moszczenica-Poręba and new double circuit line 400kV Podborze-Czeczott. | [10 empty] | design & permitting | after 2020 | The delay in the plans appeared after updating of the NDP. The time schedule of the project was shifted to meet the schedule of the generation connection.
| 356 | Janów (PL) |  | New substation 400kV Janów (with transformation 400/110kV 400 MVA) will be connected by splitting and extending existing line Rogowiec-Płock. | [10 empty] | planned | 2020 | The investment process is according to the plan.
| 357 | Joachimów (PL) |  | Replacement of a transformer 400/220kV (500 MVA). | [10 empty] | planned | 2020 | The investment process ongoing according to plan
| 359 | Morzyczyn (PL) | Pomorzany/ Glinki (PL) | New line 220kV (522 MVA). | [10 empty] | planned | >2020 | Future realization of the investment dependent upon needs of increase of security of supply in the Szczecin agglomeration area.
| 360 | Miłosna (PL) | Siekierki (PL) | New cable connection 220kV Miłosna - Warszawa Siekierki (333 MVA, 10km). | [10 empty] | planned | >2020 | Future realization of the investment dependent upon needs of increase of security of supply in the Warcowa agglomeration area.
| 361 | Ołtarzew (PL) | Mory (PL) | Replacement of conductors (high temperature conductors). (new capacity 461 MVA). | [10 empty] | planned | 2020 | The investment process ongoing according to plan. The upgrade method not decided yet.
| 362 | Wielopole (PL) | Moszczenica (PL) | Replacement of conductors (high temperature conductors). (new capacity 461 MVA). | [10 empty] | planned | 2020 | The investment process ongoing according to plan. The upgrade method not decided yet.
| 363 | Byczyna (PL) | Siersza (PL) | Replacement of conductors (high temperature conductors). (new capacity 461 MVA). | [10 empty] | planned | 2020 | The investment process ongoing according to plan. The upgrade method not decided yet.
| 367 | several substations in PSE O control area |  | Installation of an additional transformer + replacement of an existing one (400/110kV and 220/110kV) and shunt reactors in substations, upgrading and decommissioning of substations. | [10 empty] | planned | 2020 | The investment process ongoing according to plan.
| 397 | Varangerbotn (NO) | Pirttikoski or Petäjäskoski (FI) | New single circuit 380 - 400kV OHL (500km). | [10 empty] | under consideration | 2020/2025 | Based on a common Statnett/Fingrid study conclusion from the more detailed study on the project that is can be postponed beyond 2021. The need is related to the oil/refinery and wind development on the Northern Norway
| 407 | Tonstad (NO) | Arendal (NO) | Voltage upgrading of existing single circuit 400kV OHL Tonstad-Solhom-Arendal. | [10 empty] | 0 | 0 | This investment proposed as stand-alone in the TYNDP 2010 is now merged into investment 37.406. Its evolution is monitored there. | This investment proposed as stand-alone in the TYNDP 2010 is now merged into investment 37.406. Its evolution is monitored there.
| 409 | Feda, Tonstad (NO) |  | Reactive power devices in 400kV substations. | [10 empty] | 0 | 0 | This investment proposed as stand-alone in the TYNDP 2010 is now merged into investment 37.406. Its evolution is monitored there. | This investment proposed as stand-alone in the TYNDP 2010 is now merged into investment 37.406. Its evolution is monitored there.
| 413a | Sima (NO) | Samnanger (NO) | New 420kV line Sima-Samnanger to ensure security of supply in the region of Hordaland/ Bergen, and to integrate new hydro power. | [10 empty] | under construction | 2013/2014 | Project going according to the plan
| 419 | Namsos (NO) | Storheia (NO) | New 119km 800MVA single circuit Namsos-Roan-Storheia OHL to connect new wind power generation at Fosen. | [10 empty] | under construction | 2015 | This projects is now embedded in the investment 104.415.
| 319 | Skawina (PL) |  | A new AC 400/110kV substation next to existing 220/110kV substation in Cracow Agglomeration Area with transformation 400/110kV 2x400 MVA. New substation Skawina is connected by splitting and extending of existing 400kV lines Tarnów - Tucznawa and Rzeszów - Tucznawa. Dismantling of existing 220/110kV transformers. | [10 empty] | design & permitting | 2015 | The investment process ongoing according to plan
| 321 | Kromolice (PL) | Pątnów (PL) | New 79km 400kV 1870 MVA OHL interconnection line Kromolice - Pątnów - with one circuit from Plewiska to Koninn temporarily on 220kV after dismantling of 220kV line Plewiska - Konin. | [10 empty] | under construction | end 2012 | The investment process ongoing according to plan. Faster commissioning date reported after update of NDP. This project is due to be put in operation by the end 2012.
| 323 | Warszawa Siekierki (PL) | Piaseczno (PL) | A new AC 220/110kV substation (with transformation 220/110kV 2x275MVA) in Warsaw Agglomeration Area connected by a new 20km 220kV 333 MVA cable/OHL line Warszawa Siekierki - Piaseczno. | [10 empty] | design & permitting | 2020 | Investment postponed due to change in new generation unit connection schedule which was scheduled for 2015 but it was withdrawn from the medium term.
| 325 | Krajnik (PL) | Pomorzany (PL) | A new AC substation in Szczecin Agglomeration Area. New substation Pomorzany is connected by new 24km 220kV 522 MVA line Krajnik - Pomorzany and 220/110kV (275 MVA) transformer to existing 110kV switchgear. | [10 empty] | planned | 2016 | The delay in the plans appeared after updating of the NDP. The time schedule of the project was shifted to meet the schedule of the generation connection (combined cycle power plant in Pomorzany).
| 332 | Recław (PL) | Glinki (PL) | A new AC substation in Szczecin Agglomeration Area. New substation Recław is connected by new 52km 220kV 522 MVA line Recław - Glinki, existing 110kV single circuit line Morzyczyn - Recław upgraded to 220kV and two 220/110kV (275 MVA) transformer to existing 110kV switchgear. Splitting of existing 220kV line Morzyczyn - Police and expanding to Glinki substation. | [10 empty] | design & permitting | 2016 | The delay in the plans appeared after updating of the NDP. The time schedule of the project was shifted due to proper coordination with other investments in the area (325).
| 333 | Pasikurowice (PL) | Świebodzice (PL) | A new AC substation in Wrocław Agglomeration Area. New substation Wrocław is connected to new 135km (sum) 400kV 1870 MVA lines: Pasikurowice-Wrocław and Świebodzice - Wrocław. New 400kV Wrocław substation with 2x400 MVA, 400/110kV transformation. New 400kV Świebodzice substation with 1x500MVA, 400/220kV transformation and 1x400 MVA, 400/110kV transformation. New 400kV OHL interconnection line Wrocław - Świebodzice after dismantling of 220kV line Świebodzice - Biskupice and new 400kV OHL interconnection line Pasikurowice - Wrocław, including new Wrocław substation. | [10 empty] | under construction | 2015 | The investment process ongoing according to plan. The line Pasikurowice-Wrocławd and the substation Wrocław are already commissioned.
| 337 | Radkowice (PL) | Kielce Piaski (PL) | New 26km 220kV 522 MVA OHL line Radkowice -Kielce Piaski, in Kielce agglomeration area. | [10 empty] | design & permitting | 2015 | The investment process ongoing according to plan
| 340 | Lubocza (PL) |  | An existing substation in Kraków Agglomeration Area. Existing substation will be upgraded by splitting and extending existing 220kV line Siersza- Klikowa and installing second ATR 220/110kV (160 MVA). | [10 empty] | commissioned | commissioned | In the previous NDPs of PL the proejcts were structure in steps of 5 years. Therefore the date of commissioning mentioned din Tend 2010 is 2015. The project will be commissioned by the end of 2012.
| 341 | Pątnów (PL) | Włocławek (PL) | Upgrading of sag limitations OHL 220kV (389 MVA). | [10 empty] | cancelled | cancelled | Investment suspended. After connection of planned generation unit in substation Włocławek Azoty the possibility of overload in the existing lines is eliminated.
| 342 | Czarna (PL) | Polkowice (PL) | New 400kV OHL interconnection line Czarna -Polkowice (1870 MVA, 22km), including new Polkowice 400kV substation with 500 MVA, 400/220kV transformation. | [10 empty] | design & permitting | 2016 | The investment process ongoing according to plan. The delay in the commissioning of the project appeared after updating of the NDP.
| 343 | Byczyna (PL) |  | Upgrading of existing AC 220kV substation Byczyna. A new 400kV AC substation in Silesia Agglomeration Area with transformation 400/220kV 2x 500 MVA. New substation Byczyna is connected by splitting and extending existing line Tarnów - Tucznawa. | [10 empty] | planned | 2015 | The investment process ongoing according to plan
| 358 | Ostrów (PL) | Kromolice (PL) | Installation of a 2nd 400kV circuit along an already existing line on the same voltage. (1870 MVA, 212km). | [10 empty] | design & permitting | 2020 | The investment process ongoing according to plan
| 364 | Czarna (PL) | Polkowice (PL) | New line will be second 400kV circuit to existing line in the same direction. (1870 MVA, 22km). | [10 empty] | planned | 2020 | The investment process ongoing according to plan. The first out of 2 circuits will be operational starting with 2015.
| 365 | Wyszków (PL) |  | New substation 400kV Wyszków (with transformation 400/110kV 400 MVA) will be connected by splitting and extending line Ostrołęka-Stanisławów. | [10 empty] | design & permitting | 2025 | The investment delayed because of spacial planning problems.
| 431 | Tjele (DK) | Trige (DK) | New 46km single circuit 400kV line via cable with capacity of approx. 1200 MW. | [10 empty] | Planned | long term | Investment moved to longer time horizon
| 203 | Area Wolmirstedt(DE) | under consideration | Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | under consideration | 2020 | Included in new investment H3 due to new wind BS generation
| 429 | Ferslev (DK) | Vester Hassing (DK) | New 20km single circuit 400kV line via a cable with a capacity of approx. 800 MW. | [10 empty] | planned | 2018 | No change
| 180 | Mengede (DE) | Kruckel (DE) | Installation of a second circuit 380kV OHL and extension of existing substations. Line length:16km. | [10 empty] | design & permitting | mid term | project develops according to the plan
| 398 | Under consideration (SE) |  | New series and shunt compensation of OHL. | [10 empty] | cancelled | cancelled |  | This investment is splitted in 2 parts (investment 104.398B and 93.398A)
| 381 | Visaginas (LT) | Liksna (LV) | Upgrade single circuit OHL (943 MVA, 50km). | [10 empty] | under consideration | 2020 | Progresses as planned
| 143 | Kassö (DK) & Ensted (DK) |  | Installation of two PSTs. This step includes also planed strengthening of existing 380kV lines in the grid of TenneT.eu and Energinet.dk . | [10 empty] | commissioned | commissioned | commissioned
| 169 | Großgartach (DE) |  | Upgrade the substation for a higher short circuit capacity. New installation includes 10 gas insulated bays, 63 kA, 3 bus-bar and 2 transformers. | [10 empty] | commissioned | commissioned | Commissioned
| 201 | Bärwalde (DE) | Schmölln (DE) | New internal double circuit 380kV-line connecting the substations St. Peter and Salzach new (replacement of the existing 220kV-line). Length: 46km. | [10 empty] | design & permitting | 2014 | Delays due to authorization process.
| 196 | wind farm Baltic 1 (DE) | Bentwisch (DE) | Connection of the offshore wind farm Baltic 1 (AC-cables on transmission voltage level). | [10 empty] | commissioned | commissioned | Commissioned
| 210 | Substations in 5 Hertz Transmission control area |  | Construction of new 380/110kV substations. | [10 empty] | commissioned | commissioned | Freiberg and Stendal/West are commissioned. The remaining substations were transferred to the 44. 209 investment.
| 382a | Bitenai (LT) |  | New 330kV switching station. | [10 empty] | commissioned | commissioned | Commissioned
| 37. 408 | Kristiansand, Feda (NO) |  | Reactive compensation due to HVDC links NorNed and Skagerak 4. Reactive power devices in 400kV substations. | [10 empty] | design & permitting | 2012/2014 | Feda is in the planning and permitting stage. Kristiansand is under construction(commissioned expected as planned 2012)
| 410 | Kristiansand (NO) |  | Spare transformer for the HVDC Skagerak interconnection transformer. | [10 empty] | under construction | 2012 | Will be commissioned 2012.
| 434 | Fraugde (DK) | Herslev(DK) | New single circuit HVDC-LCC installation including a 56km 450kV DC subsea cable with 600MW capacity. | [10 empty] | commissioned | commissioned | Commissioned Sept. 2010.
| 395 | Rauma (FI) | Finnböle (SE) | A new 500kV HVDC connection will be built in parallel with the existing one between Finland and Sweden. On the Swedish side, a 70km direct current overhead line will be built to a new substation Finnböle where the converter station will be placed. Total length of line: 300km and capacity: 800MW. | [10 empty] | commissioned | commissioned | In TYNDP 2010 project was in construction phase. Project progressed as planned and is now completed.
| 339 | Morzyczyn (PL) |  | A new AC substation in Szczecin Agglomeration Area with transformation 400/220kV 330 MVA and 400/110kV 330 MVA. New substation Morzyczyn is connected by splitting and extending existing 400kV line Krajnik - Dunowo. | [10 empty] | commissioned | commissioned | Commissioned -In the previous NDPs of PL the proejcts were structure in steps of 5 years. Therefore the date of commissioning mentioned din Tend 2010 is 2015. The project was commissioned in 2011.
| 345 | Łagisza (PL) |  | A new AC 400kV switchgear in existing substation Łagisza (with transformation 400/220kV 500 MVA and 400/110kV 330 MVA) is connected by splitting and extending of existing 400kV lines Rokitnica - Tucznawa. | [10 empty] | commissioned | commissioned | Commissioned -In the previous NDPs of PL the proejcts were structure in steps of 5 years. Therefore the date of commissioning mentioned din Tend 2010 is 2015.The project was commissioned in 2011.
| 347 | Gdańsk I (PL) |  | A new AC 400kV switchgear in existing substation Gdańsk I is connected by splitting and extending of existing 400kV lines Żarnowiec - Gdańsk Błonia. | [10 empty] | commissioned | commissioned | Commissioned -In the previous NDPs of PL the proejcts were structure in steps of 5 years. Therefore the date of commissioning mentioned din Tend 2010 is 2015.The project was commissioned in 2011.
| A61 | Samnanger (NO) | Sauda (NO) | Voltage upgrade of existing 300kV line. | [10 empty] | under consideration | 2021 | New project
| A73 | Żarnowiec (PL) |  | Extension and upgrade of an existing 110 kV switch gear and installation of 400/110 kV transformer dedicated to wind farms planned to be connected to Żarnowiec substation. Upgrade of existing 400 kV switchgear for transformer installation. | [10 empty] | planned | 2020 | The Żarnowiec substation is one of several substations in northern Poland incorporated in the project Wind Integration. The upgraded substation will serve as connection point for RES generation.

## CCE report
5 July 2012
TYDNP 2012 package - Table of projects Continental Central East Regional Group Investment Plan
Project identification |  |  |  |  | Project assessment
Project number | Investment number | Substation 1 | Substation 2 | Brief technical description | Grid Transfer Capability Increase [MW] | Socio-economic Welfare | RES integration | Improved Security of Supply | Losses variation | CO2 mitigation | Technical resilience | Flexibility | Social and environmental Impact | Project costs | Present status | Expected date of commissioning | Evolution compared to the TYNDP 2010 situation | Investment comment | Project comment
26 | 26. 63 | Lienz (AT) | Veneto region (IT) | The project foresees the reconstruction of the existing 220kV-interconnection line as 380kV-line on an optimized route to minimize the environmental impact. Total length should be in the range of 100-150km. | 750 | 3 | 2 | [6 empty] | 3 | planned | long term | Progresses as planned |  | Reinforcement of the interconnection between Italy and Austria. Also the support the interaction between the RES in mainly Italy with the pump storage in the Austrian Alps.
26 | 26. 47. 220 | Lienz (AT) |  | Erection of a new 220/220kV- PST in the substation Lienz (AT). | [10 empty] | under construction | 2012 | Project is in errecion and expected to be commissioned 2012 according to the schedule | The investment contributes also to project 47. | 26
26 | 26. 47. 216 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 26
26 | 26. 64 | Bressanone (IT) | New substation near Innsbruck (AT) | New double circuit 400kV interconnection through the pilot tunnel of the planned Brenner Base Tunnel. Total line length: 65km. | [10 empty] | under consideration | >2022 | Progresses as planned |  | 26
26 | 26. 66 | Prati di Vizze (IT) | Steinach (AT) | Upgrade of the existing 44km Prati di Vizze (IT) – Steinach (AT) single circuit 110/132kV OHL, currently operated at medium voltage and installing a 110kV/132kV PST. | [10 empty] | design & permitting | mid term | Investment delayed with 2 years due to the permitting process |  | 26
26 | 26. 83 | Volpago (IT) | North Venezia (IT) | Realization of a new 380kV line between the existing substation of North Venezia and the future 380kV substation of Volpago, connected in and out to the 380kV "Sandrigo - Cordignano” . Total line length: 31km. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 26
26 | 26. 93 | Dolo (IT) | Camin (IT) | New 15km double circuit 400kV OHL between existing Dolo and Camin 400kV substations, to be built in parallel with the existing line. | [10 empty] | under construction | 2014 | Authorization process ended, construction phase on going |  | 26
26 | 26. 97 | Polpet (IT) |  | Voltage upgrade of the existing Polpet 150kV/medium voltage substation up to 220kV, complying with 400kV standards. The substation will be connected by two shorts links to the existing Soverzene-Lienz 220kV line. | [10 empty] | design & permitting | 2015 | Authorization process started, project phase on going |  | 26
26 | 26. 47. 218 | Obersielach (AT) | Lienz (AT) | New 190km 380kV OHL connecting the substations Lienz (AT) and Obersielach (AT) to close the Austrian 380kV-Ring in the southern grid area. Line length: 190km. | [10 empty] | under consideration | long term | Progresses as planned | The investment contributes also to project 47. | 26
26 | 26. A102 | New interconnection between Italy and Austria |  | New possible interconnection line between Italy and Austria | [10 empty] | under consideration | long term | This investment replaces investment n°65 mentioned on TYNDP 2010. The previous investment evolved so much that it is substituted by a new project. Feasibility studies ongoing including internal reinforcements. |  | 26
27 | 27. 68 | Okroglo (SI) | Udine (IT) | New 120km double circuit 400kV OHL with installation of a PST in Okroglo. The thermal rating will be 1870 MVA per circuit. | >1800 | 1 | 3 | [6 empty] | 2 | planned | long term | Progresses as planned |  | This project increases the capacity between Slovenia - Italy and Slovenia - Hungary. Project will remove congestion and strengthen connection on North-South and East-West axis.
27 | 27. 92 | West Udine (IT) | Redipuglia (IT) | New 40km double circuit 400kV OHL between the existing substations of West Udine and Redipuglia, providing in and out connection to the future 400kV substation of South Udine. | [10 empty] | design & permitting | 2015 | The investment is delayed due to longer than expected authorization procedures. |  | 27
27 | 27. A96 | New interconnection between Italy and Slovenia |  | New interconnection between Italy and Slovenia | [10 empty] | under consideration | long term | Feasibility studies ongoing including the internal reinforcements. | Need for strengthening the connection between Slovenia and Italy and increasing of power exchange capability | 27
27 | 27. 223 | Cirkovce (SI) | Heviz (HU) Zerjavenec (HR) | The existing substation of Cirkovce (SI) will be connected to one circuit of the existing Heviz (HU) -Zerjavinec (HR) double circuit 400kV OHL by erecting a new 80km double circuit 400kV OHL in Slovenia. The project will result in two new cross-border circuits: Heviz (HU) - Cirkovce (SI) and Cirkovce (SI) - Žerjavenec (HR). | [10 empty] | design & permitting | 2016 | Presently in the authorization process. This investment was delayed due to permitting process. |  | 27
27 | 27. 224 | Krsko (SI) | Bericevo (SI) | New 400kV double circuit OHL. This project will strengthen connection between East and Central part of Slovenia and connect an internal loop. Line length: 80km. | [10 empty] | under construction | 2015 | Authorization process ended, construction phase is on going. This investment was delayed due to permitting process. |  | 27
27 | 27. 225 | Divaca (SI) | Cirkovce (SI) | Upgrading 220kV lines to 400kV in corridor Divaca-Klece-Bericevo-Podlog-Cirkovce. Line length: 193km. | [10 empty] | planned | long term | Progresses as planned |  | 27
27 | 27. A105 | Lika(HR) | Brinje(HR) | New 55km single circuit 400 kV OHL replacing aging 220 kV overhead line | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. A106 | Lika(HR) | Velebit(HR) | New 60km single circuit 400 kV OHL replacing aging 220 kV overhead line | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. A107 | Lika (HR) |  | New 400/110 kV substation, 2x300 MVA | [10 empty] | planned | 2017 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. A108 | Brinje (HR) |  | New 400/220 kV substation, 1x400 MVA | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 27
27 | 27. 229 | Plomin (HR) | Melina(HR) | New 90 km double circuit OHL, with two connecting substations and transformer 400/220 kV, 400 MVA | [10 empty] | design & permitting | >2016 | Project moved to long term, due to postponed commissioning date of thermal power plant Plomin |  | 27
27 | 27. 227 | Banja Luka (BA) | Lika (HR) | New 400kV interconnection line between BA and HR | [10 empty] | under consideration | 2020 | End points of OHL and commissioning date defined after bilateral HR-BA agreement |  | 27
28 | 28. 70 | Villanova (IT) | Lastva (ME) | New 1000MW HVDC interconnection line between Italy and Montenegro via 375km 500kV DC subsea cable and converter stations at both ending points. | 1000 | 1 | 2 | [6 empty] | 3 | under construction | 2015 | Authorization process ended, construction phase on going. The substations on the ME side has been changed. |  | It contributes significantly to the increase of GTC between the West Balkans and IT such contributing to market integration; complements the ME - IT cable
28 | 28. 86 | Foggia (IT) | Villanova (IT) | New 178km double circuit 400kV OHL between existing Foggia and Villanova 400kV substations, also connected in and out to the Larino and Gissi substations. A PST will be installed on the new 400kV line. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 28
28 | 28. 89 | Fano (IT) | Teramo (IT) | New 200km single circuit 400kV OHL between the existing 400kV substations of Fano and Teramo, providing the connection in and out to the future substation to be built in Macerata area. | [10 empty] | design & permitting | long term | The investment is delayed due to longer than expected authorization procedures. |  | 28
28 | 28. 232 | Visegrad (BA) | Pljevlja (ME) | New 70km single circuit 400kV OHL between Visegrad and Pljevlja | [10 empty] | planned | 2015 | Feasibility study for 400kV interconnections RS-ME-BA proposed under Infrastructure Projects Facility for Western Balkans |  | 28
28 | 28. 233a | Lastva (ME) |  | A new substation will be connected to the existing line 400kV Podgorica 2(ME)-Trebinje(BA), with two transformers 2X300MVA 400/110kV, and convertor station for the DC cable Lastva(Tivat)-Villanova (see 70). | [10 empty] | design & permitting | 2015 | Feasibility study covering the aspects of route planning, substation location, environmental and social issues and equipment selection is due to end in second half of 2011 |  | 28
28 | 28. 233b | Lastva (ME) | Pljevlja (ME) | New 160 km double circuit 400kV OHL existing substation Pljevlja and new substation Tivat. | [10 empty] | design & permitting | 2016 | Feasibility study covering the aspects of route planning, substation location, environmental and social issues and equipment selection is due to end in second half of 2011 |  | 28
28 | 28. A109 | Bajina Basta (RS) | Visegrad (BA) | New 400kV interconnection OHL between Serbia and BiH, and reconstruction of existing two OHL 220 kV between BiH and Serbia. | [10 empty] | planned | >2016 | New investment in TYNDP | New 400 kV overhead line between Serbia and BIH. It will eliminate constraints in the region for electric energy transits and exchange. | 28
28 | 28. A110 | Bajina Basta (RS) | TPP Obrenovac (RS) | New double circuit 400 kV OHL between new substation Bajina Basta (see infra), and substation Obrenovac | [10 empty] | design & permitting | >2016 | New investment in TYNDP | Obrenovac is the "strongest" 400 kV node in Serbia, thus providing significant upgrade for evacuation and energy transfer from north to south, and further down in Montenegro, through the new line between Bajina Basta and Pljevlja (ME) | 28
28 | 28. A111 | Bajina Basta (RS) | Pljevlja (ME) | New 86 km single circuit 400kV OHL connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS). | [10 empty] | planned | >2016 | New investment in TYNDP |  | 28
28 | 28. A112 | Bajina Basta (RS) |  | New 400/110 kV substation in Bajina Basta, upgrading an existing 220/110 kV substation. | [10 empty] | planned | >2016 | New investment in TYNDP |  | 28
28 | 28. A113 | Bistrica (RS) |  | New 220/110 kV substation | [10 empty] | design & permitting | 2015 | New investment in TYNDP | After a topology change in the area, the investment will eliminate firm connection in "Vardiste" (secure and stable operation in Serbian network and systems of Bosnia and Herzegovina and Montenegro), to eliminate constraints in the region for electric energy transits and exchange. | 28
28 | 28. A114 | Konjsko(HR) | Velebit(HR) | New 100km single circuit 400 kV OHL replacing ageing 220 kV overhead line | [10 empty] | planned | 2020 | Strengthening of the 400 kV corridor across the Adriatic coast in Croatia in LT period and removal of regional congestion at north-south axis , also to accommodate power transfers from Croatia and Bosnia&Herzegovina to Italy through new IT-ME DC link (Investment 70). |  | 28
28 | 28. 231 | Konjsko(HR) |  | Installation of a 150MVAr reactive power device | [10 empty] | design & permitting | 2014 | Investment postponed 1 year due to permitting process |  | 28
28 | 28. A115 | Plat (HR) |  | New 220/110 kV substation | [10 empty] | under construction | 2013 | New investment in TYNDP, contributing to mesh the network surrounding HVDC link IT-ME and to increase the reliability of the EHV system |  | 28
28 | 28. 228 | Trebinhe(BA) | Plat(HR) | Re-establishment of two previously existing 220kV single circuit interconnection Trebinje(BA)-Plat(HR); Total length 10km. | [10 empty] | planned | 2014 | Progresses as planned |  | 28
35 | 35. 137 | Vitkov (CZ) | Mechlenreuth (DE) | New 400kV single circuit tie-line between new (CZ) substation and existing (DE) substation. Length: 70km. | 500 | 5 | 4 | [6 empty] | 3 | under consideration | long term | Progresses as planned |  | This project is required to enable power flows between West and East, enhance the transfer capability between CZ and DE and supports the future generation evacuation.
35 | 35. 138 | tbd (CZ) | tbd (DE) - South-Eastern part of 5 Hertz Transmission control area (Röhrsdorf) | Possible increase of interconnection capacity between CEPS and 50Hertz Transmission is under consideration: either a new 400kV tie-line (OHL on new route) or a reinforcement of the existing 400kV tie-line Hradec (CEPS) – Röhrsdorf (50Hertz Transmission). | [10 empty] | under consideration | long term | Progresses as planned |  | 35
35 | 35. 306 | Vitkov (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA. | [10 empty] | planned | 2017/2018 | It is closely dependent on construction of line investment n°308 |  | 35
35 | 35. 307 | Vernerov (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA. | [10 empty] | planned | 2013/2016 | Commissioning date has been divided into two phases (1. phase - temporary connection of wind plant 180MW, 2. phase finalization of substation construction including connection to the distribution grid (consumption) |  | 35
35 | 35. 308 | Vernerov (CZ) | Vitkov (CZ) | New 400kV double circuit OHL, 1385 MVA. | [10 empty] | planned | long term | Permitting procedure complications are foreseen (line crosses protected area) |  | 35
35 | 35. 309 | Vitkov (CZ) | Prestice (CZ) | New 400kV double circuit OHL, 1385 MVA. | [10 empty] | under consideration | long term | Permitting procedure complications are foreseen (line crosses protected area) |  | 35
35 | 35. 311 | Kocin (CZ) |  | Upgrade of the existing substation 400/110kV; upgrade transformers 2x350MVA. | [10 empty] | design & permitting | long term | Schedule harmonization with market participants |  | 35
35 | 35. 312 | Mirovka (CZ) |  | Upgrade of the existing substation 400/110kV with two transformers 2x250MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 313 | Kocin (CZ) | Mirovka (CZ) | Connection of 2 existing 400kV substations with double circuit OHL having 120.5km length: and a capacity of 2X1385 MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 314 | Mirovka (CZ) | V413 (CZ) | New double circuit OHL with a capacity of 2x1385 MVA and 26.5km length. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 315 | Kocin (CZ) | Prestice (CZ) | Adding second circuit to existing single circuit line OHL upgrade in length of 115.8km. Target capacity 2x1385 MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 316 | Mirovka (CZ) | Cebin (CZ) | Adding second circuit to existing single circuit line (88.5km, 2x1385 MVA). | [10 empty] | under consideration | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 317 | Hradec (CZ) | Reporyje (CZ) | Upgrade of existing 400kV single circuit OHL with length of 116.9km. Target capacity 1385 MVA. | [10 empty] | commissioned | commissioned | Commissioned |  | 35
36 | 36. 141 | Ishøj/Bjæverskov (DK) | Bentwisch/Güstrow (DE) | The Kriegers Flak Combined Grid Solution is the new offshore multiterminal connection between Denmark and Germany used for both grid connection of offshore wind farms Kriegers Flak and interconnection. Technical features still have to be determined. | 600 | 5 | 3 | [6 empty] | 1 | planned | long term | Permission for Danish Wind Farm KF 3 is in pending. Connection to Sweden is withdrawn at present, but can come on a later stage. |  | The Kriegers Flak Combined Grid Solution is the new offshore multiterminal connection between Denmark and Germany used for both grid connection of offshore wind farms Kriegers Flak and interconnection.
37 | 37. 142 | Tonstad (NO) | Wilster (DE) | Nord.Link/NorGer: a new HVDC connection between Southern Norway and Northern Germany. Estimated subsea cable length: 520 - 600km. Capacity: 1000 MW. | up to 1400 | 1 | 4 | [6 empty] | 3 | design & permitting | 2018/2021 | Revised capacity and progress postponed, due to more demanding system operations and time needed to obtain necessary government permits for reinforcing the national grid. |  | The purpose is: Market integration with the continent and facilitating RES integration in southern and western Norway. Will also improve security of supply in southern Norway.
| 37. 408 | Kristiansand, Feda (NO) |  | Reactive compensation due to HVDC links NorNed and Skagerak 4. Reactive power devices in 400kV substations. | [10 empty] | design & permitting | 2012/2014 | Feda is in the planning and permitting stage. Kristiansand is under construction(commissioned expected as planned 2012)
37 | 37. 406 | (Southern part of Norway) (NO) |  | Voltage uprating of existing 300 kV line Sauda/Saurdal - Lyse - Tonstad - Feda - 1&2, Feda - Kristiansand; Sauda-Samnanger in long term. Voltage upgrading of existing single circuit 400kV OHL Tonstad-Solhom-Arendal. Reactive power devices in 400kV substations. | [10 empty] | design & permitting | 2016 (2013-2018) | Revised progress. Due to more demanding system operations and time needed to obtain necessary government permits for reinforcing the national grid. The investment now embed former TYNDP 2010's investments 407 and 409 and the technical description has been updated accordingly. |  | 37
39 | 39. 428 | Kassø (DK) | Tjele (DK) | Rebuilding of a 400kV OHL of 173km from a single-circuit to a double-circuit . This increases the transfer capacity with approx. 1000 MW. | 1000-1550 | 1 | 2 | [6 empty] | 2 | design & permitting | 2012/2014 | Progresses as planned |  | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity.
39 | 39. 144 | Audorf (DE) | Kassö (DK) | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity. It consists of partially an upgrade of existing 400kV line and partially a new 400kV route in Denmark. In Germany new 400kV line mainly in the trace of a existing 220kV line. The total length of this OHL is 114km. | [10 empty] | under consideration | 2017 | Progresses as planned |  | 39
40 | 40. 446 | Bascharage (LU) | Aubange (BE) | As a first step(2016) a PST could be placed in the existing 225kV line between LU and BE. In a second stage, two solutions are currently investigated (4 TSOs - Elia, Amprion, CREOS, RTE are involved). Solutions 1 would be a new interconnection between Creos grid in LU and ELIA grid in BE via a 16km double circuit 225kV underground cable with a capacity of 1000 MVA. Solution 2 would be the interconnection between CREOS grid in LU and ELIA grid in BE via a new 380 kV double circuit. The current study will investigate the impact of this new interconnection on other boundaries (impact of loop flow) and on internal grids . The potential reinforcements of the other boundaries and the internal grids will also be taken into account in the evaluation. | 380-900 | 2 | 5 | Luxemburg area | [5 empty] | 2 | under consideration | 2016/2020 | The commissioning date and status changed as the study to determine the best investment is still ongoing. |  | Increase the transfer capability between LU,DE, BE and FR.
40 | 40. A29 | Bascharage (LU) | tbd (BE, DE, &/o FR) | New interconnection with neighbor(s) either 220kV or 400kV | [10 empty] | under consideration | 2020 | New investment in TYNDP | An ongoing network study (4 TSOs involved) investigates the robustness of the planned 220kV connection between LU and BE and the potentially need for an upgrading to a 400kV interconnector in the South. | 40
40 | 40. 447 | Heisdorf (LU) | Berchem (LU) | New 20km double-circuit mixed (underground cable+OHL) 225kV project with 1000 MVA capacity including substations for in feed in lower voltage levels. | [10 empty] | design & permitting | 2012/2017 | Progresses as planned |  | 40
40 | 40. A30 | Bascharage (LU) | Niederstedem (DE) or tbd (DE) | Upgrading and new construction of an interconnector to DE, in conjunction with the interconnector in the south of LU; Partial upgrading of existing 220kV lines and partial new construction of lines; With power transformer station in LU | [10 empty] | under consideration | 2020 | New investment in TYNDP |  | 40
41 | 41. 149 | Dollern (DE) | Stade (DE) | New 400kV double circuit OHL Dollern - Stade including new 400kV switchgear in Stade. Length:14km. | >3000 | 4 | 5 | [6 empty] | 1 | design & permitting | mid term | This investment depends on the commissioning of a conventional power plant in the area. The additional reason for delay is the long permitting procedure associated with this investment. |  | Evacuation of the new conventional generation in the 50Hz and TenneT area.
41 | 41. 150 | Conneforde (DE) | Maade (DE) | New 400kV double circuit ( underground cable+OHL) Conneforde - Maade including new 400kV switchgear Maade. Length: 37km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 41
41 | 41. A74 | North of Control Area 5 HzT (DE) |  | Construction of new substations/lines for integration of newly build power plants in northern part of 50HzT control area. | [10 empty] | planned | long term | New investment in TYNDP, because of additional need for generation evacuation. Some of the investments are to be commissioned by the mid term and the some by long term. | Support of conventional generation integration in North-Eastern Germany, maintaining of security of supply and support of market development. | 41
42 | 42. 152 | Dörpen/West (DE) |  | New substation for connection of offshore wind farms. | >8000 | 4 | 1 | [6 empty] | 3 | under construction | mid term | Progresses as planned | Commercially sensitive information about this new wind-farm connection cannot be displayed in the TYNDP report | Integration of the offshore wind parks and the onshore grid reinforcements in the Northern DE.
42 | 42. 159 | Cluster BorWin1 (DE) | Diele (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 205km. Line capacity: 400MW. | [10 empty] | under construction | mid term | The commission date of this wind farms connection should be in 2012. Energy transportation is however already enable | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 160 | Offshore- Wind park Nordergründe (DE) | Inhausen (DE) | New AC-cable connection with a total length of 35km. | [10 empty] | design & permitting | mid term | Progresses depend on development of the off shore wind farm |  | 42
42 | 42. 161 | Offshore- Wind park GEOFreE (DE) | Göhl (DE) | New AC-cable connection with a total length of 32km. | [10 empty] | design & permitting | mid term | Progresses depend on development of the off shore wind farm |  | 42
42 | 42. 163 | Cluster HelWin1 (DE) | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 145km. Line capacity: aprox. 690MW. This Project includes also a new substation Büttel and connection of this new substation with the existing OHL Brünsbüttel - Wilster. | [10 empty] | under construction | mid term | Progresses with delay. | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 164 | Cluster SylWin1 (DE) | Büttel (DE) | New line consisting of underground +subsea cable with a total length of 210km. Line capacity: aprox.864MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 165 | Cluster DolWin1 (DE) | Dörpen/West (DE) | New line consisting of underground +subsea cable with a total length of 155km. Line capacity: 800MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 166 | Offshore Wind park Riffgat (DE) | Emden /Borßum(DE) | New AC-cable connection with a total length of 80km. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 167 | Cluster BorWin2 (DE) | Diele (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 205km. Line capacity: 800MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A82 | Cluster DolWin2 (DE) | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 160 km. Line capacity: 900 MW | [10 empty] | under construction | mid term | New investment in TYNDP, for connection of new off-shore wind-farms | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A83 | Cluster DolWin3 (DE) | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 160 km. Line capacity: 900 MW | [10 empty] | design & permitting | mid term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A84 | Cluster BorWin3 | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 180 km. Line capacity: 900 MW | [10 empty] | design & permitting | mid term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A85 | Cluster HelWin2 | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 145km. Line capacity: 690 MW | [10 empty] | under construction | mid term | New investment in TYNDP, for connection of new off-shore wind-farms | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A86 | Cluster BorWin4 (DE) | Emden/Ost (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 185 km. Line capacity: 900 MW | [10 empty] | under consideration | long term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A87 | Cluster SylWin2 (DE) | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 210km. Line capacity: 800 MW | [10 empty] | under consideration | long term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. 211 | Further connections of more offshore wind farms (DE) |  | Further connections in the clusters BorWin, DolWin, SylWin and HelWin. | [10 empty] | under consideration | long term | Progresses depend on development of the off shore wind farm |  | 42
43 | 43. A81 | Osterath (DE) | Philippsburg (DE) | New HVDC-lines from Osterath to Philippsburg to integrate new wind generation especially from North/ Baltic Sea towards Central-South Germany for consumption and storage. | 10000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany |  | Combined DC and AC new infrastructure to accommodate the new RES generation, the associated flows from North to South and also secure the SOS in South Germany.
| 43. A152 | Emden (DE) | Osterath (DE) | New HVDC-lines from Endem to Osterath to integrate new wind generation especially from North/ Baltic Sea towards Central Germany for consumption and storage. | [10 empty] | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany
| 43. A153 | Wehrendorf (DE) | Urberach (DE) | New lines in HVDC technology from the region of Lower Saxony to North Baden-Württemberg to integrate new wind generation especially from North Sea towards Central-South Europe for consumption and storage. The investment is part of the transmission corridor Cloppenburg - North Baden-Württemberg. | [10 empty] | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany
| 43. A154 | Cloppenburg (DE) | Westerkappeln (DE) | New 400-kV double circuit OHL Cloppenburg-Westerkappel (75 km). The investment is part of the transmission corridor Cloppenburg - North Baden-Württemberg. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
43 | 43. A88 | Brunsbüttel (DE), Wilster (DE), Kaltenkirchen (DE) | Großgartach (DE), Goldshöfe (DE), Grafenrheinfeld (DE) | New DC-lines to integrate new wind generation from Northern Germany towards Southern Germany and Southern Europe for consumption and storage. | [10 empty] | under consideration | long term | New Investment. |  | 43
43 | 43. A75 | Lauchstadt (DE) | Meitingen (DE) | New DC- lines to integrate new wind generation from Baltic Sea towards Central/south Europe for consumption and storage. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits |  | 43
43 | 43. A89 | Area of Northern Lower Saxony (DE) |  | New lines for integration of on- and offshore Wind generation incl. 380-kV-lines Halbemond - Emden, Emden-Conneforde and Conneforde - Cloppenburg. Total length: 160 km | [10 empty] | under consideration | long term | New Investment. |  | 43
43 | 43. A90 | Area of Schleswig-Holstein (DE) |  | About 300 km new 380-kV-lines and around 24 new transformers for integration of onshore Wind in Schleswig-Holstein, incl. lines Brunsbüttel-Barlt-Heide-Husum-Niebüll-border of Denmark, Audorf-Kiel-Göhl-Siems-Lübeck-Kaltenkirchen and Kaltenkirchen-Itzehoe-Brunsbüttel | [10 empty] | under consideration | long term | New investment in TYNDP due to new wind generation projects. | The German West-coast line (Brunsbuettel – Niebuel) is planned to be connected to the Danish grid in the 400 kV substation Endrup. The distance from the German/Danish border is approx. 80 km. Bilateral technical/economical investigations are ongoing. Reinforcements in the Danish 400 kV grid are foreseen in order to facilitate the increased power exchange capacity on the Danish-German border. | 43
44 | 44. 147 | Dollern (DE) | Hamburg/Nord (DE) | New 400kV double circuit OHL Dollern - Hamburg/Nord including one new 400/230kV transformer in substation Hamburg/Nord and new 400kV switchgear Kummerfeld. Length:43km. | 5000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 | design & permitting | mid term | Delays due to authorization process. |  | This project helps accommodating the increasing flows coming mainly form RES in NW DE to SW DE and CH.
44 | 44. 148 | Audorf (DE) | Hamburg/Nord (DE) | New 400kV double circuit OHL Audorf - Hamburg/Nord including two new 400/230kV transformers in substation Audorf. Length: 65km. | [10 empty] | design & permitting | mid term | This investment was schedulted for 2015. Presently it is foreseen a delay of around 1 year due to permitting process. |  | 44
44 | 44. 151 | Wehrendorf (DE) | Ganderkesee (DE) | New line (length: ca. 95km), extension of existing and erection of substations, erection of 380/110kV-transformers. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 156 | Niederrhein (DE) | Dörpen/West (DE) | New 400kV double circuit OHL Dörpen - Niederrhein including extension of existing substations. Length: 167km. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 157 | Wahle (DE) | Mecklar (DE) | New 400kV double circuit OHL Wahle - Mecklar including two new substations. Length: 210km. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 90. 170 | Großgartach (DE) | Hüffenhardt (DE) | New 380kV OHL. Length: 23km. Included with the project : 1 new 380kV substation, 2 transformers. | [10 empty] | under construction | 2012 | Progresses as planned |  | 44
44 | 44. 171 | Hüffenhardt (DE) | Neurott (DE) | Upgrade of the line from 220kV to 380kV. Length: 11km. Included with the project : 1 new 380kV substation. | [10 empty] | planned | 2020 | Progresses as planned |  | 44
44 | 44. 90. 172 | Mühlhausen (DE) | Großgartach (DE) | Upgrading line from 220kV to 380kV. Length:-45km. | [10 empty] | design & permitting | 2014 | Progresses as planned |  | 44
44 | 44. 90. 173 | Hoheneck (DE) | Endersbach (DE) | Upgrading line from 220kV to 380kV. Length:20km. | [10 empty] | design & permitting | 2014 | Progresses as planned |  | 44
44 | 44. 174 | Bruchsal Kändelweg (DE) | Ubstadt (DE) | A new 380kV OHL. Length:6km. | [10 empty] | design & permitting | 2014 | Postponed from one year due to permitting procedures |  | 44
44 | 44.90. 176 | Daxlanden | Eichstetten | Upgrade of transmission capacity of existing 380 kV line (120 km) | [10 empty] | under consideration | 2020 | Progresses as planned |  | 44
44 | 44. 178 | Baden-Württemberg, Süden & Nordosten (DE) |  | Installation of 2x250 MVAr 380kV capacitance banks. | [10 empty] | under construction | 2014 | One more bank in addition. Two have already been installed. Projects realised earlier because the need for reactive power compensation became urgent. |  | 44
44 | 44. 179 | Rommerskirchen (DE) | Weißenthurm (DE) | New line, extension of existing and erection of substations, erection of 380/110kV-transformers. Total line length: 100km. | [10 empty] | under construction/design & permitting | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. 181 | Dauersberg (DE) | Limburg (DE) | New 380kV double circuit OHL, extension of existing of substations, Total line length: 20km. | [10 empty] | under construction/design & permitting | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. 182 | Kriftel (DE) | Obererlenbach (DE) | New 400 kV double circuit OHL Kriftel - Obererlebenbach in existing OHL corridor. Length: 11 km | [10 empty] | planned | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. A80 | Area of West Germany (DE) |  | Installation of several 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | under consideration | long term | New investment in TYNDP, because of additional needs for RES integration (combined with SoS) |  | 44
44 | 44. 183 | Wehrendorf (DE) |  | Installation of 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 184 | Bürstadt (DE) |  | Installation of 2 x 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 185 | Area of Muensterland and Westfalia (DE) |  | New lines and installation of additional circuits, extension of existing and erection of several 380/110kV-substations. Total length: ca. 110km. | [10 empty] | design & permitting | long term | Delays due to authorization process. |  | 44
44 | 44. 186 | Gütersloh (DE) | Bechterdissen (DE) | New lines and installation of additional circuits, extension of existing and erection of 380/110kV-substation. Total line length:27km. | [10 empty] | under construction | mid term | Delays due to authorization process. |  | 44
44 | 44. 187 | Area of West-Rhineland (DE) |  | New lines and installation of additional circuits, extension of existing and erection of several 380/110kV-substations. | [10 empty] | under construction | 2013 | Progresses as planned |  | 44
44 | 44. 188 | Kruckel (DE) | Dauersberg (DE) | New lines, extension of existing and erection of several 380/110kV-substations. Total line length: 130km. | [10 empty] | planned | long term | Progresses as planned |  | 44
44 | 44. A78 | Pkt. Metternich (DE) | Niederstedem (DE) | Construction of new 380kV double-circuit OHLs, decommissioning of existing old 220kV double-circuit OHLs, extension of existing and erection of several 380/110kV-substations. Length: 108km. | [10 empty] | planned | long term | New investment in TYNDP | RES integration/ Market integration especially east-west-direction | 44
44 | 44. A77 | Area of South-Wuerttemberg (DE) |  | Construction of new 380kV double-circuit OHLs, decommissioning of existing double-circuit OHLs, extension of existing 380-kV-substations. Length: ca. 60km. | [10 empty] | planned | long term | New investment in TYNDP | RES integration combined with pump storage in the alp region (market) / increasing of the NTC DE-CH/AT | 44
44 | 44. 190 | Saar-Pfalz-Region (DE) |  | New lines, extension of existing and erection of several 380/110kV-substations. Upgrade of an existing line from 220 to 380 kV | [10 empty] | planned | long term | Delays due to authorization process. | SoS (Neub. Frltg Fraulaut-Saarwellingen) combined with RES integration | 44
| 44. A155 | Conneforde (DE) | Unterweser (DE) | Upgrade of 230-kV-circuit Unterweser-Conneforde to 400kV , Line length: 32 km. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A156 | Dollern (DE) | Elsfleht/West (DE) | New 400 kV line in existing OHL corridor Dollern - Elsfleht/West Length:100 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A157 | Dollern (DE) | Landesbergen (DE) | New 400 kV line in existing OHL corridor Dollern-Sottrum-Wechold-Landesbergen (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A158 | Hamm/Uentrop (DE) | Kruckel (DE) | Extension of existing line to a 400 kV single circuit OHL Hamm/Uentrop - Kruckel. Length: 60 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A159 | Pkt. Blatzheim (DE) | Oberzier (DE) | New 400 kV double circuit OHL Pkt. Blatzheim - Oberzier including extension of existing substations. Length 16 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A160 | Urberach (DE) | Daxlanden (DE) | New line and extension of existing line to 400 kV double circuit OHL Urberach - Pfungstadt - Weinheim - Daxlanden including extension of existing substations. Length: 219 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A161 | Bürstadt (DE) | Daxlanden (DE) | New line and extension of existing line to 400 kV double circuit OHL Bürstadt - Lambshein - Daxlanden including extension of existing substastions. Length: 134 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A162 | Großgartach (DE) | Endersbach (DE) | Extension of existing 400-kV-line Großgartach - Endersbach. (Lenght: 32 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
44 | 44. 175 | Birkenfeld (DE) | Ötisheim (DE) | A new 380kV OHL. Length:11km. | [10 empty] | planned | 2020 | New investment in TYNDP |  | 44
44 | 44. 189 | Niederrhein (DE) | Utfort (DE) | New 400 kV double-circuit OHL Niederrhein-Utfort (24 km). | [10 empty] | under consideration | long term | New investment in TYNDP |  | 44
45 | 45. 90. 177 |  |  |  | 5000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 |  |  | 0 | The investment contributes both to project 45 and project 90. For the technical description see project 90. | This project helps accommodating the increasing flows coming mainly form RES in NE DE to South DE and to the Alps.
45 | 45. 191 | Neuenhagen (DE) | Vierraden (DE) | Project of new 380kV double-circuit OHL Neuenhagen-Vierraden-Bertikow with 125km length as prerequisite for the planned upgrading of the existing 220kV double-circuit interconnection Krajnik (PL) – Vierraden (DE Hertz Transmission). | [10 empty] | design & permitting | 2013/2015 | Project in permitting phase, strong local resistance |  | 45
45 | 45. 193 | Halle/Saale (DE) | Schweinfurt (DE) | New 380kV double-circuit OHL between the substations Vieselbach-Altenfeld-Redwitz with 215km length combined with upgrade between Redwitz and Grafenrheinfeld (see project 153). The Section Lauchstedt-Vieselbach has already been commissioned. Support of RES integration in Germany, annual redispatching cost reduction, maintaining of security of supply and support of the market development. The line crosses the former border between Eastern and Western Germany and is right downstream in the main load flow direction. The project will help to avoid loop flows through neighboring grids. | [10 empty] | design & permitting | mid term | Investment partly completed, strong local public resistance- delay due to permitting process |  | 45
45 | 45. 197 | Neuenhagen (DE) | Wustermark (DE) | Construction of new 380kV double-circuit OHL between the substations Wustermark-Neuenhagen with 75km length. Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | under construction | mid term | Investment partly under construction and partly in permitting phase. Expected date of commissioning was adjusted due to long permitting process and strong local public resistance. |  | 45
45 | 45. 199 | Western Pomerania (DE) | Uckermark North (DE) | Construction of new 380kV double-circuit OHLs in North-Eastern part of 50HzT control area and decommissioning of existing old 220kV double-circuit OHLs, incl. 380-kV-line Bertikow-Pasewalk (30 km). Length: 135km.Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015 | Progresses as planned |  | 45
45 | 45. 200 | Lubmin (DE) | Erfurt area (DE) | 380-kV-grid enhancement and structural change area Lubmin-Stralsund and area Magdeburg/Wolmirstedt, incl. 380-kV-line Güstrow-Wolmirsted (195 km) | [10 empty] | planned | long term | Progresses as planned |  | 45
45 | 45. 202 | Area upper Lausitz(DE) | Area Gera(DE) | Upgrading existing double-circuit 380kV OHL in the South-Eastern part of the control area of 50Hertz Transmission. Bärwalde-Schmölln length approx.. 50km. Support of RES and conventional generation integration in North-Eastern Germany, maintaining of security of supply and support of market development. | [10 empty] | design & permitting | 2017 | Progresses as planned |  | 45
45 | 45. 204 | Calbe (DE) |  | Construction of new 380kV double-circuit OHL in substation Calbe for double connection/loop into an existing line. | [10 empty] | planned | mid term / long term | The evolution of this investment depends on the development of the power plant in the area. The date mentioned in the TYNDP 2010 was a typing mistake. |  | 45
45 | 45. 205 | Fördertsedt (DE) | Area Magdeburg(DE) | Construction of new 380kV double-circuit OHL from the substation Förderstedt with 20 km length for double connection/loop in for Förderstedt; Reinforcement of existing switchgear, Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015/2020 | Progresses as planned |  | 45
45 | 45. 206 | Area Leipzig(DE) | Area Chemnitz(DE) | Construction of new double-circuit 380-kV-overhead line in existing corridor Röhrsdorf-Remptendorf (103 km) | [10 empty] | under consideration | 2020 | Progresses as planned |  | 45
45 | 45. 207 | Substations in South-Western part of 5 Hertz Transmission control area (DE) |  | Construction of new 380kV substation in Southern Magdeburg area and restructuring of existing 220kV equipment. total length: aprox .50 km | [10 empty] | planned | long term | Some of the investments are to be commissioned by the mid term and the some by long term. |  | 45
45 | 45. 208 | Lines and Substations in South-Western part of 5 Hertz Transmission control area (DE) |  | Construction of new 380kV double-circuit OHL in existing corridor Pulgar-Vieselbach (103 km) Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015/2020 | Progresses as planned |  | 45
45 | 45. 209 | Substations in 5 Hertz Transmission control area |  | Extension of existing and erection of new 380 kV-substations and several 380/110kV-substations, incl. reactive power compensation devices. | [10 empty] | design & permitting | mid term | This investment includes several substations in the control area of 50Hertz Transmission control area. Present status varies form design & permitting, planning to under consideration and the date of commissioning varies from short/mid to long term. |  | 45
| 45. A163 | Wolmirstedt (DE) | Wahle (DE) | New double circuit OHL 380 kV; Line length 111 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A164 | Vieselbach (DE) | Mecklar (DE) | New double circuit OHL 400 kV line in existing OHL corridor . (129 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A165 | Mecklar (DE) | Grafenrheinfeld (DE) | New double circuit OHL 400-kV-line (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A166 | Altenfeld (DE) | Grafenrheinfeld (DE) | New double circuit OHL 400-kV-line (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A169 | Grafenrheinfeld (DE) | Grossgartach (DE) | Additional 380 Kv circuit on a existing lines. Length: 160 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A167 | Redwitz (DE) | Schwandorf (DE) | New double circuit OHL 400 kV line in existing OHL corridor Redwitz-Mechlenreuth-Etzenricht-Schwandorf (185 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A168 | Raitersaich (DE) | Isar (DE) | New 400 kV line in existing OHL corridor Raitersaich - Ludersheim - Sittling - Isar (160 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
45 | 45. 153 | Redwitz (DE) | Grafenrheinfeld (DE) | Upgrade of 230kV connection Redwitz - Grafenrheinfeld to 400kV, including new 400kV switchgear Eltmann. Line length: 97km. | [10 empty] | design & permitting | mid term | Investment delay due to delay in the implementation of the line Halle-Schweinfurt(investment 45. 193) |  | 45
45 | 45. 154 | Redwitz (DE) |  | New 500 MVAr SVC in substation Redwitz. | [10 empty] | planned | mid term | Progresses as planned |  | 45
45 | 45. 155 | Raitersaich (DE) |  | New 500 MVAr SVC in substation Raitersaich. | [10 empty] | planned | mid term | Progresses as planned |  | 45
45 | 45. 47. 158 | [15 empty] | 0 | The investment contributes both to project 45 and project 47. For the technical description see project 47. | 45
46 | 46. 194 | wind farm cluster Baltic Sea East (DE) | Lüdershagen/ Lubmin (DE) | Offshore wind farm connection project (by AC-cables on transmission voltage level or by clustering with DC connections) has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. | >2000 | 4 | 1 | [6 empty] | 1 | design & permitting | 2012-2020 | This investment includes several connections of offshore wind farms in the eastern part of the Baltic Sea. The present expected date of commissioning varies from 2012 to 2020. |  | The integration of offshore wind generation in the Baltic Sea.
46 | 46. 195 | wind farm cluster Baltic Sea West (DE) | Bentwisch (DE) | Offshore wind farm connection project (by AC-cables on transmission voltage level or by clustering with DC connections) has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. | [10 empty] | design & permitting | 2013-2020 | This investment includes several connections of offshore wind farms in the western part of the Baltic Sea. The present expected date of commissioning varies from 2013 to 2020. |  | 46
47 | 47. A76 | Vöhringen / Leupolz (DE) | Westtirol (AT) | Upgrade of an existing OHL to 380 kV, extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. Transmissions routs Vöhringen - Westtirol and Pkt. Woringen - Memmingen. Length: 114 km. This project will increase the current power exchange capacity between the DE, AT and CH. | >2000 | 1 | 2 | [6 empty] | 3 | planned | long term | New investment in TYNDP |  | The reinforcement of the interconnection between Austria and Germany. Also the support the interaction between the RES in Northern Europe(mainly DE) with the pump storage in the Austrian Alps. The project scheduling is not related only to the network needs, but even to the feasibility and to the authorization process (the possibility to anticipate specific projects could be evaluated in the future considering the three above mentioned elements).
47 | 47. 158 | Irsching (DE) | Ottenhofen (DE) | Upgrade of 230kV connection Irsching - Ottenhofen to 400kV, including new 400kV switchgear Zolling. Length 76km. | [10 empty] | planned | mid term | Progresses as planned | The investment contributes also to project 45. | 47
47 | 47. 212 | Isar / Ottenhofen (DE) | St. Peter (AT) | New 400kV double circuit OHL Isar - St. Peter including new 400kV switchgears Altheim, Simbach and St. Peter, and one new 400/230kV transformer in substation Altheim and fourth circuit on line Isar - Ottenhofen. Line length: 90km. | [10 empty] | design & permitting | 2017 | Progresses as planned |  | 47
47 | 47. 26. 216 | St. Peter (AT) | Tauern (AT) | Completion of the 380kV-line St. Peter - Tauern. This contains an upgrade of the existing 380kV-line St. Peter - Salzburg from 220kV-operation to 380kV-operation and the erection of a new internal double circuit 380kV-line connecting the substations Salzburg and Tauern (replacement of existing 220kV-lines on optimized routes). Moreover the erection of the new substations Wagenham and Pongau and the integration of the substations Salzburg and Kaprun is planned. Line length: 130km. | [10 empty] | design & permitting | 2017/2019 | Preparation for the permitting procedure is ongoing. APG is making efforts to set the 380-kV-Salzburg-line 2017 into service. Depending on possible delays during the permitting procedure the commissioning is expected between 2017 and 2019 | The investment contributes also to project 26. | 47
47 | 47. 26. 218 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 47
47 | 47. 219 | Westtirol (AT) | Zell-Ziller (AT) | Upgrade of the existing 220kV-line Westtirol - Zell-Ziller and erection of additional 220/380kV-Transformers. Line length: 105km. | [10 empty] | partly under construction | 2013-2020 | Project consists of several measures and is on schedule |  | 47
47 | 47. 26. 220 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 47
47 | 47. 221 | St. Peter (AT) | Ernsthofen (AT) | Upgrade from 220kV-operation to 380kV and erection of a 380kV-Substation in Ernsthofen and St. Peter. | [10 empty] | under construction | 2013 | The project is on schedule. Permissions are obtained. Commissioning is expected for 2013 |  | 47
48 | 48. 214 | Gabcikovo (SK) | Gőnyü area (HU) | New interconnection (new 2x400 kV tie-line) between SK and HU starting from Gabčíkovo substation (SK) to the Gőnyü substation on Hungarian side ( preliminary decision). Project also includes the erection of new switching station Gabčíkovo next to the existing one. | 1100 SK -> HU; HU -> SK 400 | 3 | 2 | (North-West Hungary) | [5 empty] | 1 | under consideration | 2016 | The commissioning date has been moved to earlier term due to earlier erection of new 400 kV line Veľký Ďur - Gabčíkovo that help to evacuate power from new NPP. | Negotiations still in progress. This project is closely connected with the project of erection of new line between Rimavska Sobota substation (SK) and Sajoivanka substation (HU); see below. | This cluster will increase the transfer capacity between Slovak and Hungarian network systems and increase security of supply. The internal interconnections in Slovakia are necessary for the same objective. Also this cluster is important for support of North - South flow from RES in North of EU.
48 | 48. 298 | Veľký Ďur (SK) | Gabčíkovo (SK) | Erection of new 2x400kV line between two important substations and extension of the substation Veľký Ďur (SK) Line length:93km. | [10 empty] | planned | 2016 | The commissioning date has been moved to earlier term due to ensure security of power evacuation from new NPP in V.ĎUR area. |  | 48
48 | 48. A125 | Veľký Ďur (SK) | Levice (SK) | The erection of new 1x400 kV line between two important Veľký Ďur and Levice substations, including extension of the V.Ďur and Levice substation. The driver for this project is expected connection of to new generation units in Veľký Ďur area. | [10 empty] | under consideration | 2018 | New investment in TYNDP, which will significantly increase of the security and reliability of the power evacuation from new NPP. |  | 48
48 | 48. A126 | Rimavská Sobota (SK) | Sajóivánka (HU) | Connection of the two existing substations (R.Sobota (SK) - Sajoóivánka (HU)) by the new 2x400 kV line (preliminary armed only with one circuit). | [10 empty] | under consideration | 2016 | New investment in TYNDP | Negotiations/bilateral studies in progress. This project is closely connected with the project 2x400kV line Gabčíkovo (SK) - Hungary (see above). | 48
48 | 48. A127 | Sajóivánka (HU) |  | Second 400/120 kV transformer and 2x70 Mvar shunt reactors in station Sajóivánka | [10 empty] | under consideration | 2016 | New investment in TYNDP |  | 48
48 | 48. A128 | Győr (HU) |  | Third 400/120 kV transformer and 70 Mvar shunt reactor in station Győr | [10 empty] | under consideration | 2016 | New investment in TYNDP |  | 48
50 | 50. 238 | Pancevo (RS) | Resita (RO) | New 131 km double circuit 400kV OHL between existing substations in Romania and Serbia (63 km on Romanian side and 68 km on Serbian side). | 1000 | 1 | 3 | Area BeLgrade and south Banat region | [5 empty] | 1 | design & permitting | 2015 (2019?) | Due to financing gap, the commissioning deadline was postponed to 2019. RO intends to apply for funding through the Operational Programme 'Increase of Economic Competitiveness' - Priority Axis 4. This would ensure realization of the project and allow for faster finalization (2015 instead of estimated 2019). Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | This project increases the transfer capability between Serbia, Romania and accommodates new RES generation on the West/East part of Romanian, respectively Serbia. It also increases the transfer capability on the interface between RO+BG/RS+BA+ME.
50 | 50. 269 | Portile de Fier (RO) | Resita (RO) | New 400kV OHL between existing substation 400 kV Portile de Fier and new 400 kV substation Resita. Line length: 116km. New 400 kV substation Resita, with 400/220 kV and 400/110 kV transformers, as development of the existing 220/110 kV substation. | [10 empty] | design & permitting | 2016 | Constructive characteristics were updated as a result of progress of feasibility and design studies. Commissioning date has been slightly shifted. |  | 50
50 | 50. A116 | Beograd 2 (RS) |  | New 400/110 kV substation on the Belgrade territory | [10 empty] | under construction | 2012 | New investment in TYNDP | By taking large amount of load from other Belgrade substations, the investment will both in/ improve the local SoS significantly, and ii/ relieve the constraints on the EHV local network and enable greater inter-area transits. | 50
50 | 50. A117 | Kraljevo 3 (RS) |  | Upgrade of the existing 220/110kV substation Kraljevo 3 by constructing the 400 kV level. | [10 empty] | design & permitting | 2015 | New investment in TYNDP |  | 50
50 | 50. A118 | Kraljevo 3 (RS) | Bajina Basta (RS) | New 140km double circuit 400kV OHL between substation Kraljevo 3 and substation Bajina Basta. Kraljevo 3 (400kV) will be connected to Kragujevac 2 (400 kV) substation, which is connected to a Sofia (Bulgaria) through a 400 kV line. | [10 empty] | planned | >2015 | New investment in TYNDP | New axis for transits from East to the West, typically from Bulgaria to Bosnia and Montenegro, and further to the west. | 50
50 | 50. 270 | Resita( RO) | Timisoara-Sacalaz-Arad (RO) | Upgrade of an existing 220kV double circuit line to 400kV double circuit line and replacement of 220 kV substations Timisoara and Sacalaz with 400 kV substations. Line length: 156km. | [10 empty] | design & permitting | 2022 | Due to financing gap, the commissioning deadline was postponed to 2022. Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 50
53 | 53. 276 | Suceava(RO) | Gadalin(RO) | New 400kV OHL between existing stations. Line length: 260km. | 2000-2500 | 4 | 1 | [6 empty] | 2 | planned | 2021 | Constructive design characteristics and time schedule were updated as a result of progress of feasibility and design studies. |  | The project will help evacuate important amount of new generation (wind +nuclear generation) in Eastern part of Romania
53 | 53. A131 | Stejaru(RO) | Gheorghieni(RO) | Reconductoring (with HTLS) of existing simple circuit 220kV line. | [10 empty] | under consideration | 2015 | New investment in the TYNDP, required to integrate new RES generation and maintain the GTC for the entire project. |  | 53
53 | 53. 273 | Cernavoda (RO) | Stalpu | New 400kV double circuit OHL between existing stations. Line length:145km. | [10 empty] | planned | 2017 | Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 53
53 | 53. 274 | Constanta (RO) | Medgidia(RO) | New 400kV double circuit (one circuit wired) OHL between existing stations. Line length:75km. | [10 empty] | planned | 2020 | As for other investments, the commissioning date was postponed due to financing gap. Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 53
53 | 53. 275 | Smardan(RO) | Gutinas(RO) | New 400kV double circuit OHL between existing stations. Line length:140km. | [10 empty] | planned | 2020 | As for other investments, the commissioning date was postponed due to financing gap. Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 53
53 | 53. 271 | connection IN-OUT in Medgidia(RO) of actual 4 kV OHL Isaccea(RO)-Varna (BG) |  | The 400kV Isaccea (RO) - Varna (BG) is passing near 400 kV substation Medgidia S. The line shall be connected in Medgidia S, through a double circuit OHL. New wind farms shall be connected to the 400 kV OHL Isaccea - Medgidia S section . Substation Medgidia S, 400 kV, shall be refurbished with GIS technology in order to provide necessary space for new connections. | [10 empty] | design & permitting | 2015 | As for other investments, the commissioning date was postponed due to financing gap. Constructive characteristics were updated as a result of progress of feasibility and design studies. |  | 53
53 | 53. A132 | Stalpu (RO) | Teleajen (RO) - Brazi (RO) | Upgrade of an existing 220kV single circuit line to 400kV. New 400 kV substations: Stalpu (400/110kV, 1x250 MVA), Teleajen (400/110kV, 1x400 MVA) | [10 empty] | planned | 2018 | New investment in TYNDP | This investment was merged with investment 273 in TYNDP 2010. They are now presented as separate investments in TYNDP 2012, according to internal project organization. The network development is still the same. | 53
53 | 53. A133 | Fantanele (RO) | Ungheni (RO) | Reconductoring (with HTLS) of existing simple circuit 220kV line. | [10 empty] | under consideration | long term | New investment in the TYNDP, required to accommodate new RES generation not foreseen in the TYNDP 2010, by increasing the GTC for the entire project. |  | 53
53 | 53. 272 | connection IN-OUT in Medgidia(RO) of actual 4 kV OHL Isaccea(RO)-Dobrudja(BG) |  | Connection IN-OUT in Medgidia (RO) of existing 400kV OHL Isaccea (RO)-Dobrudja (BG), passing nearby. The line shall be connected in Medgidia S, through a double circuit OHL. Substation Medgidia S, 400 kV, shall be refurbished with GIS technology in order to provide necessary space for new connections. | [10 empty] | design & permitting | 2015 | As for other investments, the commissioning date was postponed due to financing gap. Constructive characteristics were updated as a result of progress of feasibility and design studies. | New wind farms shall be connected to the 400 kV OHL Isaccea - Medgidia S section. | 53
53 | 53. A134 | Gheorghieni(RO) | Fantanele (RO) | Reconductoring (with HTLS) of existing simple circuit 220kV line. | [10 empty] | under consideration | 2015 | New investment in the TYNDP, required to accommodate new RES generation not foreseen in the TYNDP 2010, by increasing the GTC for the entire project. |  | 53
54 | 54. 293 | Voľa (SK) | point of splitting (SK) | Splitting of the existing single 400kV line between Lemešany and Veľké Kapušany substations to connect the new 400kV substation Voľa with transformation 400/110kV (replacing existing 220kV substation). New 400kV double circuit OHL. Length: 23km | 500 | 2 | 2 | [6 empty] | 1 | design & permitting | 2013 | Progresses as planned |  | This cluster will increase the transfer capacity between Slovak and Hungarian network systems and increase security of supply. The internal interconnections in Slovakia are necessary for the same objective. Also this cluster is important for support of North - South flow from RES in North of EU.
54 | 54. 294 | Lemešany (SK) | Veľké Kapušany (SK) | Erection of new 400 kV line between Lemešany and Veľké Kapušany substations. The project includes the extension both substations Lemešany and V.Kapušany. Line length:100 (including the loop erected under the Investment 54.293). | [10 empty] | planned | 2018 | Progresses as planned |  | 54
54 | 54. A127 | Veľké Kapušany (SK) | tbd (HU) | Erection of new 2x400 line between SK and Hungary (substation on Hungarian side still to be defined) | [10 empty] | under consideration | 2021 | New investment in TYNDP |  | 54
55 | 55. 302 | Vyskov (CZ) | Cechy stred (CZ) | New second circuit 400kV OHL; 1385 MVA. | 3000 | 5 | 5 | Prague area | [5 empty] | 1 | design & permitting | 2015 | Progresses as planned |  | This project is required both to ease power flows West to East and to enhance security of supply of Prague.
55 | 55. 303 | Babylon (CZ) | Bezdecin (CZ) | New second circuit 400kV OHL; 1385 MVA. | [10 empty] | planned | 2016 | Progresses as planned |  | 55
55 | 55. 304 | Babylon (CZ) | Vyskov (CZ) | New second circuit 400kV OHL; 1385 MVA. | [10 empty] | planned | 2018 | Progresses as planned |  | 55
55 | 55. A91 | Praha Sever (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA . | [10 empty] | planned | long term | New investment in TYNDP |  | 55
55 | 55. 310 | Vyskov (CZ) | Reporyje (CZ) | New connection between 2 existing substations line single circuit OHL 1385 MVA. | [10 empty] | under consideration | long term | Schedule harmonization with other priority investments: this investment has been delayed because of priority given to other investments |  | 55
56 | 56. A92 | Chodov (CZ) | Cechy stred (CZ) | Adding second circuit to existing single circuit line OHL upgrade in length of 35.1km. Target capacity 2x1385 MVA. | 1000 | 5 | 5 | [6 empty] | 1 | planned | 2021 | New investment in TYNDP |  | This project is required both to ease power flows West to East and for future generation evacuation.
56 | 56. A93 | Tynec (CZ) | Krasikov (CZ) | Adding second circuit to existing single circuit line OHL upgrade in length of 103.8km. Target capacity 2x1385 MVA. | [10 empty] | planned | 2025 | New investment in TYNDP |  | 56
57 | 57. 320 | Dargoleza (PL) |  | A new AC 400/110kV (450 MVA) substation between existing substations Słupsk and Żarnowiec in Northern Poland. New substation Dargoleza is connected by splitting and extending of existing 400kV line Słupsk - Dargoleza. | 3000 | 4 | 1 | [6 empty] | 2 | planned | 2020 | The new substation Dargoleza is required for the connection new wind generation in Northern Poland. The time horizon for comissioning of this investment has been changed due to change in wind farms connection schedule in the region. |  | Wind – the infrastructure in this project assures reliable connection of 3000 MW of wind generation in northern Poland. It also allows the evacuation of power in the southern direction.
57 | 57. 328 | Piła Krzewina (PL) | Bydgoszcz Zachód (PL) | New 84km 400kV double circuit 2x1870 MVA OHL interconnection line Piła Krzewina - Bydgoszcz Zachód temporarily on 220kV. | [10 empty] | design & permitting | 2016 | The time schedule of the project was shifted to meet the schedule of the RES (wind) generation connection. This one year delay in the plans appeared after updating of the NDP. The change in the NDP introduced a double circuit. |  | 57
57 | 57. 329 | Żydowo (PL) | Słupsk (PL) | A new AC 400/110kV substation next to existing 220/110kV substation in Northern Poland with transformation 400/110kV 450 MVA. New substation Żydowo is connected by new 70km 400kV 2x1870 MVA OHL double circuit lines Żydowo - Słupsk and Żydowo - Gdańsk Przyjaźń. Dismantling of existing 220/110kV transformers + Upgrade of substation SŁupsk | [10 empty] | planned | 2020 | The date of commissioning evolved due to regulatory, social and environmental issues. The investment also foresee upgrade works in substation Słupsk. |  | 57
57 | 57. 330 | Żydowo (PL) | Gdańsk Przyjaźń (PL) | A new AC substation in Gdańsk Agglomeration Area. New substation Gdańsk Przyjaźń is connected by splitting and extending of one circuit of existing line Żarnowiec - Gdańsk Błonia and new 150km 400kV 2x1870 MVA double circuit OHL line Żydowo - Gdańsk Przyjaźń with one circuit from Żydowo to Gdańsk temporarily on 220kV after dismantling of 220kV line Żydowo - Gdańsk. | [10 empty] | planned | 2020 | The date of commissioning evolved due to regulatory, social and environmental issues. |  | 57
57 | 57. 352 | Dunowo (PL) | Plewiska (PL) | Construction of a new double circuit 400kV OHL Dunowo - Żydowo (2x1870 MVA) partly using existing 220kV line + Construction of a new 400kV OHL Plewiska - Piła Krzewina - Żydowo (2x1870 MVA); single circuit temporarily working as a 220kV + A new AC 400kV switchgear in existing substation Pila Krzewina + upgrade of substation Dunowo | [10 empty] | design & permitting | 2020 | Progressed as planned. The investment also foresee upgrade works in substation Dunowo. |  | 57
58 | 58. 353 | Krajnik (PL) | Baczyna (PL) | Construction of a new double circuit 400kV OHL Krajnik - Baczyna (2x1870 MVA, 91km); single circuit temporarily working at 220kV on Krajnik - Gorzów part + New substation 400kV Baczyna will be connected by splitting and extending existing line Krajnik-Plewiska + Upgrading of limitations line Krajnik - Plewiska. | >1000 | 1 | 2 | [6 empty] | 2 | planned | 2020 | Progresses as planned |  | Bridge – third interconnection between Poland and Germany.
58 | 58. 355 | Mikułowa (PL) | Świebodzice (PL) | Double circuit line 220kV Mikułowa-Świebodzice will be upgraded to 400kV - single circuit temporarily working at 220kV. | [10 empty] | planned | 2020 | Progresses as planned |  | 58
58 | 58. A67 | Gubin (PL) |  | New 400 kV substation planned near the PL-DE border. The substation will be connected to planned line Eisenhüttenstadt (DE) - Plewiska (PL) creating new lines Eisenhüttenstadt (DE) - Gubin (PL) and Gubin (PL) - Plewiska (PL). | [10 empty] | planned | 2020 | New investment in TYNDP | This new substation on the third DE-PL connection is necessary for future generation connection while ensuring interconnection capability. | 58
58 | 58. 140 | Eisenhüttenstadt (DE) | Plewiska (PL) | New 400kV double circuit OHL Eisenhüttenstadt (DE) - Plewiska (PL) including the construction of new substation Plewiska Bis (PL) | [10 empty] | planned | 2020 | Progresses as planned |  | 58
59 | 59. 368 | Ełk (PL) | PL-LT border (LT) | Construction of a new 400kV OHL Ełk to PL-LT border. (2x1870 MVA, 108km). | 1000 | 1 | 5 | South LT and NE/central PL | [5 empty] | 3 | design & permitting | 2015 | Progresses as planned |  | “LitPol Link” project. Interconnection of Lithuanian power system with Polish power system via Back to Back station. This project allows integration of Baltics to the internal European power market,
59 | 59. 369 | Siedlce Ujrzanów (PL) | Miłosna (PL) | Construction of a new 400kV OHL Siedlce Ujrzanów - Miłosna (1870 MVA, 84km) + A new AC 400kV switchgear in existing substation Siedlce Ujrzanow with transformation 400/110kV 400 MVA. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 59
59 | 59. 370 | Ełk (PL) | Łomża (PL) | Construction of a new 400kV double circuit OHL Ełk - Łomża (2x1870 MVA, 95km) + A new AC 400kV switchgear in existing substation Elk + A new 400 kV AC substation Łomża | [10 empty] | design & permitting | 2015 | Łomża has been elected as end substation for the project and the technical description is adapted accordingly. Progresses as planned otherwise. |  | 59
59 | 59. 371 | Ostrołęka (PL) | Narew (PL) | Construction of a new 400kV OHL Ostrołęka-Łomża-Narew (1870 MVA, 120km) + A new AC 400kV switchgear in existing substation Ostroleka (in two stages) with transformation 400/220kV 500 MVA and with transformation 400/110kV 400 MVA + extension of 400 switchgear in substation Narew. | [10 empty] | design & permitting | 2015 | Progressed as planned. The investment also foresee extension works in substation Narew. |  | 59
59 | 59. 372 | Oltarzew (PL) |  | A new AC substation with two transformers 400/220kV 2x500 MVA and one 400/110kV 330 MVA will be connected by splitting 400kV line Rogowiec-Miłosna and Miłosna-Płock and 220kV line Mory-Sochaczew and Mory-Janów. | [10 empty] | under construction | 2015 | Progresses as planned |  | 59
59 | 59. 373 | Ostrołęka (PL) | Stanisławów (PL) | Single circuit line 220kV Ostrołęka-Miłosna will be partly upgraded to double circuit line 400kV (2x1870 MVA, 106km) with development of Ostrołęka 400kV substation + New substation 400kV Stanisławów will be connected by splitting and extending existing line Miłosna-Narew and Miłosna-Siedlce. | [10 empty] | design & permitting | 2020 | Progresses as planned |  | 59
59 | 59. 374 | Kozienice (PL) | Siedlce Ujrzanów (PL) | Existing single circuit line will be upgraded to 400kV line in the same direction (1870 MVA, 90km) + upgrade of Kozienice substation to connect the new line | [10 empty] | design & permitting | 2020 | Progressed as planned. The investment also foresee extension works in substation Kozienice |  | 59
59 | 59. 375 | Płock (PL) | Olsztyn Mątki (PL) | New single circuit line 400kV (1870 MVA, 180km) with development of Olsztyn Mątki 400kV substation. | [10 empty] | design & permitting | 2020 | Progresses as planned |  | 59
59 | 59. 376 | Alytus (LT) | PL-LT border (PL) | Construction of Back-to-Back convertor station near Alytus 330kV substation. Construction of double circuit 400 kV OHL between Alytus and PL – LT border (2 x 1,870 MVA, 51 km). | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 59
59 | 59. 379 | Kruonis (LT) | Alytus (LT) | New double circuit 330kV OHL (2x1080 MVA, 53km). | [10 empty] | planned | 2015 | Progresses faster than intially planned to support the LitPol project |  | 59
90 | 90. 131 | Bickigen (CH) |  | Addition of a second 400/220kV transformer in an existing substation. | 4000 | 1 | 2 | [6 empty] | 3 | design & permitting | 2012 | Progresses as planned |  | This project increase the transfer capability between FR, DE , AT towards pump storage in CH.
90 | 90. 132 | Mühleberg (CH) |  | Construction of a new 400/220kV substation. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 90
90 | 90. 134 | Bassecourt (CH) | Romanel (CH) | Construction of different new 400kV line sections and voltage upgrade of existing 225kV lines into 400kV lines. Total length: 140km. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 90
90 | 90. 136 | Area of Bodensee (DE, AT, CH) |  | Construction of new lines, extension of existing ones in direction of 400/220/110kV-substation. This project will increase the current power exchange capacity between the DE, AT and CH. The project is expected to increase NTC and Improved the security of supply. | [10 empty] | planned | long term | Progress as planned |  | 90
90 | 90. 129 | Beznau (CH) | Mettlen (CH) | Upgrade of the existing 65km double circuit 220kV OHL to 400kV. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 90
90 | 90. 130 | La Punt (CH) | Pradella / Ova Spin (CH) | Installation of the second circuit on existing towers of a double-circuit 400kV OHL (50km). | [10 empty] | planned | 2017 | Delays due to authorization process. |  | 90
90 | 90. 133 | Bonaduz (CH) | Mettlen (CH) | Upgrade of the existing 180km double circuit 220kV OHL into 400kV. | [10 empty] | under consideration | 2020 | Progresses as planned |  | 90
90 | 90. 44. 170 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 172 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 173 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 176 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 45. 177 | Goldshöfe (DE) | Bünzwangen (DE) | A new 380kV OHL. Length: 45km. | [10 empty] | under consideration | 2020 | Progresses as planned | The investment contributes also to project 45. | 90
92 | 92. 146 | Aachen/Düren region (DE) | Lixhe (BE) | Connection between Germany and Belgium including new 100km HVDC underground cable and extension of existing 380kV-substations. On Belgian side, new 380 kV circuit between Lixhe and Herderen and second 380 kV overheadline in/out from Herderen to Lixhe. In Belgium, addition of 2 transformers 380/150 kV in Lixhe and in Limburg part; | 1000 | 3 | 2 | Northern Belgium | [5 empty] | 2 | design & permitting | 2017 | The project entered design and permitting phase in 2011, technical description has been completed and expected date of comissioning is 2017 | Alegro Project | First Belgium-Germany interconnection. This project enhances security of supply of both BE and DE. This HVDC link in an AC grid brings flexibility and bidirectional power control allowing integration of RES in both countries. This project aims to be a demonstration for HVDC link integration in the AC meshed grid.
94 | 94. 139 | Vierraden (DE) | Krajnik (PL) | Upgrade of existing 220 kV line Vierraden-Krajnik to double circuit 400 kV OHL. | >1000 | 1 | 2 | [6 empty] | 1 | design & permitting | long term | Expected date of commissioning was adjusted due to long permitting process and strong local public resistance. |  | PSTs – Control of the transits of power on the polish synchronous profile (increase of import capacity, increase of grid operation safety).
94 | 94. A68 | Krajnik (PL) |  | Upgrade 400 kV | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A69 | Mikułowa (PL) |  | Upgrade 400 kV | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A70 | Krajnik (PL) |  | New PST | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A71 | Mikułowa (PL) |  | New PST | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
95 | 95. A119 | Dobrudja(BG) | Burgas (BG) | New 140km single circuit 400kV OHL in parallel to the existing one. | 1500 | 4 | 3 | [6 empty] | 1 | planned | 2016 | New investment in TYNDP, required to accommodate 2000MW RES in Dobrudja region |  | It contributes to the accommodation of large amount of RES in Dobrudja region (2000 MW). It also contributes to North-South transfers and increases the SoS in Burgas region.
95 | 95. 265 | Vidno (BG) | Svoboda (BG) | New 400kV double circuit OHL to accommodate 2000 MW RES generation in N-E Bulgaria (Dobruja region). Line length: 2x70km. | [10 empty] | planned | 2015 | Moved from LT(TYNDP 2010) to MT due to high interest for very fast implementation of about 2000MW RES generation in Dobrudja region |  | 95
95 | 95. 263 | SS 4 /11 kV Svoboda(Krusari) |  | New 400/110kV substation to accommodate the expected RES generation(2000MW) in N-E Bulgaria (Dobruja region) | [10 empty] | planned | 2015 |  |  | 95
95 | 95. 264 | SS 4 /11 kV Vidno |  | New 400/110kV substation to accommodate the expected RES generation(2000MW) in N-E Bulgaria (Dobruja region) | [10 empty] | planned | 2015 |  |  | 95
95 | 95. 266 | IN-OUT in Svoboda on actual 4 kV OHL Isaccea(RO)-Varna (BG) |  | New 400kV double circuit OHL to accommodate the expected RES generation(2000MW) in N-E Bulgaria (Dobruja region). Line length: 2x10km. | [10 empty] | planned | 2015 |  |  | 95
99 | 99. 324 | Dobrzeń (PL) | Wrocław/ Pasikurowice (PL) | New 76 km 400kV 2x1870 MVA OHL double circuit line from Dobrzeń to splitted Pasikurowice - Wrocław line + upgrade and extension of 400 kV switchgear in substation Dobrzeń. | 1800 | 4 | 5 | Warsaw and lower Silesia area | [5 empty] | 1 | design & permitting | 2017 | Progresses globally as planned. Technical description and commissioning date have been updated so as to deliver full benefit as from 2017 |  | Dobrzeń - the project introduces new infrastructure (2x400 kV line) to allow power evacuation from two (2x9000 MW) conventional units to be installed in existing power plant Opole. The new line provides power supply for agglomeration Wroclaw, it increases the SoS for this area.
100 | 100. 335 | Ostrołęka (PL) | Olsztyn Mątki (PL) | New 138km 400kV 2x1870 MVA double circuit OHL line Ostrołęka - Olsztyn Mątki after dismantling of 220kV line Ostrołęka - Olsztyn with one circuit from Ostrołęka to Olsztyn temporarily on 220kV. | 1000 | 4 | 5 | [6 empty] | 1 | design & permitting | 2017 | The time schedule of the project was shifted to meet the schedule of the generation connection. |  | Ostrołęka - the new 400 kV line allows power evacuation from new 1000 MW conventional unit to be installed in existing power plant Ostroleka.
101 | 101. 327 | Kozienice (PL) | Ołtarzew (PL) | New 130km 400kV 2x1870 MVA OHL double circuit line Kozienice - Ołtarzew + upgrade and extension of 400 kV switchgear in substation Kozienice for the connection of new line | 1000 | 4 | 5 | Warsaw area | [5 empty] | 1 | design & permitting | 2017 | The time schedule of the project was shifted to meet the schedule of the generation connection. |  | Kozienice - the new 2x400 kV line allows power evacuation from new 1000 MW conventional unit to be installed in existing power plant Kozienice. The new unit is foreseen to supply Warsaw agglomeration area. The project also allows to close the 400 kV ring around Warsaw agglomeration are increasing the SoS significantly.
101 | 101. 338 | Kozienice (PL) | Mory/ Piaseczno (PL) | Replacement of conductors (high temperature conductors). | [10 empty] | under construction | 2014 | Progresses as planned, with commissioning now expected in 2014 |  | 101
102 | 102. A72 | Gdańsk Błonia (PL) |  | Extension and upgrade of an existing 400/110 kV substation Gdańsk Błonia for connection of planned 900 MW power plant. | 2900 | 4 | 5 | [6 empty] | 2 | planned | 2020 | New investment in TYNDP | Power Evacuation North. The upgraded substation will connect a planned 900 MW CCPP. | North - the North-South corridor provides necessary capacity to evacuate the power from new 2900 MW of conventional generation planned to be installed in northern Poland.
102 | 102. 334 | Pątnów (PL) | Grudziądz (PL) | New 174km 400kV 2x1870 MVA double circuit OHL line Pątnów - Grudziądz after dismantling of 220kV line Pątnów - Jasiniec (two parallel lines) and Jasiniec - Grudziądz. One circuit from Pątnów to Grudziądz via Jasiniec temporarily on 220kV. | [10 empty] | design & permitting | 2020 | The time schedule of the project was shifted to meet the schedule of the generation connection. | Power Evacuation North | 102
102 | 102. 326 | Grudziądz (PL) | Gdańsk Przyjaźń (PL) | A new AC 400/110kV substation between existing substation Grudziądz and planned substation Gdańsk Przyjaźń. New substation Pelplin is connected by new 110km 400kV 2x1870 MVA OHL double circuit lines Grudziądz - Pelplin and Pelplin - Gdańsk Przyjaźń after dismantling of 220kV line Jasiniec - Gdańsk. | [10 empty] | planned | 2020 | The time schedule of the project was shifted to meet the schedule of the generation connection. | Power Evacuation North | 102
103 | 103. 145 | Niederrhein (DE) | Doetinchem (NL) | New 400kV line double circuit DE-NL interconnection line. Length:60km. | 13900 | 3 | 1 | NW part of Netherlands | [5 empty] | 3 | design & permitting | >=2013 | Delays due to authorization process. |  | The project reinforces the Dutch grid to accommodate new conventional and renewable generation, to handle new flow patterns and to increase the interconnection capacity between DE and NL"
103 | 103. 438 | Eemshaven (NL) | Diemen (NL) | New 175-200km AC overhead line with capacity of 2x2650 MVA of 380kV. | [10 empty] | design & permitting | 2018 | Delays due to authorization process. |  | 103
103 | 103. 439 | Borssele (NL) | Geertruidenberg (NL) | New 100-130km double-circuit 380kV OHL with 2x2650 MVA capacity. | [10 empty] | design & permitting | 2016 | Delays due to authorization process. |  | 103
103 | 103. 440 | Maasvlakte (NL) | Beverwijk (NL) | New 380 kV double-circuit mixed project (OHL+ underground cable) including approximately 20km of underground cable for 2650 MVA. The cable sections are a pilot project. The total length of cable at 380kV is frozen until more experience is gained. | [10 empty] | under construction | 2016 | Delays due to authorization process. |  | 103
103 | 103. 441 | Zwolle (NL) | Hengelo (NL) | Upgrade of the capacity of the existing 60km double circuit 380kV OHL to reach a capacity of 2x2650 MVA. | [10 empty] | under consideration | long term | Progresses as planned. |  | 103
103 | 103. 442 | Krimpen aan de Ijssel (NL) | Maasbracht (NL) | Upgrade of the capacity of the existing 150km double circuit 380kV OHL to reach a capacity of 2x2650 MVA. | [10 empty] | under consideration | long term | Progresses as planned. |  | 103
108 | 108. A134 | Tarnita (RO) | Mintia (RO) | New 145km double circuit 400kV OHL | 1000 | 4 | 1 | [6 empty] | 1 | planned | 2018 | New investment in TYNDP | Connection of pumped storage hydro plant Tarnita Lapustesti to the grid. The plant has an installed capacity of 1000 MW and will support system balancing, especially in order to face the intermittent RES output. | The project will connect to the grid 1000MW hydro pump storage.
108 | 108. A135 | Tarnita (RO) | Cluj E - Gadalin (RO) | New 40km double circuit 400kV OHL | [10 empty] | planned | 2018 | New investment in TYNDP |  | 108
108 | 108. A136 | Tarnita (RO) |  | New 400kV substation | [10 empty] | planned | 2018 | New investment in TYNDP |  | 108
| 58 | Ensdorf (DE) | St. Avold (FR) | Change of conductors on the German part of this single circuit 220kV line (9 km) and installation of a phase-shifter in Ensdorf (DE) 220kV substation. | [10 empty] | commissioned | commissioned | Commissioned
| 69 | Candia (IT) | Konjsko (HR) | New 1000MW HVDC interconnection line between Italy and Croatia via 280km 500kVDC subsea cable and converters stations at both ending points. | [10 empty] | under consideration | post 2022 | These incestments are very sensitive to the market and still under investigation
| 168 | Goldshöfe (DE) | Dellmensigen (DE) | Upgrade the line Goldshöfe - Dellmensigen from 220kV to 380kV . Line length:114km. Included with the project : 3x 380kV substations, 2 transformers. | [10 empty] | under construction | 2014 | Investment 168 has been postponed to 2014 due to local resistance against the project in a specific area. The rest of the investment is ready.
| 168a | Region South-West Bavaria (DE) |  | Upgrading the existing 220kV OHL to 380kV,length 100km and the extension of existing substations, erection of 380/110kV-transformers. | [10 empty] | cancelled | cancelled | The project was abandoned - was not seen necessary with the new set of projects in place. Note: in the previous TYNDP the status of the project was under consideration and not planned (printing mistake)
| 192 | Hamburg/Krümmel (DE) | Schwerin (DE) | This 380kV double-circuit OHL project will close the missing gap in North-East German grid infrastructure. Only 65km of new line must be constructed, 22km already exist. | [10 empty] | under construction | 2012/2013 | Commissioning delayed by complex permitting procedure, line is partly constructed, is expected to be commissioned in 2012/2013 short term
| 198 | Wuhlheide (DE) | Thyrow (DE) | Berlin South Ring: replacement of an existing old 220kV double-circuit OHL by a 380kV double-circuit OHL. Length: 50km. | [10 empty] | cancelled | cancelled | Project was depending on the replacement of a CHP power plant based in Berlin, due to a new general CHP-concept the plant size could be adopted and the upgrade of the existing 220-kV connection to 380-kV was not necessary any longer, project was given up with regard to the CHP-Plant investor
| 222 | Silz (AT) | Zell-Ziller (AT) | Upgrade of the existing 220kV-double circuit- OHL Zell-Ziller - Silz. Line length: 42km. | [10 empty] | under construction | 2013/2014 | Progress as planned | This line, due to change in, switched from the TSO environment to the distribution area.
| 230 | TPP Sisak (HR) | Mraclin(HR)/Prijedor(BA) | Connection of new generator on existing line 220kV Mraclin (HR) - Prijedor (BA) via a new double circuit OHL. Line length: 12km. | [10 empty] | design & permitting | 2012-2013 | The commissioning date is postponed due to the prolonged permitting procedures and due to the harmonization with installation of new generating unit in TPP Sisak.
| 279 | Gyor (HU) | Martonvasar (HU) | Upgrade of an existing 220kV single circuit line to 400kV double circuit. Line length:84km. | [10 empty] | under construction | 2012 | It will be commissioned by the end of 2012
| 282 | Sajoszoged / God (HU) | Detk (HU) | New substation Detk with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Sajoszoged-God. | [10 empty] | design & permitting | 2017 | The project was delayed due to a change in the generation(decommissioning of units connected to 120 kV deferred) which led to a delay in investment need
| 284 | Martonvasar / Paks (HU) | Dunaujvaros (HU) | New substation Dunaujvaros with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Martonvasar-Paks. | [10 empty] | design & permitting | 2015 | 2012->2015: Delayed due to delay in investment need, according to National Plan 2010 (load growth in the specific area will be lower than previously forecasted)
| 285 | Debrecen (HU) |  | New substation Debrecen with 2*250 MVA 400/120kV transformation is connected by changing the operating voltage of line Sajoszoged-Debrecen from 220kV to 400kV, this line being already designed for 400kV. | [10 empty] | design & permitting | 2013 | Progress as planned.
| 286 | Martonvasar / Liter (HU) | Szekesfehervar (HU) | New substation Szekesfehervar with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Martonvasar-Liter. | [10 empty] | planned | 2016 | 2014->2016: Delayed due to delay in investment need, according to National Plan 2010 (load growth in the specific area will be lower than previously forecasted)
| 287 | Albertirsa / God (HU) | Godollo (HU) | New substation Godollo with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Albertirsa-God. | [10 empty] | planned | 2015 | progress as planned
| 288 | Albertirsa / Martonvasar (HU) | Szazhalombatta (HU) | New substation Szazhalombatta is connected by splitting and extending existing line Albertirsa-Martonvasar. | [10 empty] | planned | 2015 | progress as planned
| 289 | Felsozsolca (HU) | Sajoivanka (HU) | Reconstruction of line to double circuit, installation of the 2nd transformer in substation Sajoivanka. Line length: 29km. | [10 empty] | cancelled | cancelled | Cancelled: new cluster #53 makes this investment unnecessary.
| 290 | Oroszlany (HU) |  | New substation Oroszlany with 2*250 MVA 400/120kV transformation is connected by splitting and extending the second circuit of line Martonvasar-Gyor. | [10 empty] | under consideration | 2016 | 2017->2016: Earlier completion is foreseen for financing and organization reasons.
| 291 | Sajoszoged (HU) |  | New 400/120kV 250MVA transformer with PST. | [10 empty] | cancelled | cancelled | Cancelled according to National Plan 2010; generation pattern in the specific area will change significantly thus this investment is no longer necessary.
| 292 | Debrecen (HU) |  | Reconstruction of 750kV substation. | [10 empty] | design & permitting | 2013 | progress as planned
| 296 | Medzibrod (SK) | point of splitting (SK) | Connection of existing 220/110kV Medzibrod substation to the 400kV system by splitting the single 400kV line Sučany - Liptovská Mara. Project includes also the reconstruction of Medzibrod substation from 220kV level to 400kV including transformation 400/110kV. Line length:36km. | [10 empty] | under construction | 2013 | Substation Medzibrod has been reconstructed to the level of 400 kV (still operated on the level 220 kV till the new 400 kV lines will be completed).
| 297 | Križovany (SK) | Horná Ždaňa (SK) | The new substation Bystričany with transformation 400/110kV will be connected to the 400kV system by two new 2x400kV lines from Horná Ždaňa and Križovany substations by splitting only one circuit in Bystričany substation. In the future the substation will be also equipped with a 220kV switchgear. Line length:112km. | [10 empty] | planned | 2019 | Change of the date according to the changed investment plan schedule in the development plan of SEPS.
| 299 | Krasikov (CZ) | Horni Zivotice (CZ) | New single circuit 400kV OHL, 1385 MVA. | [10 empty] | design & permitting | 2014 | Progresses as planned
| 322 | Kromolice (PL) |  | A new AC substation between existing substations Plewiska and Ostrów and Pątnów in Poznań Agglomeration Area with transformation 400/110kV 400 MVA. New substation Kromolice is connected by splitting and extending existing line Ostrów-Plewiska and Pątnów - Plewiska. | [10 empty] | under construction | 2012 | The investment process ongoing according to plan. Faster commissioning date reported after update of NDP. The project will be commissioned by the end on 2012,
| 331 | Gorzów (PL) | Leśniow (PL) | Upgrading of sag limitations (new capacity 461 MVA). | [10 empty] | planned | 2015 | The investment process ongoing according to plan
| 336 | Warszawa Praga (PL) |  | A new AC substation with 2x275 MVA 220/110kV transformation between existing substations Miłosna and Mory in Warszawa Agglomeration Area, New substation Warszawa Praga is connected by splitting and extending existing line Miłosna-Mory. | [10 empty] | planned | >2015 | The project is in the plans for generation connection purpose. Planned comissioning is dependent upon generation investment (the investor has withdrawn a new gen. unit from the plans). There is an existing combined heat power plant in this area; possible new generation in the future.
| 344 | Lublin Systemowa (PL) | Abramowice (PL) | New 220kV cable/OHL interconnection line Lublin Systemowa - Abramowice, in Lublin agglomeration area (522 MVA, 18km). | [10 empty] | design & permitting | >2020 | Investment postponed due to change in generation sector plans.
| 346 | Halemba (PL) |  | Halemba substation is connected by splitting and extending of existing 220kV lines Kopanina - Katowice. | [10 empty] | cancelled | cancelled | Project withdrawn from TSO plans because of cancellation of construction of new generation unit.
| 348 | several substations in PSE O control area |  | Installation additional and exchange existing transformers (400/110kV and 220/110kV), capacitors and SVC in substations, upgrading of substations. | [10 empty] | design & permitting | 2015 | The investment process ongoing according to plan.
| 349 | Puławy (PL) |  | A new AC 400kV switchgear in existing substation Pulawy (with transformation 400/220kV 500 MVA) will be connected by splitting and extending existing 400kV lines: Kozienice- Lublin Systemowa and Kozienice - Ostrowiec. | [10 empty] | planned | 2020 | The investment process ongoing according to plan. This investment is connected to the construction of a new power plant.
| 350 | Chełm (PL) | Lublin Systemowa (PL) | Construction of a new 400 kV OHL Lublin Systemowa-Chełm with single circuit (1870 MVA). A new AC 400kV switchgear in existing substation Chelm with transformation 400/220kV 500 MVA. | [10 empty] | planned | 2020 | Upon withdrawal of new conventional power plant from the plans the content of the project in the area has changed. Initially the project was foreseen to accommodate a conventional generator.
| 351 | Blachownia (PL) |  | A new AC 400kV switchgear in existing substation Blachownia (with transformation 400/220kV 500 MVA and 400/110kV 400 MVA) will be connected by splitting and extending existing 400kV line Joachimów - Wielopole and 220kV line Kedzierzyn - Groszowice. | [10 empty] | planned | 2020 | The project is in the plans for generation connection purpose. Planned comissioning is dependent upon generation investment (the investor has withdrawn a new gen. unit from the plans). There is an existing heat power plant in this area; possible new generation in the future.
| 354 | Byczyna (PL) | Podborze (PL) | Double line 400kV Byczyna-Czeczott-Podborze (2x1870 MVA, 155km) will be built in parallel with 220kV line Byczyna-Bieruń-Poręba-Podborze in the same road + New substation 400 and 220kV Podborze (with transformation 400/220kV 500 MVA) will be connected by splitting and extending existing lines Wielopole-Nosovice, Kopanina-Liskovec, Bujaków-Liskovec, Komorowice-Bieruń, Moszczenica-Poręba and new double circuit line 400kV Podborze-Czeczott. | [10 empty] | design & permitting | after 2020 | The delay in the plans appeared after updating of the NDP. The time schedule of the project was shifted to meet the schedule of the generation connection.
| 356 | Janów (PL) |  | New substation 400kV Janów (with transformation 400/110kV 400 MVA) will be connected by splitting and extending existing line Rogowiec-Płock. | [10 empty] | planned | 2020 | The investment process is according to the plan.
| 357 | Joachimów (PL) |  | Replacement of a transformer 400/220kV (500 MVA). | [10 empty] | planned | 2020 | The investment process ongoing according to plan
| 359 | Morzyczyn (PL) | Pomorzany/ Glinki (PL) | New line 220kV (522 MVA). | [10 empty] | planned | >2020 | Future realization of the investment dependent upon needs of increase of security of supply in the Szczecin agglomeration area.
| 360 | Miłosna (PL) | Siekierki (PL) | New cable connection 220kV Miłosna - Warszawa Siekierki (333 MVA, 10km). | [10 empty] | planned | >2020 | Future realization of the investment dependent upon needs of increase of security of supply in the Warcowa agglomeration area.
| 361 | Ołtarzew (PL) | Mory (PL) | Replacement of conductors (high temperature conductors). (new capacity 461 MVA). | [10 empty] | planned | 2020 | The investment process ongoing according to plan. The upgrade method not decided yet.
| 362 | Wielopole (PL) | Moszczenica (PL) | Replacement of conductors (high temperature conductors). (new capacity 461 MVA). | [10 empty] | planned | 2020 | The investment process ongoing according to plan. The upgrade method not decided yet.
| 363 | Byczyna (PL) | Siersza (PL) | Replacement of conductors (high temperature conductors). (new capacity 461 MVA). | [10 empty] | planned | 2020 | The investment process ongoing according to plan. The upgrade method not decided yet.
| 367 | several substations in PSE O control area |  | Installation of an additional transformer + replacement of an existing one (400/110kV and 220/110kV) and shunt reactors in substations, upgrading and decommissioning of substations. | [10 empty] | planned | 2020 | The investment process ongoing according to plan.
| 319 | Skawina (PL) |  | A new AC 400/110kV substation next to existing 220/110kV substation in Cracow Agglomeration Area with transformation 400/110kV 2x400 MVA. New substation Skawina is connected by splitting and extending of existing 400kV lines Tarnów - Tucznawa and Rzeszów - Tucznawa. Dismantling of existing 220/110kV transformers. | [10 empty] | design & permitting | 2015 | The investment process ongoing according to plan
| 321 | Kromolice (PL) | Pątnów (PL) | New 79km 400kV 1870 MVA OHL interconnection line Kromolice - Pątnów - with one circuit from Plewiska to Koninn temporarily on 220kV after dismantling of 220kV line Plewiska - Konin. | [10 empty] | under construction | end 2012 | The investment process ongoing according to plan. Faster commissioning date reported after update of NDP. This project is due to be put in operation by the end 2012.
| 323 | Warszawa Siekierki (PL) | Piaseczno (PL) | A new AC 220/110kV substation (with transformation 220/110kV 2x275MVA) in Warsaw Agglomeration Area connected by a new 20km 220kV 333 MVA cable/OHL line Warszawa Siekierki - Piaseczno. | [10 empty] | design & permitting | 2020 | Investment postponed due to change in new generation unit connection schedule which was scheduled for 2015 but it was withdrawn from the medium term.
| 325 | Krajnik (PL) | Pomorzany (PL) | A new AC substation in Szczecin Agglomeration Area. New substation Pomorzany is connected by new 24km 220kV 522 MVA line Krajnik - Pomorzany and 220/110kV (275 MVA) transformer to existing 110kV switchgear. | [10 empty] | planned | 2016 | The delay in the plans appeared after updating of the NDP. The time schedule of the project was shifted to meet the schedule of the generation connection (combined cycle power plant in Pomorzany).
| 332 | Recław (PL) | Glinki (PL) | A new AC substation in Szczecin Agglomeration Area. New substation Recław is connected by new 52km 220kV 522 MVA line Recław - Glinki, existing 110kV single circuit line Morzyczyn - Recław upgraded to 220kV and two 220/110kV (275 MVA) transformer to existing 110kV switchgear. Splitting of existing 220kV line Morzyczyn - Police and expanding to Glinki substation. | [10 empty] | design & permitting | 2016 | The delay in the plans appeared after updating of the NDP. The time schedule of the project was shifted due to proper coordination with other investments in the area (325).
| 333 | Pasikurowice (PL) | Świebodzice (PL) | A new AC substation in Wrocław Agglomeration Area. New substation Wrocław is connected to new 135km (sum) 400kV 1870 MVA lines: Pasikurowice-Wrocław and Świebodzice - Wrocław. New 400kV Wrocław substation with 2x400 MVA, 400/110kV transformation. New 400kV Świebodzice substation with 1x500MVA, 400/220kV transformation and 1x400 MVA, 400/110kV transformation. New 400kV OHL interconnection line Wrocław - Świebodzice after dismantling of 220kV line Świebodzice - Biskupice and new 400kV OHL interconnection line Pasikurowice - Wrocław, including new Wrocław substation. | [10 empty] | under construction | 2015 | The investment process ongoing according to plan. The line Pasikurowice-Wrocławd and the substation Wrocław are already commissioned.
| 337 | Radkowice (PL) | Kielce Piaski (PL) | New 26km 220kV 522 MVA OHL line Radkowice -Kielce Piaski, in Kielce agglomeration area. | [10 empty] | design & permitting | 2015 | The investment process ongoing according to plan
| 340 | Lubocza (PL) |  | An existing substation in Kraków Agglomeration Area. Existing substation will be upgraded by splitting and extending existing 220kV line Siersza- Klikowa and installing second ATR 220/110kV (160 MVA). | [10 empty] | commissioned | commissioned | In the previous NDPs of PL the proejcts were structure in steps of 5 years. Therefore the date of commissioning mentioned din Tend 2010 is 2015. The project will be commissioned by the end of 2012.
| 341 | Pątnów (PL) | Włocławek (PL) | Upgrading of sag limitations OHL 220kV (389 MVA). | [10 empty] | cancelled | cancelled | Investment suspended. After connection of planned generation unit in substation Włocławek Azoty the possibility of overload in the existing lines is eliminated.
| 342 | Czarna (PL) | Polkowice (PL) | New 400kV OHL interconnection line Czarna -Polkowice (1870 MVA, 22km), including new Polkowice 400kV substation with 500 MVA, 400/220kV transformation. | [10 empty] | design & permitting | 2016 | The investment process ongoing according to plan. The delay in the commissioning of the project appeared after updating of the NDP.
| 343 | Byczyna (PL) |  | Upgrading of existing AC 220kV substation Byczyna. A new 400kV AC substation in Silesia Agglomeration Area with transformation 400/220kV 2x 500 MVA. New substation Byczyna is connected by splitting and extending existing line Tarnów - Tucznawa. | [10 empty] | planned | 2015 | The investment process ongoing according to plan
| 358 | Ostrów (PL) | Kromolice (PL) | Installation of a 2nd 400kV circuit along an already existing line on the same voltage. (1870 MVA, 212km). | [10 empty] | design & permitting | 2020 | The investment process ongoing according to plan
| 364 | Czarna (PL) | Polkowice (PL) | New line will be second 400kV circuit to existing line in the same direction. (1870 MVA, 22km). | [10 empty] | planned | 2020 | The investment process ongoing according to plan. The first out of 2 circuits will be operational starting with 2015.
| 365 | Wyszków (PL) |  | New substation 400kV Wyszków (with transformation 400/110kV 400 MVA) will be connected by splitting and extending line Ostrołęka-Stanisławów. | [10 empty] | design & permitting | 2025 | The investment delayed because of spacial planning problems.
| 203 | Area Wolmirstedt(DE) | under consideration | Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | under consideration | 2020 | Included in new investment H3 due to new wind BS generation
| 180 | Mengede (DE) | Kruckel (DE) | Installation of a second circuit 380kV OHL and extension of existing substations. Line length:16km. | [10 empty] | design & permitting | mid term | project develops according to the plan
| 217 | Dürnrohr (AT) | Sarasdorf (AT) | Installation of the 3rd and 4th circuit on the existing line Dürnrohr - Sarasdorf and restructuring in the area of the substation Bisamberg and the 220kV-Weinviertel-line . Total length: 100km. | [10 empty] | under construction | 2014 | The project is on schedule. Permissions are obtained. Commissioning is expected for 2014
| 169 | Großgartach (DE) |  | Upgrade the substation for a higher short circuit capacity. New installation includes 10 gas insulated bays, 63 kA, 3 bus-bar and 2 transformers. | [10 empty] | commissioned | commissioned | Commissioned
| 201 | Bärwalde (DE) | Schmölln (DE) | New internal double circuit 380kV-line connecting the substations St. Peter and Salzach new (replacement of the existing 220kV-line). Length: 46km. | [10 empty] | design & permitting | 2014 | Delays due to authorization process.
| 196 | wind farm Baltic 1 (DE) | Bentwisch (DE) | Connection of the offshore wind farm Baltic 1 (AC-cables on transmission voltage level). | [10 empty] | commissioned | commissioned | Commissioned
| 210 | Substations in 5 Hertz Transmission control area |  | Construction of new 380/110kV substations. | [10 empty] | commissioned | commissioned | Freiberg and Stendal/West are commissioned. The remaining substations were transferred to the 44. 209 investment.
| 213 | Wien SO (AT) | Szombathely (HU) | Installation of the 2nd circuit on the existing interconnection from Wien SO (AT, APG) to the border (both circuits have already been installed on the Hungarian side, one is connected to Györ and the 2nd circuit to Szombathely). Line length: 63km. | [10 empty] | commissioned | commissioned | 2011->2010: Completed earlier. It was due to scheduling of the field work.
| 215 | St. Peter (AT) | Salzach neu (AT) | New internal double circuit 380kV-line connecting the substations St. Peter and Salzach neu (replacement of the existing 220kV-line). Length: 46km. | [10 empty] | commissioned | commissioned | Commissioned
| 226 | Ernestinovo (HR) | Pecs (HU) | New 400kV double circuit interconnection line between existing stations. Line length: 86km. | [10 empty] | commissioned | commissioned | Commissioned
| 277 | Heviz (HU) | Szombathely (HU) | New 400kV transmission line between existing stations. Line length: 78km. | [10 empty] | commissioned | commissioned | Commissioned
| 278 | Gyor / Liter (HU) | Gonyu (HU) | New substation Gonyu (generator connection point) is connected by splitting and extending existing line Gyor-Liter. | [10 empty] | commissioned | commissioned | Commissioned
| 295 | Lemešany (SK) | Moldava (SK) | New 31km double circuit 400kV line, replacing a 220 kV one. The part of the line from Moldava substation up to switching substation Košice was put into operation in 10/2009. | [10 empty] | commissioned | commissioned | Commissioned 2011
| 300 | Chotejovice (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA . | [10 empty] | commissioned | commissioned | Commissioned
| 301 | Vyskov (CZ) | Chotejovice (CZ) | New single circuit 400kV OHL; 1385 MVA. | [10 empty] | commissioned | commissioned | Commissioned
| 305 | Kletne (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA . | [10 empty] | commissioned | commissioned | Commissioned
| 280 | Gyor / Martonvasar (HU) | Bicske (HU) | New substation Bicske with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Gyor-Martonvasar line. | [10 empty] | commissioned | commissioned | 2012->2010: Completed earlier. It was due to financing and field organization issues.
| 283 | Albertirsa / Bekescsaba (HU) | Szolnok (HU) | New substation Szolnok with 2*250 MVA 400/120kV transformers is connected by splitting and extending existing line Albertirsa-Bekescsaba. | [10 empty] | commissioned | commissioned | 2012->2011: Earlier completion due to scheduling of the field work.
| 281 | Albertirsa (HU) | Martonvasar (HU) | Adding second circuit to existing 400kV single circuit OHL. Line length: 45km. | [10 empty] | commissioned | commissioned | Commissioned earlier due to scheduling of the field work.
| 339 | Morzyczyn (PL) |  | A new AC substation in Szczecin Agglomeration Area with transformation 400/220kV 330 MVA and 400/110kV 330 MVA. New substation Morzyczyn is connected by splitting and extending existing 400kV line Krajnik - Dunowo. | [10 empty] | commissioned | commissioned | Commissioned -In the previous NDPs of PL the proejcts were structure in steps of 5 years. Therefore the date of commissioning mentioned din Tend 2010 is 2015. The project was commissioned in 2011.
| 345 | Łagisza (PL) |  | A new AC 400kV switchgear in existing substation Łagisza (with transformation 400/220kV 500 MVA and 400/110kV 330 MVA) is connected by splitting and extending of existing 400kV lines Rokitnica - Tucznawa. | [10 empty] | commissioned | commissioned | Commissioned -In the previous NDPs of PL the proejcts were structure in steps of 5 years. Therefore the date of commissioning mentioned din Tend 2010 is 2015.The project was commissioned in 2011.
| 347 | Gdańsk I (PL) |  | A new AC 400kV switchgear in existing substation Gdańsk I is connected by splitting and extending of existing 400kV lines Żarnowiec - Gdańsk Błonia. | [10 empty] | commissioned | commissioned | Commissioned -In the previous NDPs of PL the proejcts were structure in steps of 5 years. Therefore the date of commissioning mentioned din Tend 2010 is 2015.The project was commissioned in 2011.
| 67 | Divaca (SI) |  | Installation of a new 400kV PST to assist control of power flows to Italy on secure level and secure the operation of Slovenian grid enabling full utilization of regional market. | [10 empty] | commissioned | commissioned | This is PST in SS Divaca and it has been is in operation since 2011.
| A130 | Albertfalva (HU) |  | New 220/120kV 160MVA transformer. | [10 empty] | planned | 2020 | Appeared in National Plan 2010, transformer capacity extension on 220/120 kV is needed for maintaining SoS.
| A94 | Prosenice (CZ) | Kletne (CZ) | New connection between existing substation a new substation (see investment 299) | [10 empty] | under consideration | long term | New project
| A95 | Detmarovice (CZ) |  | New substation equipped with transformers 2x350MVA | [10 empty] | planned | long term | New project
| A73 | Żarnowiec (PL) |  | Extension and upgrade of an existing 110 kV switch gear and installation of 400/110 kV transformer dedicated to wind farms planned to be connected to Żarnowiec substation. Upgrade of existing 400 kV switchgear for transformer installation. | [10 empty] | planned | 2020 | The Żarnowiec substation is one of several substations in northern Poland incorporated in the project Wind Integration. The upgraded substation will serve as connection point for RES generation.
| A103 | Weinviertel-line New investment for the integration of RES (mainly wind power) in the north-eastern part of Austria (Weinviertel) |  | To allow the grid integration of the planned renewable energy generation (mainly wind power) in the north-eastern part of Austria ("Weinviertel") and to cover the foreseen load growth in that region the transmission grid infrastructure has to be enforced and new substations for the connection have to be erected | [10 empty] | planned | 2016/2017 | New project
| A145 | Tynec (CZ) | Cechy stred (CZ) | New second circuit to existing single circuit OHL, upgrade in length of 46.2km. Target capacity 2x1730MVA. | [10 empty] | planned | long term | New project | This investment item is a complementary to the project 56.Complication during permit granting process is foreseen. It is intended also to ask for EU financial support.
| A146 | Hradec (CZ) | Vyskov (CZ) | New second circuit to existing single circuit OHL, upgrade in length of 45.3km. Target capacity 2x1730MVA. | [10 empty] | planned | long term | New project | This investment item is a complementary to the project 35.Complication during permit granting process is foreseen. It is intended also to ask for EU financial support.
| A147 | Phase Shifting Transformer Hradec |  | Construction of new PST in substation Hradec with target capacity 2x1700MVA | [10 empty] | planned | mid term | New project | This investment item is a complementary to the project 35.Complication during permit granting process is foreseen. It is intended also to ask for EU financial support.
| A148 | Prosenice (CZ) | Krasikov (CZ) | New second circuit to existing single circuit OHL, upgrade in length of 87.5km. Target capacity 2x1730MVA. | [10 empty] | planned | long term | New project | This investment item is a part of the Eastern area close to Poland and Slovakia which involves projects that address both interregional connection/transmission and international transmission needs. Investment will also strengthen the grid in developing area and ensure security. of supply in this area. Complication during permit granting process is foreseen. It is intended also to ask for EU financial support.
| A149 | Nosovice (CZ) | Prosenice (CZ) | New second circuit to existing single circuit OHL, upgrade in length of 79.4km. Target capacity 2x1730MVA. | [10 empty] | planned | long term | New project | This investment item is a part of the Eastern area close to Poland and Slovakia which involves projects that address both interregional connection/transmission and international transmission needs. Investment will also strengthen the grid in developing area and ensure security. of supply in this area. Complication during permit granting process is foreseen. It is intended also to ask for EU financial support.
| A150 | Hradec (CZ) | Chrast (CZ) | New second circuit to existing single circuit OHL, upgrade in length of 82.4km. Target capacity 2x1730MVA. | [10 empty] | planned | long term | New project | This investment item is a complementary to the project 35.Complication during permit granting process is foreseen. It is intended also to ask for EU financial support.
| A151 | Prestice (CZ) | Chrast (CZ) | New second circuit to existing single circuit OHL, upgrade in length of 32.8km. Target capacity 2x1730MVA. | [10 empty] | planned | long term | New project | This investment item is a complementary to the project 35.Complication during permit granting process is foreseen. It is intended also to ask for EU financial support.

## NS report
5 July 2012
TYDNP 2012 package - Table of projects North Sea Regional Group Investment Plan
Project identification |  |  |  |  | Project assessment
Project number | Investment number | Substation 1 | Substation 2 | Brief technical description | Grid Transfer Capability Increase [MW] | Socio-economic Welfare | RES integration | Improved Security of Supply | Losses variation | CO2 mitigation | Technical resilience | Flexibility | Social and environmental Impact | Project costs | Present status | Expected date of commissioning | Evolution compared to the TYNDP 2010 situation | Investment comment | Project comment
5 | 5. 19 | Vic (ES) | Pierola (ES) | Upgrading (uprating) the existing 75km single circuit Vic-Pierola 400kV line in order to increase its capacity from 1360 MVA to 1710 MVA. | 1200-1400 in both directions | 1 | 2 | Perpignan, Gerona | [5 empty] | 2 | under construction | 2012 | Delays due to authorization process. |  | Mid-term interconnection project between France and Spain ("2.8 GW") . It includes cross border lines and internal lines required to assure NTC.
5 | 5. 20 | Arkale (ES) | Hernani (ES) | Upgrading the existing single circuit Arkale-Hernani n°2 220kV OHL in order to increase its capacity up to 640 MVA. | [10 empty] | design & permitting | 2014 | Delays due to authorization process. |  | 5
5 | 5. 36 | Sta.Llogaia (ES) | Baixas (FR) | New HVDC (VSC) bipolar interconnection in the Eastern part of the border, via 320kV DC underground cable using existing infrastructures corridors and converters in both ending points. | [10 empty] | partly under construction, design & permitting | 2014 | Progresses as planned. |  | 5
5 | 5. 37 | Santa Llogaia (ES) | Bescanó (ES) | New double circuit Sta.Llogaia-Ramis-Bescano-Vic/ Senmenat 400kV OHL (single circuit in some sections) New 400kV substations in Bescano, Ramis and Sta.Llogaia, with 400/220kV transformers in Ramis and Bescano. | [10 empty] | under construction | 2011-2013 | Bescano-Vic/Senmenat 400 KV commissioned. Difficulties in the authorization process of the section Bescano-Sta Llogaia 400kV |  | 5
5 | 5. 46 | Baixas (FR) | Gaudière (FR) | Reconductoring of existing 70km double circuit 400kV OHL to increase its capacity. | [10 empty] | design & permitting | end 2013 | Progresses as planned |  | 5
16 | 16. 38 | Gatica (ES) | Aquitaine (FR) | New HVDC interconnection in the western part of the border via DC subsea cable in the Biscay Gulf. | Fr->Es 1200 ; Es ->Fr 2000 | 1 | 2 | Biarritz, Basque country | [5 empty] | 3 | under consideration | ca. 2020 | New investment in TYNDP, defined since last release, aiming 4 GW capacity between France and Spain. |  | Long-term interconnection project between France and Spain ("4 GW") . It includes cross border lines and internal lines required to assure NTC.
16 | 16. A14 | Amorebieta (ES) Garraf (ES) Adrall (ES) Orcoyen (ES) | Gueñes (ES) Secuita (ES) La Pobla (ES) Elgea (ES) | Uprates required in basque country and Catalonia in order to use fully the benefit of the longterm ES-FR interconnection. | [10 empty] | under consideration | 2016 | New investment in TYNDP meant to solve congestion in this area. |  | 16
16 | 16. A17 | Arkale (ES) |  | New PST on Arkale-Argia 220 kV interconnection line | [10 empty] | design & permitting | 2016 | New investment enabling to take full advantage of the transfer capacity of the new subsea interconnection. |  | 16
17 | 17. 42 | Lonny (FR) | Vesle (FR) | Reconstruction of the existing 70km single circuit 400kV OHL as double circuit OHL. | 9000 | 1 | 2 | Reims, Paris area | [5 empty] | 3 | design & permitting | 2016 | Progresses as planned |  | Project needed to cope with larger and more volatile North South power flows from Normandy to Champagne, triggered especially by the development of new generation sources (along the Channel coasts, from Picardie to Champagne and further North abroad) that would naturally flow to large consumption areas: Paris area, but also more broadly from Brittany to Reims.
17 | 17. 44 | Havre (FR) | Rougemontier (FR) | Reconductoring of existing 54km double circuit 400kV OHL to increase its capacity. | [10 empty] | under construction | 2018 | As the pace of generation installation is lower than expected, the investment has been postponed. | This investment is needed for integrating new generation in Le Havre area. As the pace of generation installation is lower than assumed earlier, the investment has been postponed from 2015 to 2018 | 17
17 | 17. A18 | tbd (FR) | tbd (FR) | New network reinforcement between Haute Normandy and the south of Paris area. Length about 160 km. | [10 empty] | under consideration | long term | New investment in TYNDP, defined since last release | Either existing assets uprate or new HVDC, actual needs still being evaluated, depending on uncertainties on generation location | 17
17 | 17. 45 | Taute (FR) | Oudon (FR) | "Cotentin-Maine "Project : new 163km double circuit 400kV OHL connected to existing network via two new substations in Cotentin and Maine regions. | [10 empty] | under construction | 2013 | Delays due to authorization process. |  | 17
17 | 17. A144 | Cergy (FR) | Terrier (FR) | MORP project : new single circuit 400-kV line between existing 400-kV substations | [10 empty] | planned | 2018 | New investment in TYNDP, defined since last release, triggered by larger and more volatile power flows between generation developing North of Paris and Paris area. |  | 17
18 | 18. 48 | Gaudière (FR) | Rueyres (FR) | Reconductoring with ACCS limiting section (10km) of existing single circuit 400kV OHL. | >1000 | 3 | 5 | Provence area | [5 empty] | 3 | under construction | end 2012 | Progresses as planned |  | Larger and more volatile North South power flows in South-Western France, triggered by the development of local RES generation but also influenced by transits flows with neighboring countries.
18 | 18. A19 | tbd (FR) | tbd (FR) | Restructuration of whole EHV grid in Massif Central area | [10 empty] | under consideration | long term | New investment in TYNDP, defined since last release, triggered by larger and more volatile power flows in South West France. |  | 18
18 | 18. 20. A20 | (Provence) (FR) | (Midi) (FR) | New subsea HVDC link between Marseille area and Languedoc | [10 empty] | design & permitting | 2018 | New investment in TYNDP, defined since last release, triggered by larger and more volatile power flows in South West France. |  | 18
19 | 19. 51 | Boutre (FR) | La Bocca (FR) | PACA "Filet de sécurité" project: construction of 3 new AC 220kV underground cables (Boutre - Trans [65 km], Biançon - Fréjus [26 km] & Biançon - La Bocca [17 km]) and installation of reactive power compensation devices in 220 kV Boutre and Trans substations | 500 | 2 | 5 | French riviera | [5 empty] | 1 | design & permitting | 2015 | Progresses as planned |  | Security of supply of the French riviera
20 | 20. 53 | Coulange (FR) | Le Chaffard (FR) | Reconductoring (with ACCS / ACCR) of two existing double circuit 400kV OHL (Coulange - Pivoz-Cordier - Le Chaffard and Coulange - Beaumont-Monteux - Le Chaffard). Total length of both lines: 275km | 2400 | 1 | 5 | South East France | [5 empty] | 2 | under construction | 2016 | Progresses as planned | Construction over 4 years because the works are only possible during limited periods every years on this strategic corridor | The project aims at ensuring the reliable grid operation to cope with new generation development along the Rhone Valley and more volatile power flows between the Alps and South Western France.
20 | 20. 18, A20 | [15 empty] | 0 | The investment contributes both to project 18 and project 20. For the technical description see project 18 | 20
21 | 21. 54 | Cornier (FR) | Piossasco (IT) | Replacement of conductors (by ACCS) on Albertville (FR) - Montagny (FR) - Cornier (FR) and Albertville (FR) - La Coche (FR) - La Praz (FR) - Villarodin (FR) - Venaus (IT) - Piossasco (IT) single circuit 400kV OHLs. In addition, change of conductors and operation at 400kV of an existing single circuit OHL between Grande Ile and Albertville (FR) currently operated at lower voltage, and associated works in Albertville (FR) 400kV substation. (Total length of lines : 257 km) | 1800 from FR to IT, (600 in the MT) | 1 | 5 | [6 empty] | 3 | under construction | 2012/2013 | Mainly progresses as planned although the works on existing lines take slightly longer than initially thought |  | Planned France-Italy interconnection development
21 | 21. 55 | Grande Ile (FR) | Piossasco (IT) | "Savoie - Piémont" Project : New 190km HVDC (VSC) interconnection FR-IT via underground cable and converter stations at both ends (two poles, each of them with 600MW capacity). The cables will be laid in the security gallery of the Frejus motorway tunnel and possibly also along the existing motorways' right-of-way. | [10 empty] | design & permitting | 2017/2018 | Progresses as planned |  | 21
21 | 21. 81 | Trino (IT) | Lacchiarella (IT) | A new 380kV double circuit OHL between the existing 380kV substations of Trino and Lacchiarella in North West Italy area. Total line length: 95km, Voltage upgrade of the existing Magenta 220/132kV substation up to 380kV. | [10 empty] | under construction | 2013 | Authorization process ended, construction phase on going |  | 21
21 | 21. 84 | Casanova (IT) | Vignole (IT) | Voltage upgrade of the existing 100km Casanova-Vignole 220kV OHL to 400kV and new 400/220/150kV substation in Asti area. | [10 empty] | design & permitting | long term | Delays due to authorization process. |  | 21
21 | 21. 101 | Turin (IT) |  | Restructuring of the 220kV network in the urban area of Turin. Some new 220kV cables, some new 220/132kV substations and some reinforcements of existing assets are planned. Total length: 63km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 21
22 | 22. 57 | under consideration (FR) | under consideration (CH) | Reinforcement of the interconnection in the area of Geneva's lake. | < 1000 from FR to CH and < 1500 from CH to FR | 3 | 2 | [6 empty] | 1 | under consideration | long term | Progresses as planned. Several technical options (route, technologies) have been designed and are being investigated. | The very uncertain environment, regarding commissioning and decommissioning of generation in particular makes the assessment complex. | France-Switzerland interconnection development under consideration.
23 | 23. 60 | under consideration (FR) | under consideration (BE) | To be determined. | 1800-3000 | 3 | 2 | Lille, Ruien area | [5 empty] | 2 | under consideration | 2018-2020 | Project entered a feasibility study phase. Expected date of commissioning is now 2018. |  | France-Belgium interconnection development: internal French grid reinforcements, that are prerequisite to maintain the present NTC and further interconnection development under consideration. This project enhances security of supply in Belgium and allows intra and inter countries RES integration.
23 | 23. A21 | Avelin (FR) | Mastaing (FR) | Operation at 400 kV of existing line currently operated at 220 kV | [10 empty] | design & permitting | 2017 | New investment in the TYNDP | Upgrade of all grid assets in Northern France at the same standard | 23
23 | 23. A22 | Avelin (FR) | Gavrelle (FR) | Substitution of a new double-circuit 400kV OHL to an existing 400-kV single circuit OHL | [10 empty] | design & permitting | 2017 | New investment in the TYNDP |  | 23
24 | 24. 60a | Lillo (BE) | Mercator (BE) | Brabo Project : Doubling of the axis Zandvliet-Mercator via Lillo. First part : erecting a new 22km double circuit 380kV OHL with 1500 MVA capacity Lillo and Mercator. | 1500 | 2 | 2 | Antwerp area | [5 empty] | 2 | design & permitting | 2017 | New date of operation advanced to 2017 due to new generation projects. | Brabo Project | The project aims at ensuring the reliable grid operation to cope with new generation development in the northern part of Belgium and more volatile north south flows. It also enhances the security of supply in Antwerp harbor.
24 | 24. 445 | Zandvliet (BE) | Lillo (BE) | Brabo Project : Doubling of the axis Zandvliet-Mercator via Lillo. Second part : erecting a new 22km double circuit 380kV OHL with 1500 MVA capacity Lillo and Zandvliet and a new 400 kV substation in Lillo. | [10 empty] | design & permitting | 2017 | Permits cancelled by national authority . New permitting procedure has started | Brabo Project | 24
24 | 24. 445a | Gramme (BE) | Van Eyck (BE) | Doubling of 108km 380kV axis Gramme-Van Eyck + high performance conductors + new 380 kV substation (Van Eyck) | [10 empty] | design & permitting | 2014 | Permitting phase has started |  | 24
24 | 24. A26 | Horta (BE) | Doel/Mercator (BE) | Upgrade with high performance conductors. | [10 empty] | design & permitting | 2016-2020 | New investment in the TYNDP (The grid simulations performed by Regional Group North Sea showed higher North-South physical flows on northern Belgian boundary. This project avoid a NTC reduction due to higher loop flows.) |  | 24
24 | 24. A27 | Zandvliet (BE) |  | New PST in Zandvliet substation | [10 empty] | planned | 2016-2020 | New investment in the TYNDP (The grid simulations performed by Regional Group North Sea showed higher North-South physical flows on northern Belgian boundary. This project avoid a NTC reduction due to higher loop flows) | 4th PST on the Belgian north border. | 24
25 | 25. 62 | Under Consideration (FR) | Under Consideration (GB) | IFA2:New subsea HVDC link between the UK and France. Capacity is still to be determined. (Possibly 1000MW) | 1000 | 1 | 5 | [6 empty] | 2 | under consideration | 2020 | Further investigations during the feasibility phase have led to reassess the expected commissioning date for "IFA2" |  | France-UK interconnection development under consideration
35 | 35. 137 | Vitkov (CZ) | Mechlenreuth (DE) | New 400kV single circuit tie-line between new (CZ) substation and existing (DE) substation. Length: 70km. | 500 | 5 | 4 | [6 empty] | 3 | under consideration | long term | Progresses as planned |  | This project is required to enable power flows between West and East, enhance the transfer capability between CZ and DE and supports the future generation evacuation.
35 | 35. 138 | tbd (CZ) | tbd (DE) - South-Eastern part of 5 Hertz Transmission control area (Röhrsdorf) | Possible increase of interconnection capacity between CEPS and 50Hertz Transmission is under consideration: either a new 400kV tie-line (OHL on new route) or a reinforcement of the existing 400kV tie-line Hradec (CEPS) – Röhrsdorf (50Hertz Transmission). | [10 empty] | under consideration | long term | Progresses as planned |  | 35
35 | 35. 306 | Vitkov (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA. | [10 empty] | planned | 2017/2018 | It is closely dependent on construction of line investment n°308 |  | 35
35 | 35. 307 | Vernerov (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA. | [10 empty] | planned | 2013/2016 | Commissioning date has been divided into two phases (1. phase - temporary connection of wind plant 180MW, 2. phase finalization of substation construction including connection to the distribution grid (consumption) |  | 35
35 | 35. 308 | Vernerov (CZ) | Vitkov (CZ) | New 400kV double circuit OHL, 1385 MVA. | [10 empty] | planned | long term | Permitting procedure complications are foreseen (line crosses protected area) |  | 35
35 | 35. 309 | Vitkov (CZ) | Prestice (CZ) | New 400kV double circuit OHL, 1385 MVA. | [10 empty] | under consideration | long term | Permitting procedure complications are foreseen (line crosses protected area) |  | 35
35 | 35. 311 | Kocin (CZ) |  | Upgrade of the existing substation 400/110kV; upgrade transformers 2x350MVA. | [10 empty] | design & permitting | long term | Schedule harmonization with market participants |  | 35
35 | 35. 312 | Mirovka (CZ) |  | Upgrade of the existing substation 400/110kV with two transformers 2x250MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 313 | Kocin (CZ) | Mirovka (CZ) | Connection of 2 existing 400kV substations with double circuit OHL having 120.5km length: and a capacity of 2X1385 MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 314 | Mirovka (CZ) | V413 (CZ) | New double circuit OHL with a capacity of 2x1385 MVA and 26.5km length. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 315 | Kocin (CZ) | Prestice (CZ) | Adding second circuit to existing single circuit line OHL upgrade in length of 115.8km. Target capacity 2x1385 MVA. | [10 empty] | planned | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 316 | Mirovka (CZ) | Cebin (CZ) | Adding second circuit to existing single circuit line (88.5km, 2x1385 MVA). | [10 empty] | under consideration | long term | Schedule harmonization decided with market participants |  | 35
35 | 35. 317 | Hradec (CZ) | Reporyje (CZ) | Upgrade of existing 400kV single circuit OHL with length of 116.9km. Target capacity 1385 MVA. | [10 empty] | commissioned | commissioned | Commissioned |  | 35
36 | 36. 141 | Ishøj/Bjæverskov (DK) | Bentwisch/Güstrow (DE) | The Kriegers Flak Combined Grid Solution is the new offshore multiterminal connection between Denmark and Germany used for both grid connection of offshore wind farms Kriegers Flak and interconnection. Technical features still have to be determined. | 600 | 5 | 3 | [6 empty] | 1 | planned | long term | Permission for Danish Wind Farm KF 3 is in pending. Connection to Sweden is withdrawn at present, but can come on a later stage. |  | The Kriegers Flak Combined Grid Solution is the new offshore multiterminal connection between Denmark and Germany used for both grid connection of offshore wind farms Kriegers Flak and interconnection.
37 | 37. 142 | Tonstad (NO) | Wilster (DE) | Nord.Link/NorGer: a new HVDC connection between Southern Norway and Northern Germany. Estimated subsea cable length: 520 - 600km. Capacity: 1000 MW. | up to 1400 | 1 | 4 | [6 empty] | 3 | design & permitting | 2018/2021 | Revised capacity and progress postponed, due to more demanding system operations and time needed to obtain necessary government permits for reinforcing the national grid. |  | The purpose is: Market integration with the continent and facilitating RES integration in southern and western Norway. Will also improve security of supply in southern Norway.
| 37. 408 | Kristiansand, Feda (NO) |  | Reactive compensation due to HVDC links NorNed and Skagerak 4. Reactive power devices in 400kV substations. | [10 empty] | design & permitting | 2012/2014 | Feda is in the planning and permitting stage. Kristiansand is under construction(commissioned expected as planned 2012)
37 | 37. 406 | (Southern part of Norway) (NO) |  | Voltage uprating of existing 300 kV line Sauda/Saurdal - Lyse - Tonstad - Feda - 1&2, Feda - Kristiansand; Sauda-Samnanger in long term. Voltage upgrading of existing single circuit 400kV OHL Tonstad-Solhom-Arendal. Reactive power devices in 400kV substations. | [10 empty] | design & permitting | 2016 (2013-2018) | Revised progress. Due to more demanding system operations and time needed to obtain necessary government permits for reinforcing the national grid. The investment now embed former TYNDP 2010's investments 407 and 409 and the technical description has been updated accordingly. |  | 37
38 | 38. 425 | Feda (NO) | tbd (NL) | NorNed 2: a second HVDC connection between Norway and The Netherlands via 570km 450kV DC subsea cable with 700 - 1400MW capacity. | 700 | 5 | 2 | [6 empty] | 2 | under consideration | Long term | NorNed 2 is now not likely be realised during this planning period but is included in the TYNDP calculations and therefore on the project list. NorNed 2 is not included in the current Norwegian national grid development plan. |  | Additional interconnection between NO and NL under consideration
39 | 39. 428 | Kassø (DK) | Tjele (DK) | Rebuilding of a 400kV OHL of 173km from a single-circuit to a double-circuit . This increases the transfer capacity with approx. 1000 MW. | 1000-1550 | 1 | 2 | [6 empty] | 2 | design & permitting | 2012/2014 | Progresses as planned |  | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity.
39 | 39. 144 | Audorf (DE) | Kassö (DK) | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity. It consists of partially an upgrade of existing 400kV line and partially a new 400kV route in Denmark. In Germany new 400kV line mainly in the trace of a existing 220kV line. The total length of this OHL is 114km. | [10 empty] | under consideration | 2017 | Progresses as planned |  | 39
40 | 40. 446 | Bascharage (LU) | Aubange (BE) | As a first step(2016) a PST could be placed in the existing 225kV line between LU and BE. In a second stage, two solutions are currently investigated (4 TSOs - Elia, Amprion, CREOS, RTE are involved). Solutions 1 would be a new interconnection between Creos grid in LU and ELIA grid in BE via a 16km double circuit 225kV underground cable with a capacity of 1000 MVA. Solution 2 would be the interconnection between CREOS grid in LU and ELIA grid in BE via a new 380 kV double circuit. The current study will investigate the impact of this new interconnection on other boundaries (impact of loop flow) and on internal grids . The potential reinforcements of the other boundaries and the internal grids will also be taken into account in the evaluation. | 380-900 | 2 | 5 | Luxemburg area | [5 empty] | 2 | under consideration | 2016/2020 | The commissioning date and status changed as the study to determine the best investment is still ongoing. |  | Increase the transfer capability between LU,DE, BE and FR.
40 | 40. A29 | Bascharage (LU) | tbd (BE, DE, &/o FR) | New interconnection with neighbor(s) either 220kV or 400kV | [10 empty] | under consideration | 2020 | New investment in TYNDP | An ongoing network study (4 TSOs involved) investigates the robustness of the planned 220kV connection between LU and BE and the potentially need for an upgrading to a 400kV interconnector in the South. | 40
40 | 40. 447 | Heisdorf (LU) | Berchem (LU) | New 20km double-circuit mixed (underground cable+OHL) 225kV project with 1000 MVA capacity including substations for in feed in lower voltage levels. | [10 empty] | design & permitting | 2012/2017 | Progresses as planned |  | 40
40 | 40. A30 | Bascharage (LU) | Niederstedem (DE) or tbd (DE) | Upgrading and new construction of an interconnector to DE, in conjunction with the interconnector in the south of LU; Partial upgrading of existing 220kV lines and partial new construction of lines; With power transformer station in LU | [10 empty] | under consideration | 2020 | New investment in TYNDP |  | 40
41 | 41. 149 | Dollern (DE) | Stade (DE) | New 400kV double circuit OHL Dollern - Stade including new 400kV switchgear in Stade. Length:14km. | >3000 | 4 | 5 | [6 empty] | 1 | design & permitting | mid term | This investment depends on the commissioning of a conventional power plant in the area. The additional reason for delay is the long permitting procedure associated with this investment. |  | Evacuation of the new conventional generation in the 50Hz and TenneT area.
41 | 41. 150 | Conneforde (DE) | Maade (DE) | New 400kV double circuit ( underground cable+OHL) Conneforde - Maade including new 400kV switchgear Maade. Length: 37km. | [10 empty] | design & permitting | long term | Progresses as planned |  | 41
41 | 41. A74 | North of Control Area 5 HzT (DE) |  | Construction of new substations/lines for integration of newly build power plants in northern part of 50HzT control area. | [10 empty] | planned | long term | New investment in TYNDP, because of additional need for generation evacuation. Some of the investments are to be commissioned by the mid term and the some by long term. | Support of conventional generation integration in North-Eastern Germany, maintaining of security of supply and support of market development. | 41
42 | 42. 152 | Dörpen/West (DE) |  | New substation for connection of offshore wind farms. | >8000 | 4 | 1 | [6 empty] | 3 | under construction | mid term | Progresses as planned | Commercially sensitive information about this new wind-farm connection cannot be displayed in the TYNDP report | Integration of the offshore wind parks and the onshore grid reinforcements in the Northern DE.
42 | 42. 159 | Cluster BorWin1 (DE) | Diele (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 205km. Line capacity: 400MW. | [10 empty] | under construction | mid term | The commission date of this wind farms connection should be in 2012. Energy transportation is however already enable | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 160 | Offshore- Wind park Nordergründe (DE) | Inhausen (DE) | New AC-cable connection with a total length of 35km. | [10 empty] | design & permitting | mid term | Progresses depend on development of the off shore wind farm |  | 42
42 | 42. 161 | Offshore- Wind park GEOFreE (DE) | Göhl (DE) | New AC-cable connection with a total length of 32km. | [10 empty] | design & permitting | mid term | Progresses depend on development of the off shore wind farm |  | 42
42 | 42. 163 | Cluster HelWin1 (DE) | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 145km. Line capacity: aprox. 690MW. This Project includes also a new substation Büttel and connection of this new substation with the existing OHL Brünsbüttel - Wilster. | [10 empty] | under construction | mid term | Progresses with delay. | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 164 | Cluster SylWin1 (DE) | Büttel (DE) | New line consisting of underground +subsea cable with a total length of 210km. Line capacity: aprox.864MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 165 | Cluster DolWin1 (DE) | Dörpen/West (DE) | New line consisting of underground +subsea cable with a total length of 155km. Line capacity: 800MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 166 | Offshore Wind park Riffgat (DE) | Emden /Borßum(DE) | New AC-cable connection with a total length of 80km. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. 167 | Cluster BorWin2 (DE) | Diele (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 205km. Line capacity: 800MW. | [10 empty] | under construction | mid term | Progresses as planned | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A82 | Cluster DolWin2 (DE) | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 160 km. Line capacity: 900 MW | [10 empty] | under construction | mid term | New investment in TYNDP, for connection of new off-shore wind-farms | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A83 | Cluster DolWin3 (DE) | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 160 km. Line capacity: 900 MW | [10 empty] | design & permitting | mid term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A84 | Cluster BorWin3 | Dörpen/West (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 180 km. Line capacity: 900 MW | [10 empty] | design & permitting | mid term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A85 | Cluster HelWin2 | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 145km. Line capacity: 690 MW | [10 empty] | under construction | mid term | New investment in TYNDP, for connection of new off-shore wind-farms | Due to nondisclosure agreements it is not possible to give further information about this wind farm connection in TYNDP | 42
42 | 42. A86 | Cluster BorWin4 (DE) | Emden/Ost (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 185 km. Line capacity: 900 MW | [10 empty] | under consideration | long term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. A87 | Cluster SylWin2 (DE) | Büttel (DE) | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 210km. Line capacity: 800 MW | [10 empty] | under consideration | long term | New investment in TYNDP, for connection of new off-shore wind-farms |  | 42
42 | 42. 211 | Further connections of more offshore wind farms (DE) |  | Further connections in the clusters BorWin, DolWin, SylWin and HelWin. | [10 empty] | under consideration | long term | Progresses depend on development of the off shore wind farm |  | 42
43 | 43. A81 | Osterath (DE) | Philippsburg (DE) | New HVDC-lines from Osterath to Philippsburg to integrate new wind generation especially from North/ Baltic Sea towards Central-South Germany for consumption and storage. | 10000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany |  | Combined DC and AC new infrastructure to accommodate the new RES generation, the associated flows from North to South and also secure the SOS in South Germany.
| 43. A152 | Emden (DE) | Osterath (DE) | New HVDC-lines from Endem to Osterath to integrate new wind generation especially from North/ Baltic Sea towards Central Germany for consumption and storage. | [10 empty] | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany
| 43. A153 | Wehrendorf (DE) | Urberach (DE) | New lines in HVDC technology from the region of Lower Saxony to North Baden-Württemberg to integrate new wind generation especially from North Sea towards Central-South Europe for consumption and storage. The investment is part of the transmission corridor Cloppenburg - North Baden-Württemberg. | [10 empty] | under consideration | long term | New investment in TYNDP, due to long distance RES integration; voltage stability of the grid; SOS in the South of Germany
| 43. A154 | Cloppenburg (DE) | Westerkappeln (DE) | New 400-kV double circuit OHL Cloppenburg-Westerkappel (75 km). The investment is part of the transmission corridor Cloppenburg - North Baden-Württemberg. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
43 | 43. A88 | Brunsbüttel (DE), Wilster (DE), Kaltenkirchen (DE) | Großgartach (DE), Goldshöfe (DE), Grafenrheinfeld (DE) | New DC-lines to integrate new wind generation from Northern Germany towards Southern Germany and Southern Europe for consumption and storage. | [10 empty] | under consideration | long term | New Investment. |  | 43
43 | 43. A75 | Lauchstadt (DE) | Meitingen (DE) | New DC- lines to integrate new wind generation from Baltic Sea towards Central/south Europe for consumption and storage. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits |  | 43
43 | 43. A89 | Area of Northern Lower Saxony (DE) |  | New lines for integration of on- and offshore Wind generation incl. 380-kV-lines Halbemond - Emden, Emden-Conneforde and Conneforde - Cloppenburg. Total length: 160 km | [10 empty] | under consideration | long term | New Investment. |  | 43
43 | 43. A90 | Area of Schleswig-Holstein (DE) |  | About 300 km new 380-kV-lines and around 24 new transformers for integration of onshore Wind in Schleswig-Holstein, incl. lines Brunsbüttel-Barlt-Heide-Husum-Niebüll-border of Denmark, Audorf-Kiel-Göhl-Siems-Lübeck-Kaltenkirchen and Kaltenkirchen-Itzehoe-Brunsbüttel | [10 empty] | under consideration | long term | New investment in TYNDP due to new wind generation projects. | The German West-coast line (Brunsbuettel – Niebuel) is planned to be connected to the Danish grid in the 400 kV substation Endrup. The distance from the German/Danish border is approx. 80 km. Bilateral technical/economical investigations are ongoing. Reinforcements in the Danish 400 kV grid are foreseen in order to facilitate the increased power exchange capacity on the Danish-German border. | 43
44 | 44. 147 | Dollern (DE) | Hamburg/Nord (DE) | New 400kV double circuit OHL Dollern - Hamburg/Nord including one new 400/230kV transformer in substation Hamburg/Nord and new 400kV switchgear Kummerfeld. Length:43km. | 5000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 | design & permitting | mid term | Delays due to authorization process. |  | This project helps accommodating the increasing flows coming mainly form RES in NW DE to SW DE and CH.
44 | 44. 148 | Audorf (DE) | Hamburg/Nord (DE) | New 400kV double circuit OHL Audorf - Hamburg/Nord including two new 400/230kV transformers in substation Audorf. Length: 65km. | [10 empty] | design & permitting | mid term | This investment was schedulted for 2015. Presently it is foreseen a delay of around 1 year due to permitting process. |  | 44
44 | 44. 151 | Wehrendorf (DE) | Ganderkesee (DE) | New line (length: ca. 95km), extension of existing and erection of substations, erection of 380/110kV-transformers. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 156 | Niederrhein (DE) | Dörpen/West (DE) | New 400kV double circuit OHL Dörpen - Niederrhein including extension of existing substations. Length: 167km. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 157 | Wahle (DE) | Mecklar (DE) | New 400kV double circuit OHL Wahle - Mecklar including two new substations. Length: 210km. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 90. 170 | Großgartach (DE) | Hüffenhardt (DE) | New 380kV OHL. Length: 23km. Included with the project : 1 new 380kV substation, 2 transformers. | [10 empty] | under construction | 2012 | Progresses as planned |  | 44
44 | 44. 171 | Hüffenhardt (DE) | Neurott (DE) | Upgrade of the line from 220kV to 380kV. Length: 11km. Included with the project : 1 new 380kV substation. | [10 empty] | planned | 2020 | Progresses as planned |  | 44
44 | 44. 90. 172 | Mühlhausen (DE) | Großgartach (DE) | Upgrading line from 220kV to 380kV. Length:-45km. | [10 empty] | design & permitting | 2014 | Progresses as planned |  | 44
44 | 44. 90. 173 | Hoheneck (DE) | Endersbach (DE) | Upgrading line from 220kV to 380kV. Length:20km. | [10 empty] | design & permitting | 2014 | Progresses as planned |  | 44
44 | 44. 174 | Bruchsal Kändelweg (DE) | Ubstadt (DE) | A new 380kV OHL. Length:6km. | [10 empty] | design & permitting | 2014 | Postponed from one year due to permitting procedures |  | 44
44 | 44.90. 176 | Daxlanden | Eichstetten | Upgrade of transmission capacity of existing 380 kV line (120 km) | [10 empty] | under consideration | 2020 | Progresses as planned |  | 44
44 | 44. 178 | Baden-Württemberg, Süden & Nordosten (DE) |  | Installation of 2x250 MVAr 380kV capacitance banks. | [10 empty] | under construction | 2014 | One more bank in addition. Two have already been installed. Projects realised earlier because the need for reactive power compensation became urgent. |  | 44
44 | 44. 179 | Rommerskirchen (DE) | Weißenthurm (DE) | New line, extension of existing and erection of substations, erection of 380/110kV-transformers. Total line length: 100km. | [10 empty] | under construction/design & permitting | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. 181 | Dauersberg (DE) | Limburg (DE) | New 380kV double circuit OHL, extension of existing of substations, Total line length: 20km. | [10 empty] | under construction/design & permitting | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. 182 | Kriftel (DE) | Obererlenbach (DE) | New 400 kV double circuit OHL Kriftel - Obererlebenbach in existing OHL corridor. Length: 11 km | [10 empty] | planned | mid term | Some parts are commissioned but the main elements of the investment are still in design and permitting due to delays in permitting process. |  | 44
44 | 44. A80 | Area of West Germany (DE) |  | Installation of several 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | under consideration | long term | New investment in TYNDP, because of additional needs for RES integration (combined with SoS) |  | 44
44 | 44. 183 | Wehrendorf (DE) |  | Installation of 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 184 | Bürstadt (DE) |  | Installation of 2 x 300 MVAr 380kV capacitance banks, extension of existing substations. | [10 empty] | design & permitting | mid term | Delays due to authorization process. |  | 44
44 | 44. 185 | Area of Muensterland and Westfalia (DE) |  | New lines and installation of additional circuits, extension of existing and erection of several 380/110kV-substations. Total length: ca. 110km. | [10 empty] | design & permitting | long term | Delays due to authorization process. |  | 44
44 | 44. 186 | Gütersloh (DE) | Bechterdissen (DE) | New lines and installation of additional circuits, extension of existing and erection of 380/110kV-substation. Total line length:27km. | [10 empty] | under construction | mid term | Delays due to authorization process. |  | 44
44 | 44. 187 | Area of West-Rhineland (DE) |  | New lines and installation of additional circuits, extension of existing and erection of several 380/110kV-substations. | [10 empty] | under construction | 2013 | Progresses as planned |  | 44
44 | 44. 188 | Kruckel (DE) | Dauersberg (DE) | New lines, extension of existing and erection of several 380/110kV-substations. Total line length: 130km. | [10 empty] | planned | long term | Progresses as planned |  | 44
44 | 44. A78 | Pkt. Metternich (DE) | Niederstedem (DE) | Construction of new 380kV double-circuit OHLs, decommissioning of existing old 220kV double-circuit OHLs, extension of existing and erection of several 380/110kV-substations. Length: 108km. | [10 empty] | planned | long term | New investment in TYNDP | RES integration/ Market integration especially east-west-direction | 44
44 | 44. A77 | Area of South-Wuerttemberg (DE) |  | Construction of new 380kV double-circuit OHLs, decommissioning of existing double-circuit OHLs, extension of existing 380-kV-substations. Length: ca. 60km. | [10 empty] | planned | long term | New investment in TYNDP | RES integration combined with pump storage in the alp region (market) / increasing of the NTC DE-CH/AT | 44
44 | 44. 190 | Saar-Pfalz-Region (DE) |  | New lines, extension of existing and erection of several 380/110kV-substations. Upgrade of an existing line from 220 to 380 kV | [10 empty] | planned | long term | Delays due to authorization process. | SoS (Neub. Frltg Fraulaut-Saarwellingen) combined with RES integration | 44
| 44. A155 | Conneforde (DE) | Unterweser (DE) | Upgrade of 230-kV-circuit Unterweser-Conneforde to 400kV , Line length: 32 km. | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A156 | Dollern (DE) | Elsfleht/West (DE) | New 400 kV line in existing OHL corridor Dollern - Elsfleht/West Length:100 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A157 | Dollern (DE) | Landesbergen (DE) | New 400 kV line in existing OHL corridor Dollern-Sottrum-Wechold-Landesbergen (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A158 | Hamm/Uentrop (DE) | Kruckel (DE) | Extension of existing line to a 400 kV single circuit OHL Hamm/Uentrop - Kruckel. Length: 60 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A159 | Pkt. Blatzheim (DE) | Oberzier (DE) | New 400 kV double circuit OHL Pkt. Blatzheim - Oberzier including extension of existing substations. Length 16 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A160 | Urberach (DE) | Daxlanden (DE) | New line and extension of existing line to 400 kV double circuit OHL Urberach - Pfungstadt - Weinheim - Daxlanden including extension of existing substations. Length: 219 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A161 | Bürstadt (DE) | Daxlanden (DE) | New line and extension of existing line to 400 kV double circuit OHL Bürstadt - Lambshein - Daxlanden including extension of existing substastions. Length: 134 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 44. A162 | Großgartach (DE) | Endersbach (DE) | Extension of existing 400-kV-line Großgartach - Endersbach. (Lenght: 32 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
44 | 44. 175 | Birkenfeld (DE) | Ötisheim (DE) | A new 380kV OHL. Length:11km. | [10 empty] | planned | 2020 | New investment in TYNDP |  | 44
44 | 44. 189 | Niederrhein (DE) | Utfort (DE) | New 400 kV double-circuit OHL Niederrhein-Utfort (24 km). | [10 empty] | under consideration | long term | New investment in TYNDP |  | 44
45 | 45. 90. 177 |  |  |  | 5000 | 1 | 2 | Bavaria and Baden-Wurtenbergh area | [5 empty] | 3 |  |  | 0 | The investment contributes both to project 45 and project 90. For the technical description see project 90. | This project helps accommodating the increasing flows coming mainly form RES in NE DE to South DE and to the Alps.
45 | 45. 191 | Neuenhagen (DE) | Vierraden (DE) | Project of new 380kV double-circuit OHL Neuenhagen-Vierraden-Bertikow with 125km length as prerequisite for the planned upgrading of the existing 220kV double-circuit interconnection Krajnik (PL) – Vierraden (DE Hertz Transmission). | [10 empty] | design & permitting | 2013/2015 | Project in permitting phase, strong local resistance |  | 45
45 | 45. 193 | Halle/Saale (DE) | Schweinfurt (DE) | New 380kV double-circuit OHL between the substations Vieselbach-Altenfeld-Redwitz with 215km length combined with upgrade between Redwitz and Grafenrheinfeld (see project 153). The Section Lauchstedt-Vieselbach has already been commissioned. Support of RES integration in Germany, annual redispatching cost reduction, maintaining of security of supply and support of the market development. The line crosses the former border between Eastern and Western Germany and is right downstream in the main load flow direction. The project will help to avoid loop flows through neighboring grids. | [10 empty] | design & permitting | mid term | Investment partly completed, strong local public resistance- delay due to permitting process |  | 45
45 | 45. 197 | Neuenhagen (DE) | Wustermark (DE) | Construction of new 380kV double-circuit OHL between the substations Wustermark-Neuenhagen with 75km length. Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | under construction | mid term | Investment partly under construction and partly in permitting phase. Expected date of commissioning was adjusted due to long permitting process and strong local public resistance. |  | 45
45 | 45. 199 | Western Pomerania (DE) | Uckermark North (DE) | Construction of new 380kV double-circuit OHLs in North-Eastern part of 50HzT control area and decommissioning of existing old 220kV double-circuit OHLs, incl. 380-kV-line Bertikow-Pasewalk (30 km). Length: 135km.Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015 | Progresses as planned |  | 45
45 | 45. 200 | Lubmin (DE) | Erfurt area (DE) | 380-kV-grid enhancement and structural change area Lubmin-Stralsund and area Magdeburg/Wolmirstedt, incl. 380-kV-line Güstrow-Wolmirsted (195 km) | [10 empty] | planned | long term | Progresses as planned |  | 45
45 | 45. 202 | Area upper Lausitz(DE) | Area Gera(DE) | Upgrading existing double-circuit 380kV OHL in the South-Eastern part of the control area of 50Hertz Transmission. Bärwalde-Schmölln length approx.. 50km. Support of RES and conventional generation integration in North-Eastern Germany, maintaining of security of supply and support of market development. | [10 empty] | design & permitting | 2017 | Progresses as planned |  | 45
45 | 45. 204 | Calbe (DE) |  | Construction of new 380kV double-circuit OHL in substation Calbe for double connection/loop into an existing line. | [10 empty] | planned | mid term / long term | The evolution of this investment depends on the development of the power plant in the area. The date mentioned in the TYNDP 2010 was a typing mistake. |  | 45
45 | 45. 205 | Fördertsedt (DE) | Area Magdeburg(DE) | Construction of new 380kV double-circuit OHL from the substation Förderstedt with 20 km length for double connection/loop in for Förderstedt; Reinforcement of existing switchgear, Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015/2020 | Progresses as planned |  | 45
45 | 45. 206 | Area Leipzig(DE) | Area Chemnitz(DE) | Construction of new double-circuit 380-kV-overhead line in existing corridor Röhrsdorf-Remptendorf (103 km) | [10 empty] | under consideration | 2020 | Progresses as planned |  | 45
45 | 45. 207 | Substations in South-Western part of 5 Hertz Transmission control area (DE) |  | Construction of new 380kV substation in Southern Magdeburg area and restructuring of existing 220kV equipment. total length: aprox .50 km | [10 empty] | planned | long term | Some of the investments are to be commissioned by the mid term and the some by long term. |  | 45
45 | 45. 208 | Lines and Substations in South-Western part of 5 Hertz Transmission control area (DE) |  | Construction of new 380kV double-circuit OHL in existing corridor Pulgar-Vieselbach (103 km) Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | planned | 2015/2020 | Progresses as planned |  | 45
45 | 45. 209 | Substations in 5 Hertz Transmission control area |  | Extension of existing and erection of new 380 kV-substations and several 380/110kV-substations, incl. reactive power compensation devices. | [10 empty] | design & permitting | mid term | This investment includes several substations in the control area of 50Hertz Transmission control area. Present status varies form design & permitting, planning to under consideration and the date of commissioning varies from short/mid to long term. |  | 45
| 45. A163 | Wolmirstedt (DE) | Wahle (DE) | New double circuit OHL 380 kV; Line length 111 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A164 | Vieselbach (DE) | Mecklar (DE) | New double circuit OHL 400 kV line in existing OHL corridor . (129 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A165 | Mecklar (DE) | Grafenrheinfeld (DE) | New double circuit OHL 400-kV-line (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A166 | Altenfeld (DE) | Grafenrheinfeld (DE) | New double circuit OHL 400-kV-line (130 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A169 | Grafenrheinfeld (DE) | Grossgartach (DE) | Additional 380 Kv circuit on a existing lines. Length: 160 km | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A167 | Redwitz (DE) | Schwandorf (DE) | New double circuit OHL 400 kV line in existing OHL corridor Redwitz-Mechlenreuth-Etzenricht-Schwandorf (185 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
| 45. A168 | Raitersaich (DE) | Isar (DE) | New 400 kV line in existing OHL corridor Raitersaich - Ludersheim - Sittling - Isar (160 km) | [10 empty] | under consideration | long term | New Investment due to increase of RES and changes in conventional power plants in Germany and increase transits
45 | 45. 153 | Redwitz (DE) | Grafenrheinfeld (DE) | Upgrade of 230kV connection Redwitz - Grafenrheinfeld to 400kV, including new 400kV switchgear Eltmann. Line length: 97km. | [10 empty] | design & permitting | mid term | Investment delay due to delay in the implementation of the line Halle-Schweinfurt(investment 45. 193) |  | 45
45 | 45. 154 | Redwitz (DE) |  | New 500 MVAr SVC in substation Redwitz. | [10 empty] | planned | mid term | Progresses as planned |  | 45
45 | 45. 155 | Raitersaich (DE) |  | New 500 MVAr SVC in substation Raitersaich. | [10 empty] | planned | mid term | Progresses as planned |  | 45
45 | 45. 47. 158 | [15 empty] | 0 | The investment contributes both to project 45 and project 47. For the technical description see project 47. | 45
46 | 46. 194 | wind farm cluster Baltic Sea East (DE) | Lüdershagen/ Lubmin (DE) | Offshore wind farm connection project (by AC-cables on transmission voltage level or by clustering with DC connections) has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. | >2000 | 4 | 1 | [6 empty] | 1 | design & permitting | 2012-2020 | This investment includes several connections of offshore wind farms in the eastern part of the Baltic Sea. The present expected date of commissioning varies from 2012 to 2020. |  | The integration of offshore wind generation in the Baltic Sea.
46 | 46. 195 | wind farm cluster Baltic Sea West (DE) | Bentwisch (DE) | Offshore wind farm connection project (by AC-cables on transmission voltage level or by clustering with DC connections) has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. | [10 empty] | design & permitting | 2013-2020 | This investment includes several connections of offshore wind farms in the western part of the Baltic Sea. The present expected date of commissioning varies from 2013 to 2020. |  | 46
47 | 47. A76 | Vöhringen / Leupolz (DE) | Westtirol (AT) | Upgrade of an existing OHL to 380 kV, extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. Transmissions routs Vöhringen - Westtirol and Pkt. Woringen - Memmingen. Length: 114 km. This project will increase the current power exchange capacity between the DE, AT and CH. | >2000 | 1 | 2 | [6 empty] | 3 | planned | long term | New investment in TYNDP |  | The reinforcement of the interconnection between Austria and Germany. Also the support the interaction between the RES in Northern Europe(mainly DE) with the pump storage in the Austrian Alps. The project scheduling is not related only to the network needs, but even to the feasibility and to the authorization process (the possibility to anticipate specific projects could be evaluated in the future considering the three above mentioned elements).
47 | 47. 158 | Irsching (DE) | Ottenhofen (DE) | Upgrade of 230kV connection Irsching - Ottenhofen to 400kV, including new 400kV switchgear Zolling. Length 76km. | [10 empty] | planned | mid term | Progresses as planned | The investment contributes also to project 45. | 47
47 | 47. 212 | Isar / Ottenhofen (DE) | St. Peter (AT) | New 400kV double circuit OHL Isar - St. Peter including new 400kV switchgears Altheim, Simbach and St. Peter, and one new 400/230kV transformer in substation Altheim and fourth circuit on line Isar - Ottenhofen. Line length: 90km. | [10 empty] | design & permitting | 2017 | Progresses as planned |  | 47
47 | 47. 26. 216 | St. Peter (AT) | Tauern (AT) | Completion of the 380kV-line St. Peter - Tauern. This contains an upgrade of the existing 380kV-line St. Peter - Salzburg from 220kV-operation to 380kV-operation and the erection of a new internal double circuit 380kV-line connecting the substations Salzburg and Tauern (replacement of existing 220kV-lines on optimized routes). Moreover the erection of the new substations Wagenham and Pongau and the integration of the substations Salzburg and Kaprun is planned. Line length: 130km. | [10 empty] | design & permitting | 2017/2019 | Preparation for the permitting procedure is ongoing. APG is making efforts to set the 380-kV-Salzburg-line 2017 into service. Depending on possible delays during the permitting procedure the commissioning is expected between 2017 and 2019 | The investment contributes also to project 26. | 47
47 | 47. 26. 218 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 47
47 | 47. 219 | Westtirol (AT) | Zell-Ziller (AT) | Upgrade of the existing 220kV-line Westtirol - Zell-Ziller and erection of additional 220/380kV-Transformers. Line length: 105km. | [10 empty] | partly under construction | 2013-2020 | Project consists of several measures and is on schedule |  | 47
47 | 47. 26. 220 | [15 empty] | 0 | The investment contributes both to project 26 and project 47. For the technical description see project 47. | 47
47 | 47. 221 | St. Peter (AT) | Ernsthofen (AT) | Upgrade from 220kV-operation to 380kV and erection of a 380kV-Substation in Ernsthofen and St. Peter. | [10 empty] | under construction | 2013 | The project is on schedule. Permissions are obtained. Commissioning is expected for 2013 |  | 47
58 | 58. 353 | Krajnik (PL) | Baczyna (PL) | Construction of a new double circuit 400kV OHL Krajnik - Baczyna (2x1870 MVA, 91km); single circuit temporarily working at 220kV on Krajnik - Gorzów part + New substation 400kV Baczyna will be connected by splitting and extending existing line Krajnik-Plewiska + Upgrading of limitations line Krajnik - Plewiska. | >1000 | 1 | 2 | [6 empty] | 2 | planned | 2020 | Progresses as planned |  | Bridge – third interconnection between Poland and Germany.
58 | 58. 355 | Mikułowa (PL) | Świebodzice (PL) | Double circuit line 220kV Mikułowa-Świebodzice will be upgraded to 400kV - single circuit temporarily working at 220kV. | [10 empty] | planned | 2020 | Progresses as planned |  | 58
58 | 58. A67 | Gubin (PL) |  | New 400 kV substation planned near the PL-DE border. The substation will be connected to planned line Eisenhüttenstadt (DE) - Plewiska (PL) creating new lines Eisenhüttenstadt (DE) - Gubin (PL) and Gubin (PL) - Plewiska (PL). | [10 empty] | planned | 2020 | New investment in TYNDP | This new substation on the third DE-PL connection is necessary for future generation connection while ensuring interconnection capability. | 58
58 | 58. 140 | Eisenhüttenstadt (DE) | Plewiska (PL) | New 400kV double circuit OHL Eisenhüttenstadt (DE) - Plewiska (PL) including the construction of new substation Plewiska Bis (PL) | [10 empty] | planned | 2020 | Progresses as planned |  | 58
67 | 67. 402 | Barkeryd (SE) Hallsberg (SE) | Tveiten (NO) Hurva (SE) | "South West link" consisting of three main parts: 1) New 400kV line between Hallsberg and Barkeryd (SE) 2) New double HVDC VSC underground cable and OHL between Barkeryd and Hurva (SE) 3) New double HVDC VSC line between Barkeryd (SE) and Tveiten (NO). The project also include new substations and converter stations in the connection points line double circuit new OHL Hallsberg - Barkeryd 170km, underground VSC Barkeryd - Hurva 250km and VSC Barkeryd - Tveiten with 103km on the Norwegian side. Expected capacity: 1200MW. | 1400 (E-W), 1200 (N-S) | 3 | 2 | [6 empty] | 3 | design & permitting | 2014-2019 | Commissioning date updated after bilateral negotiations between the two countries. Hallsberg-Barkeryd-Hurva expected in 2014; Barkeryd-Tveiten in 2019 |  | 5 investments of HVDC and AC lines in Sweden and Norway as well as between the countries, resulting in increased GTC and market integration
67 | 67. 411 | Rød (NO) | Sylling (NO) | Voltage upgrading of existing single circuit 300kV OHL Rød-Tveiten-Flesaker-Sylling in connection with the new HVDC line to Sweden, the Syd Vest link. | [10 empty] | design & permitting | 2018/2020 | Investment postponed, especially because of long permitting processes. |  | 67
67 | 67. 412 | Rød (NO) - Sylling (NO) - Flesaker (NO) - | Hasle (NO) Tegneby (NO) Tegneby (NO) | Reinvestment and capacity increase Oslofjord 400kV subsea cables. Three cables: Filtvedt - Brenntangen, Solberg - Brenntangen, and Teigen - Evje. | [10 empty] | design & permitting | 2015 | Investment delayed, especially because of long permitting processes. One cable is under construction. |  | 67
68 | 68. 421 | Ofoten (NO) | Balsfjord (NO) | New 160km single circuit 400kV OHL. | 350-1500 | 2 | 1 | Northern Norway | [5 empty] | 2 | design & permitting | 2016 | Investment delayed, especially because of long permitting processes. |  | The main purpose of this project is to secure the northern part of NO.
68 | 68. 422 | Balsfjord (NO) | Hammerfest (NO) | New 360 km single circuit 400kV OHL. | [10 empty] | design & permitting | 2018 | Investment delayed, especially because of long permitting processes.
68 | 68. 423 | Skaidi (NO) | Varangerbotn (NO) | New 230 km single circuit 400kV OHL. | [10 empty] | planned | 2022 | Investment postponed, especially because of long permitting processes.
69 | 69. 424j | Bramford (GB) | Twinstead (GB) | New 400kV double circuit | 2600 | 4 | 1 | [6 empty] | 2 | Design & Permitting | 2018/2019 | Delayed by one year to 2018/19 due to an anticipated slower growth in the uptake of wind. |  | This project supports the evacuation of energy from a new nuclear power plant and from the offshore wind parks of the Eastern coast of GB.
69 | 69. A39 | Sizewell C (GB) | Bramford (GB) | Reconductor Sizewell C-Bramford-Sizewell | 1800 | [9 empty] | Planned | 2015/16 | New investment in TYNDP, answering an expected growth in offshore wind and nuclear generation in and around Norfolk and East Anglia, above what was anticipated for the TYNDP 2010. |  | 69
69 | 69. A40 | Norwich Main (GB) | Bramford (GB) | Norfolk Offshore Wind: NORW-BRFO Tee-in to Lowestoft | [10 empty] | Planned | 2015/16 | New investment in TYNDP, answering an expected growth in offshore wind and nuclear generation in and around Norfolk and East Anglia, above what was anticipated for the TYNDP 2010. |  | 69
69 | 69. A41 | Walpole (GB) | Bramford (GB) | Reconductoring Norwich Main-Walpole and Bramford-Norwich Main | [10 empty] | Under Construction | 2015/2016 | New investment in TYNDP, answering an expected growth in offshore wind and nuclear generation in and around Norfolk and East Anglia, above what was anticipated for the TYNDP 2010. |  | 69
70 | 70. 405 | Kristiansand (NO) | Rød (NO) | Voltage upgrading of an existing single circuit 300kV OHL and a new section of OHL between Rød and Bamle. Total length: 175km. | 700 | 5 | 2 | [6 empty] | 2 | design & permitting | 2014 | Progresses as planned |  | Market integration and RES integration.
70 | 70. 426 | Kristiansand (NO) | Tjele (DK) | Skagerak 4: 4th HVDC connection between Southern Norway and Western Denmark, built in parallel with the existing 3 HVDC cables; new 700MW including 230km 500kV DC subsea cable. | [10 empty] | Under construction | 2014 | Progresses as planned |  | 70
71 | 71. 427 | Endrup (DK) | Eemshaven (NL) | COBRA: New single circuit HVDC connection between Jutland and the Netherlands via 350km subsea cable; the DC voltage will be up to 320kVand the capacity 600-700MW. | 700 | 5 | 2 | [6 empty] | 2 | design & permitting | 2016 | Progresses as planned |  | Cobra
72 | 72. 430 | Revsing (DK) | Landerupgård (DK) | New 18km single circuit 400kV line via cable with capacity of approx. 1200 MW. | 950 | 4 | 1 | DK west and north DE | [5 empty] | 2 | Planned | 2017 | Progresses as planned |  | The main purpose of the project is to integrate and transmit large scale wind power in DK west.
72 | 72. 435 | Endrup (DK) | Revsing(DK) | Upgrade of 50km double-circuit 400kV OHL to reach a capacity of approx. 2000MW. | [10 empty] | design & permitting | 2015 | Earlier date of commissioning than initially expected caused by reprioritization of project. Also one of the substations has been changed: Endrup was replaced by Tjele. |  | 72
72 | 72. 436 | Idomlund (DK) | Endrup (DK) | New 74km single circuit 400kV line via cable with capacity of approx. 1200MW. | [10 empty] | under consideration | 2018/2020 | Envisaged route changed from Idomlund-Tjele to Idomlund-Endrup |  | 72
73 | 73. 432 | Asvæsværket (DK) | Kyndbyværket (DK) | New 60km single circuit 400kV line via cable with capacity of approx. 1200 MW. | >1000 | 4 | 4 | [6 empty] | 1 | design & permitting | 2014 | Progresses as planned |  | The project will increase the stability of the DK eastern power system and allow for larger transmission and transit.
73 | 73. 433 | Glentegård (DK) | Amagerværket & H.C. Ørstedværket (DK) | New 22km single circuit 400kV line via cable with capacity of approx. 1200MW. | [10 empty] | planned | 2016 | Progresses as planned |  | 73
74 | 74. 443 | Richborough (GB) | Zeebrugge (BE) | Nemo Project: New DC sea link including 135km of 250kV DC subsea cable with 1000MW capacity | >1000 | 1 | 2 | Thames estuary | [5 empty] | 2 | Planned | 2018 | Investment delayed to 2018 due to authorization delays related to needed internal grid reinforcements | Nemo project | Interconnection between UK and the mainland Europe(BE).
74 | 74. 449 | Richborough (GB) | Canterbury (GB) | New 400kV double circuit OHL and new 400kV substation in Richborough | [10 empty] | Planned | 2019/2020 | Progresses as planned | The reinforcements shown here reflect initial options but are subject to consultation and review of other feasible options. | 74
74 | 74. 450 | Sellindge (GB) | Dungeness (GB) | Reconductor Sellindge-Dungeness | [10 empty] | Planned | 2014/2015 | The reconductoring of the Sellindge to Dungeness circuits (Project 450) remain as originally planned in the TYNDP 2010. |  | 74
75 | 75. 444 | Zomergem (BE) | Zeebrugge (BE) | New approx. 50km double-circuit 380kV ( 3000MVA for each circuit) between Zomergem and Zeebrugge to evacuate the locally (offshore) produced power line and allow connection of NEMO to 380 kV grid. | 1500 | 4 | 1 | [6 empty] | 2 | design & permitting | 2014 | Progresses as planned | Stevin project | The project allows the connection of 2,3 GW of offshore wind production. It also allows onshore RES connection. This project enhances security of supply of Belgian coastal area and allows the NEMO connection.
75 | 75. A28 | Zeebrugge (BE) | offshore platform (BE) | 2 offshore platforms connected to AC grid with underground cables including compensation | [10 empty] | planned | 2016 | New investment in TYNDP, resulting from recent studies demonstrating such a platform would be optimal for Belgian offshore wind off take. Planning and implementation of the project depends on the evolution of Belgian legislation. | Belgian offshore platform | 75
76 | 76. A42 | Pelham (GB) | Waltham Cross (GB) | Reconductor Pelham-Rye House-Waltham Cross | 7600 | 4 | 1 | London area | [5 empty] | 3 | Design & Permitting | 2015/2016 | New investment in TYNDP | New projects in the London area, not previously reported in the TYNDP 2010. All of these investments are required due to a combination of age related asset replacement, increasing power flows and changing customer demand connection requirements. A further driver for all of these projects is that power flows through London increase during interconnector export to mainland Europe (Power flows from the north through London to the interconnectors within the Thames Estuary). | All of these investments are required due to a combination of age related asset replacement, increasing power flows and changing customer demand connection requirements. A further driver for all of these projects is that power flows through London increase during interconnector export to mainland Europe (Power flows from the north through London to the interconnectors within the Thames Estuary).
76 | 76. A43 | Hackney (GB) | Waltham Cross (GB) | Uprate to 400kV Hackney-Tottenham-Waltham Cross | [10 empty] | Design & Permitting | 2015/2016 | New investment in TYNDP |  | 76
76 | 76. A44 | Hackney (GB) | St. John's Wood (GB) | New 400kV St. John's Wood-Hackney double circuit | [10 empty] | Design & Permitting | 2017/2018 | New investment in TYNDP |  | 76
76 | 76. A45 | Tilbury (GB) | Elstree (GB) | Uprate to 400kV Tilbury-Warley-Elstree | [10 empty] | Planned | 2021/22 | New investment in TYNDP |  | 76
76 | 76. A46 | St. John's Wood (GB) | Wimbledon (GB) | New 400kV St. John's Wood-Wimbledon cables | [10 empty] | Design & Permitting | 2017/2018 | New investment in TYNDP |  | 76
76 | 76. A47 | West Weybridge (GB) | Beddington (GB) | Uprate to 400kV West Weybridge-Chessington-Beddington | [10 empty] | Planned | 2017/2018 | New investment in TYNDP |  | 76
77 | 77. 452 | Deeside (GB) | Hunterston (GB) | New 2000MW HVDC Link via 360km 500kV DC subsea cable on the West Coast of the UK and new 400kV substation in Deeside | 4000 | 4 | 1 | [6 empty] | 3 | Design & Permitting | 2015/2016 | Progresses as planned (still targetting the financial year 2015/2016) |  | This project facilitates the connection of RES and the connection of the remote Scottish Islands.
77 | 77. 453 | Peterhead (GB) | Hawthorn Pit (GB) | New 2000MW HVDC Link via 365km 500kV DC subsea cable on the East Coast of the UK and new 400kV substation in Hawthorn Pit | [10 empty] | Planned | 2018/2019 | Progresses as planned (still targetting the financial year 2018/2019) |  | 77
77 | 77. 454 | Hawthorn Pit (GB) | Norton (GB) | Uprate to 400kV Hawthorn Pit-Norton | [10 empty] | Planned | 2018/2019 | Progresses as planned (still targetting the financial year 2018/2019) |  | 77
77 | 77. 456 | Harker (GB) | Quernmore (GB) | Reconductor Harker-Hutton-Quernmore | [10 empty] | Design & Permitting | 2014/2015 | Progresses as planned (still targetting the financial year 2014/2015) |  | 77
77 | 77. 449a | Gravir (GB) | Beauly (GB) | Western Isles link. New 450MW HVDC link, +/- 150kV. Route length 156km (80km subsea, 76km onshore underground cable). | [10 empty] | design & permitting | 2015 | The 2010 TYNDP showed commissioning scheduled for 2013. However the developers of the large Western Isles wind farm projects which drive the need for the link, have experienced commercial delays. Commissioning of the link is therefore now projected for 2015. |  | 77
77 | 77. 450a | Kergord and Caithness (GB) | Blackhillock (GB) | The Moray Firth HVDC development - Shetland and Caithness links with offshore HVDC hub. Three ended HVDC link, 2 x 600MW legs and common 1200MW leg. Total route length 395km. | [10 empty] | design & permitting | 2016 | Projected commissioning is now 2016. The 2010 TYNDP showed commissioning scheduled for 2014. At that time the concept was to include an offshore node in a subsea HVDC link that was planned from Shetland to the Scottish mainland. That link was being designed to connect the Viking Energy wind farm project on Shetland. The Shetland link was termed the Base Project and the node was referred to as Incremental Works. The node would receive a connection from Caithness in 2016 for the export of renewables from that region and would also offer the potential for connection of adjacent offshore wind farms. However, the Viking project suffered consenting delays, and so late in 2010 the Caithness to Moray HVDC link was re-designated as the Base Project into which the node would be incorporated. The achievable timetable for the Caithness leg with commissioning in 2016 then became the timetable for the investment. |  | 77
77 | 77. 451a | Dounreay (GB) | Beauly (GB) | String a second 275kV OHL circuit on existing towers. | [10 empty] | under construction | 2012 | Progresses as planned |  | 77
77 | 77. 452a | Beauly (GB) | Kintore (GB) | Reconductor existing 275kV overhead line route. | [10 empty] | design & permitting | 2014 | Progresses as planned (still targetting the financial year 2014/2015) |  | 77
77 | 77. 453a | Blackhillock (GB) | Kincardine (GB) | Reinsulate existing 275kV route for 400kV operation and establish three new 400kV substations en-route. | [10 empty] | design & permitting | 2016 | Scheduled completion in 2016 is one year later than foreseen in the 2010 TYNDP. The north of Scotland transmission system is significantly depleted by construction outages to accommodate the main Beauly-Denny rebuild by 2014. The system access that is available for this investment (453a) to accommodate a build-up of renewable generation leads to the revised completion date in 2016. |  | 77
77 | 77. 455 | Beauly (GB) | Denny (GB) | New double circuit 400kV OHL (220km) with new terminal substations and substation extensions en route. | [10 empty] | under construction | 2014 | Progresses as planned |  | 77
77 | 77. 457 | Harker (GB) | Stella West (GB) | New 400kV series and shunt compensation at a number of locations across the Anglo-Scottish border. | [10 empty] | design & permitting | 2014/2015 | Progresses as planned |  | 77
78 | 78. 458 | Hinkley (GB) | Seabank (GB) | New 60km double circuit 400kV OHL | 3200 | 4 | 1 | [6 empty] | 2 | design & permitting | 2019/20 | Seabank has been delayed by three years due to corresponding delays to the associated new nuclear project. |  | Project needed for renewables off of the South West peninsula, the replanting of Hinkley Point nuclear power station and further CCGT at Seabank
79 | 79. A48 | Trawsfynydd (GB) | Treudyyn (GB) | Reconductor Trawsfynydd-Treuddyn | 1700 | 4 | 1 | [6 empty] | 3 | Planned | 2017/2018 | New investment in the TYNDP, as it was mistakenly omitted from the TYNDP 2010 submission. It is necessary due to RES Integration in North Wales. |  | Reinforcement of the internal grid to integrate the additional flows from the RES generation.
79 | 79. 459 | New Substation (GB) | Legacy-Shrewsbury Tee (GB) | New 400kV double circuit OHL and new 400kV substation in Mid-Wales | 880 | [9 empty] | Design & Permitting | 2016/2017 | Progresses as planned (still targetting the financial year 2016/2017) | Investment needed to connect Mid-Wales wind farms | 79
79 | 79. 459b | Wylfa (GB) | Pembroke (GB) | New HVDC bipolar interconnection with possible offshore connection points at the Irish Sea offshore wind farm. | 2000 | [9 empty] | Planned | 2020/21 | Design Change – The design of the HVDC reinforcement circuit from Wylfa has changed from that in the TYNDP 2010 to now terminate at Pembroke instead of Mid-Wales. This has the potential to save some onshore consenting challenges. Additional benefits may be realised by coordinating the development of the offshore transmission assets with that of the onshore system. The location of the Wylfa HVDC termination may yet move offshore to be located closer to the wind turbines. The expected commissioning date has remained at 2020. |  | 79
79 | 79. 460 | Pentir (GB) | Trawsfynydd (GB) | Upgrade Pentir-Trawsfynydd to double circuit | 3800 | [9 empty] | planned | 2016/2017 | Slight delay in expected commissioning date | Investment needed to accommodate new wind generation off Anglesey and nuclear replanting at Wylfa | 79
79 | 79. 460b | Wylfa (GB) | Pentir (GB) | New 400kV Wylfa-Pentir double circuit | 3600 | [9 empty] | planned | 2017/2018 | Progresses as planned (still targetting the financial year 2017/2018) | Investment needed to connect offshore wind and nuclear | 79
80 | 80. 461 | Woodland (IE) | Deeside (GB) | A new 260 km HVDC (200 kV DC) underground and subsea connection between Ireland and Britain with 500MW capacity. On the Irish side, a 45km direct current underground cable will be built to the Woodland substation where the VSC converter station will be placed. | 500 | 3 | 2 | Island of Ireland? | [5 empty] | 2 | under construction | 2012 | Investment still on schedule for 2012, with less than 1-year delay |  | This medium term project will establish 500MW interconnection capacity between Ireland and GB
81 | 81. 462 | Woodland (IE) | Turleenan (NI) | A new 140 km single circuit 400 kV 1500 MVA OHL from Turleenan 400/275 kV in Northern Ireland to Woodland 400/220 kV in Ireland. This is a new interconnector project between Ireland and Northern Ireland. | 600 | 3 | 2 | NE Ireland | [5 empty] | 1 | design & permitting | 2016 | Project delayed due to permitting process in both jurisdictions. The intermediate station Moyhill is differed pending outcome of future load growth. |  | This medium term project will increase transfer capacity between Ireland and N Ireland to improve security of supply and facilitate Single Market development
82 | 82. 470 | Bellacorick (IE) | Cashla or Flagford (IE) | New 130km single circuit 400 kV OHL from north West Mayo to the EHV system. | 650 | 4 | 1 | [6 empty] | 3 | design & permitting | 2019 | Investment technical description and commissioning date are now defined, and status changed to "design and permitting". |  | The infrastructure development is required to facilitate connection of renewables in the North and West of the Island; It will further integrate the Ireland and N Ireland transmission systems and provide capacity for substantial demand growth in the area.
82 | 82. A37 | tbd (NI) | Tunes Wind (NI) | North coast off-shore wind farm. Multiple connection options are under consideration. | 300 | [9 empty] | under consideration | 2020 | New investment in TYNDP |  | 82
82 | 82. 463 | tbd (IE) | tbd (NI) | Strengthening of EHV networks (partial uprate and new) into Donegal and North and West of Northern Ireland and enhanced links between the two countries. Various technologies are being considered. | 1500-2000 | [9 empty] | under consideration | 2020 | New investment in TYNDP |  | 82
83 | 83. 467 | Moneypoint (IE) | Kilpaddoge (IE) | A new 10km single circuit 220kV 500MVA (underground+subsea) cable constructed across the River Shannon Estuary from Moneypoint in Co. Clare to Tarbert or a new Kilpaddoge station in Co. Kerry. A new 400/220kV transformer at Moneypoint station is included in this project. | 1500-2000 | 4 | 1 | [6 empty] | 2 | design & permitting | 2014 | Project delayed by 2 years because awaiting the completion of the Moneypoint 400 kV station redevelopment works to facilitate the new connection, and a delay due to foreshore permitting arising from a change in one of the connection points (from Tarbert to Kilpaddoge) |  | The infrastructure development is required to facilitate connection of renewables in the South of the Island; the project will also facilitate new interconnection connecting to the grid in the south.
83 | 83. 468 | Moneypoint (IE) | North Kerry (IE) | A new 27km single 400 kV circuit, consisting of a submarine cable from Moneypoint across the Shannon Estuary and an overhead line to a new 400 kV station in north Kerry | [10 empty] | design & permitting | 2019 | Investment technical description and commissioning date are now defined, and status changed to "design and permitting". | Increased capacity between the South-West and the Mid-West regions. | 83
83 | 83. 469 | Knockraha (IE) | Dunstown (IE) | A new 250km single circuit 400kV OHL from Cork to the east, with one intermediary station in the South-East. | [10 empty] | design & permitting | 2020 | Investment technical description and commissioning date are now defined, and status changed to "design and permitting". | Increased capacity between Knockraha in the South-West and Dunstown in the Mid-East regions. The project will also facilitate future interconnection. | 83
84 | 84. 471 | Maynooth (IE) | Woodland (IE) | A new 25km single circuit 400kv OHL from Woodland 400 kV station to a new 400 kV station near or at Maynooth 220 kV station. The project may involve upgrading existing 220 kV circuits to 400 kV or utilizing the route. | 1500-2000 | 4 | 1 | Dublin area | [5 empty] | 2 | under consideration | >2020 | TYNDP 2010 investment 471 now presented in two parts (471 and IE2) |  | This project will provide a high capacity path around Dublin improving security of supply to the city and operability of the Dublin network
84 | 84. A31 | Finglas / Huntstown (IE) | Woodland (IE) | A new 25km single circuit 400 kV from Woodland 400 kV station to a new 400 kV station in the vicinity of Huntstown and Finglas 220 kV stations. | [10 empty] | under consideration | >2020 | New investment in TYNDP to avoid overloads in Dublin City network and to ensure supply to north Dublin City load |  | 84
84 | 84. A32 | Dunstown (IE) | Maynooth (IE) | A new 40km single circuit 400kV OHL circuit from Dunstown 400 kV station to a new 400 kV station in the vicinity of Maynooth 220 kV station. | [10 empty] | under consideration | >2020 | New investment in TYNDP to avoid overloads in Dublin City network, split out from TYNDP2010 investment 471 |  | 84
84 | 84. A33 | Carrickmines (IE) | Dunstown (IE) | A new 45km single circuit 400kV OHL from Dunstown 400 kV station to a new 400 kV station in the vicinity of Carrickmines 220 kV station. | [10 empty] | under consideration | >2020 | New investment in TYNDP to avoid overloads in Dublin City network |  | 84
86 | 86. A49 | Keadby (GB) | Grimsby West (GB) | KEAD-KILL KILL-SHBA KEAD-GRIW circuit uprate | 5200 | 4 | 1 | [6 empty] | 2 | under consideration | long term | New investment in TYNDP | These investments are required due to unprecedented volumes of offshore wind generation connection requests. | This projects helps accommodate new offshore RES generation in the North Sea .
86 | 86. A50 | Under Consideration (GB East Coast) | Under Consideration (GB East Coast) | Connection of Triton Knoll, Doggerbank & Hornsea GB Wind Farms and all associated works | [10 empty] | under consideration | long term | This investment groups former 424b, 424c, 424d, 424e, 424f, 424g, 424h and 424i investments of TYNDP 2010. The group of projects on the east coast of Great Britain has been removed as work is in progress to optimize the onshore/offshore coordination and reduce potential consenting issues. Given the potential for more than 20 GW of renewable offshore generation capacity in UK waters on the East Coast it is expected that multiple connection sites will be required together with suitable circuit capacity, both onshore and offshore. |  | 86
88 | 88. A23 | offshore wind farms (FR) | several French substations (FR) | Subsea cables and substations works | 3000(MT) 6000 (LT) | 4 | 1 | [6 empty] | 3 | planned | 2015-2020 | New investment in TYNDP, required to connect offshore wind farms as decided by the French government in 2010 | Project development will adapt to the pace of generation installation | Connection of 6 GW offshore wind farms in 2 phases. First 3 GW phase in progress (tender).
89 | 89. A24 | Calan (FR) | Plaine-Haute (FR) | New 80km double circuit 220kV underground cable with 2 phase shifters and T-connection of an existing HV substation; 1150 MVARs of capacitors and SVC; new transformer 400/220kV | 500 MW | 2 | 4 | Brittany area | [5 empty] | 1 | design & permitting | 2017 | New investment in TYNDP, required to secure Brittany's supply, along with DSM management plan and a new CCGT in Finistère area. |  | This project is necessary to security Brittany's supply.
90 | 90. 131 | Bickigen (CH) |  | Addition of a second 400/220kV transformer in an existing substation. | 4000 | 1 | 2 | [6 empty] | 3 | design & permitting | 2012 | Progresses as planned |  | This project increase the transfer capability between FR, DE , AT towards pump storage in CH.
90 | 90. 132 | Mühleberg (CH) |  | Construction of a new 400/220kV substation. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 90
90 | 90. 134 | Bassecourt (CH) | Romanel (CH) | Construction of different new 400kV line sections and voltage upgrade of existing 225kV lines into 400kV lines. Total length: 140km. | [10 empty] | design & permitting | 2015 | Delays due to authorization process. |  | 90
90 | 90. 136 | Area of Bodensee (DE, AT, CH) |  | Construction of new lines, extension of existing ones in direction of 400/220/110kV-substation. This project will increase the current power exchange capacity between the DE, AT and CH. The project is expected to increase NTC and Improved the security of supply. | [10 empty] | planned | long term | Progress as planned |  | 90
90 | 90. 129 | Beznau (CH) | Mettlen (CH) | Upgrade of the existing 65km double circuit 220kV OHL to 400kV. | [10 empty] | design & permitting | 2015 | Progresses as planned |  | 90
90 | 90. 130 | La Punt (CH) | Pradella / Ova Spin (CH) | Installation of the second circuit on existing towers of a double-circuit 400kV OHL (50km). | [10 empty] | planned | 2017 | Delays due to authorization process. |  | 90
90 | 90. 133 | Bonaduz (CH) | Mettlen (CH) | Upgrade of the existing 180km double circuit 220kV OHL into 400kV. | [10 empty] | under consideration | 2020 | Progresses as planned |  | 90
90 | 90. 44. 170 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 172 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 173 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 44. 176 | [15 empty] | 0 | The investment contributes both to project 44 and project 90. For the technical description see project 44. | 90
90 | 90. 45. 177 | Goldshöfe (DE) | Bünzwangen (DE) | A new 380kV OHL. Length: 45km. | [10 empty] | under consideration | 2020 | Progresses as planned | The investment contributes also to project 45. | 90
92 | 92. 146 | Aachen/Düren region (DE) | Lixhe (BE) | Connection between Germany and Belgium including new 100km HVDC underground cable and extension of existing 380kV-substations. On Belgian side, new 380 kV circuit between Lixhe and Herderen and second 380 kV overheadline in/out from Herderen to Lixhe. In Belgium, addition of 2 transformers 380/150 kV in Lixhe and in Limburg part; | 1000 | 3 | 2 | Northern Belgium | [5 empty] | 2 | design & permitting | 2017 | The project entered design and permitting phase in 2011, technical description has been completed and expected date of comissioning is 2017 | Alegro Project | First Belgium-Germany interconnection. This project enhances security of supply of both BE and DE. This HVDC link in an AC grid brings flexibility and bidirectional power control allowing integration of RES in both countries. This project aims to be a demonstration for HVDC link integration in the AC meshed grid.
93 | 93. 413 | Ørskog (NO) | Fardal (NO) | New 285 km single circuit 400kV OHL. | 2250 | 3 | 3 | South west of Trondheim (county Møre and Romsdal) | [5 empty] | 3 | under construction | 2015 | Investment delayed due to due to long permitting procedure. | The project is key to improve SoS in Mid-Norway: presently, for several N-1 contingencies, load might be disconnected. The project is also the pre-requisite to lift the ban on RES development in the whole area covered by the new line Ørskog - Fardal. | Security of supply for mid-Norway (Møre and Romsdal mainly) and RES integration in western Norway.
93 | 93. 398A | Under consideration (SE) |  | New shunt compensation of OHL. | [10 empty] | under consideration | 2015 | New part of investment 398 in TYNDP 2010 | Investment 398 in TYNDP 2010 have been divided into 398A and 398B. 398B is described in project 104. | 93
93 | 93. 403 | Scandinavia north (SE) | Scandinavia South (SE) | A joint Stattnett & Svenska Kraftnat study north - south reinforcement (AC or VSC), expected length: 400 - 500km under study. | [10 empty] | under consideration | 2025 | Postponed after reprioritization of the project portfolio |  | 93
93 | 93. 414 | Fardal (NO) | Aurland (NO) | Voltage upgrading of existing single circuit 300kV OHL Fardal-Aurland Extension of 413 - Ørskog - Fardal. | [10 empty] | planned | 2020 | Investment postponed, especially because of long permitting processes. |  | 93
93 | 93. 417 | Aura/Viklandet (NO) | Fåberg (NO) | Voltage upgrading of existing single circuit 300kV OHL Aura/Viklandet-Fåberg. | [10 empty] | under consideration | long term | Investment postponed, especially because of long permitting processes. |  | 93
93 | 93. 416 | Klæbu (NO) | Aura/ Viklandet (NO) | Voltage upgrading of existing single circuit 300kV OHL Klæbu-Aura. | [10 empty] | design & permitting | 2018 (2016-2020) | Investment postponed, especially because of long permitting processes. |  | 93
94 | 94. 139 | Vierraden (DE) | Krajnik (PL) | Upgrade of existing 220 kV line Vierraden-Krajnik to double circuit 400 kV OHL. | >1000 | 1 | 2 | [6 empty] | 1 | design & permitting | long term | Expected date of commissioning was adjusted due to long permitting process and strong local public resistance. |  | PSTs – Control of the transits of power on the polish synchronous profile (increase of import capacity, increase of grid operation safety).
94 | 94. A68 | Krajnik (PL) |  | Upgrade 400 kV | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A69 | Mikułowa (PL) |  | Upgrade 400 kV | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A70 | Krajnik (PL) |  | New PST | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
94 | 94. A71 | Mikułowa (PL) |  | New PST | [10 empty] | design & permitting | 2014 | New investment in the TYNDP, split out from investment 139 |  | 94
103 | 103. 145 | Niederrhein (DE) | Doetinchem (NL) | New 400kV line double circuit DE-NL interconnection line. Length:60km. | 13900 | 3 | 1 | NW part of Netherlands | [5 empty] | 3 | design & permitting | >=2013 | Delays due to authorization process. |  | The project reinforces the Dutch grid to accommodate new conventional and renewable generation, to handle new flow patterns and to increase the interconnection capacity between DE and NL"
103 | 103. 438 | Eemshaven (NL) | Diemen (NL) | New 175-200km AC overhead line with capacity of 2x2650 MVA of 380kV. | [10 empty] | design & permitting | 2018 | Delays due to authorization process. |  | 103
103 | 103. 439 | Borssele (NL) | Geertruidenberg (NL) | New 100-130km double-circuit 380kV OHL with 2x2650 MVA capacity. | [10 empty] | design & permitting | 2016 | Delays due to authorization process. |  | 103
103 | 103. 440 | Maasvlakte (NL) | Beverwijk (NL) | New 380 kV double-circuit mixed project (OHL+ underground cable) including approximately 20km of underground cable for 2650 MVA. The cable sections are a pilot project. The total length of cable at 380kV is frozen until more experience is gained. | [10 empty] | under construction | 2016 | Delays due to authorization process. |  | 103
103 | 103. 441 | Zwolle (NL) | Hengelo (NL) | Upgrade of the capacity of the existing 60km double circuit 380kV OHL to reach a capacity of 2x2650 MVA. | [10 empty] | under consideration | long term | Progresses as planned. |  | 103
103 | 103. 442 | Krimpen aan de Ijssel (NL) | Maasbracht (NL) | Upgrade of the capacity of the existing 150km double circuit 380kV OHL to reach a capacity of 2x2650 MVA. | [10 empty] | under consideration | long term | Progresses as planned. |  | 103
104 | 104. 398B | Under consideration (SE) |  | New series compensation of OHL. | 1200 | 2 | 1 | [6 empty] | 2 | under consideration | 2015 | Reprioritization of projects. | Investment 398 in TYNDP 2010 have been divided into 398A and 398B. 398A is described in project 93. | RES integration in mid-Norway (Trøndelag and Nordland) and reinforcement of Swedish internal interconnections in order to facilitate wind power integration in northern Sweden
104 | 104. 415 | Namsos (NO) | Klæbu and Storeheia (NO) | New line and voltage upgrade of 286km single circuit 400kV OHL | [10 empty] | design & permitting | 2015 | Delays due to authorization process. | New line and voltage upgrade to facilitate new wind power generation | 104
104 | 104. 418 | Nedre Røssåga (NO) | Namsos (NO) | Upgrade of 70km single circuit 400kV OHL | [10 empty] | design & permitting | 2019 | Investment postponed, especially because of long permitting processes. | Increased capacity between north and mid Norway. Facilitates RES integration | 104
104 | 104. 420 | Storheia (NO) | Orkdal / Trollheim (NO) | New 130km single circuit 400kV OHL | [10 empty] | design & permitting | 2017-2020 | Investment postponed due to long permitting procedure. | New line to facilitate wind power generation | 104
104 | 104. A59 | Råbäcken (SE) | Letsi - Betåsen (SE) | New 55km single circuit 400kV OHL | [10 empty] | under consideration | 2017 | New investment in TYNDP. Will probably be postponed after 2020 due to later development of wind power in the area |  | 104
104 | 104. A51 | Svartisen (NO) | Nedre Røssåga (NO) | New 116km 400kV OHL | [10 empty] | planned | 2020 | New investment in TYNDP | New line to facilitate wind power generation | 104
106 | 106. A34 | tbd (IE) | tbd (GB) | A new HVDC subsea connection between Ireland and Great Britain | 700-1000 | 3 | 2 | [6 empty] | 2 | under consideration | long term | New investment in TYNDP, conceptual, cost benefit analysis to be confirmed |  | This project will increase interconnection capacity between Ireland and Great Britain
107 | 107. A25 | tbd (IE) | tbd (FR) | A new HVDC subsea connection between Ireland and France | 700-1000 | 3 | 2 | [6 empty] | 3 | under consideration | long term | New investment in TYNDP, conceptual, cost benefit analysis to be confirmed |  | This project will establish interconnection capacity between Ireland and France
109 | 109. A35 | Oriel (IE) | Oriel Wind Farm (IE) | Oriel off-shore wind farm connecting to a new Oriel 220 kV station located on the Louth - Woodland 220 kV circuit | 330 | 4 | 1 | [6 empty] | 2 | under consideration | 2016 | New investment in TYNDP, required to connect Offshore Wind |  | This project will facilitate the connection of offshore wind
109 | 109. A36 | Carrickmines (IE) | Kish Bank Wind Farm (IE) | Kish Bank off-shore wind farm connecting to the existing Carrickmines 220 kV station | 364 | [9 empty] | under consideration | 2015 | New investment in TYNDP, required to connect Offshore Wind |  | 109
109 | 109. A38 | Northern Ireland (NI) | East Coast Offshore (IE) | 'East Coast Off-shore' wind farm connecting to a 275 kV station to be determined. Multiple connection options are under consideration. | 300-600 | [9 empty] | under consideration | 2018 | New investment in TYNDP, required to connect Offshore Wind |  | 109
110 | 110. 424 | Kvilldal (NO) | tbd (GB) | A new 1000MW HVDC bipolar installation connecting Western Norway and Great Britain via 800km subsea cable; DC voltage is to be determined. | 1000-1400 | 1 | 2 | [6 empty] | 3 | design & permitting | 2018/2021 | Capacity revised. Investment postponed, especially because of long permitting processes. |  | Market integration. Facilitate RES integration in southern and western Norway and improve security of supply.
| 40 | Avelin (FR) Mastaing (FR) |  | Installation of a 3rd busbar in Avelin (existing 400-kV substation) & replacement of components to increase the ability to withstand short-circuit power; Connection of Mastaing (existing 400kV substation) to existing 400kV circuit between Avelin (FR) & Lonny (FR) | [10 empty] | commissioned | commissioned | Commissioned
| 41 | Fruges, Sud-Aveyron, Marne-Sud, Somme (FR) |  | New 400-kV substations connected to existing 400-kV network and equipped with transformers to 220 kV or high voltage networks | [10 empty] | design & permitting | mid term | Project progress according to the plan
| 58 | Ensdorf (DE) | St. Avold (FR) | Change of conductors on the German part of this single circuit 220kV line (9 km) and installation of a phase-shifter in Ensdorf (DE) 220kV substation. | [10 empty] | commissioned | commissioned | Commissioned
| 168 | Goldshöfe (DE) | Dellmensigen (DE) | Upgrade the line Goldshöfe - Dellmensigen from 220kV to 380kV . Line length:114km. Included with the project : 3x 380kV substations, 2 transformers. | [10 empty] | under construction | 2014 | Investment 168 has been postponed to 2014 due to local resistance against the project in a specific area. The rest of the investment is ready.
| 168a | Region South-West Bavaria (DE) |  | Upgrading the existing 220kV OHL to 380kV,length 100km and the extension of existing substations, erection of 380/110kV-transformers. | [10 empty] | cancelled | cancelled | The project was abandoned - was not seen necessary with the new set of projects in place. Note: in the previous TYNDP the status of the project was under consideration and not planned (printing mistake)
| 192 | Hamburg/Krümmel (DE) | Schwerin (DE) | This 380kV double-circuit OHL project will close the missing gap in North-East German grid infrastructure. Only 65km of new line must be constructed, 22km already exist. | [10 empty] | under construction | 2012/2013 | Commissioning delayed by complex permitting procedure, line is partly constructed, is expected to be commissioned in 2012/2013 short term
| 198 | Wuhlheide (DE) | Thyrow (DE) | Berlin South Ring: replacement of an existing old 220kV double-circuit OHL by a 380kV double-circuit OHL. Length: 50km. | [10 empty] | cancelled | cancelled | Project was depending on the replacement of a CHP power plant based in Berlin, due to a new general CHP-concept the plant size could be adopted and the upgrade of the existing 220-kV connection to 380-kV was not necessary any longer, project was given up with regard to the CHP-Plant investor
| 397 | Varangerbotn (NO) | Pirttikoski or Petäjäskoski (FI) | New single circuit 380 - 400kV OHL (500km). | [10 empty] | under consideration | 2020/2025 | Based on a common Statnett/Fingrid study conclusion from the more detailed study on the project that is can be postponed beyond 2021. The need is related to the oil/refinery and wind development on the Northern Norway
| 407 | Tonstad (NO) | Arendal (NO) | Voltage upgrading of existing single circuit 400kV OHL Tonstad-Solhom-Arendal. | [10 empty] | 0 | 0 | This investment proposed as stand-alone in the TYNDP 2010 is now merged into investment 37.406. Its evolution is monitored there. | This investment proposed as stand-alone in the TYNDP 2010 is now merged into investment 37.406. Its evolution is monitored there.
| 409 | Feda, Tonstad (NO) |  | Reactive power devices in 400kV substations. | [10 empty] | 0 | 0 | This investment proposed as stand-alone in the TYNDP 2010 is now merged into investment 37.406. Its evolution is monitored there. | This investment proposed as stand-alone in the TYNDP 2010 is now merged into investment 37.406. Its evolution is monitored there.
| 413a | Sima (NO) | Samnanger (NO) | New 420kV line Sima-Samnanger to ensure security of supply in the region of Hordaland/ Bergen, and to integrate new hydro power. | [10 empty] | under construction | 2013/2014 | Project going according to the plan
| 419 | Namsos (NO) | Storheia (NO) | New 119km 800MVA single circuit Namsos-Roan-Storheia OHL to connect new wind power generation at Fosen. | [10 empty] | under construction | 2015 | This projects is now embedded in the investment 104.415.
| 456c | Quernmore(GB) | Padiham(GB) | New 400kV double circuit. | [10 empty] | canceled | cancelled | Both projects were originally proposed in TYNDP 2010 to accommodate expected new nuclear build in the area and to reinforce the local system. Since that time there has been changes to the generation background and changes anticipated system flows, therefore these new circuits are no long thought to be required.
| 465 | LAOIS-KILKENNY (IE) |  | A new 500 MVA 400/110kV substation connected into the Moneypoint-Dunstown 400kV line and the Athy-Portlaoise 110kV line, and with two 400/110kV 250 MVA transformers. This project also comprises a new 110kV line from Loughteeog to Ballyragget 38kV station and upgrading of Ballyragget station and the Ballyragget-Kilkenny 38kV line from 38kV to 110kV substation. | [10 empty] | design & permitting | 2014 | Progress according to the plan
| 431 | Tjele (DK) | Trige (DK) | New 46km single circuit 400kV line via cable with capacity of approx. 1200 MW. | [10 empty] | Planned | long term | Investment moved to longer time horizon
| 203 | Area Wolmirstedt(DE) | under consideration | Support of RES and conventional generation integration, maintaining of security of supply and support of market development. | [10 empty] | under consideration | 2020 | Included in new investment H3 due to new wind BS generation
| 456b | Harker(GB) | Quernmore(GB) | New 400kV double circuit. | [10 empty] | cancelled | cancelled | Both projects were originally proposed in TYNDP 2010 to accommodate expected new nuclear build in the area and to reinforce the local system. Since that time there has been changes to the generation background and changes anticipated system flows, therefore these new circuits are no long thought to be required.
| 451 | Rowdown (GB) |  | New 400kV quadboosters. | [10 empty] | cancelled | cancelled | The installation of new quad-boosters at Rowdown is no longer deemed necessary due to a change in strategy, with the other developments in and around London meeting the system requirements, as described in Cluster 105.
| 429 | Ferslev (DK) | Vester Hassing (DK) | New 20km single circuit 400kV line via a cable with a capacity of approx. 800 MW. | [10 empty] | planned | 2018 | No change
| 180 | Mengede (DE) | Kruckel (DE) | Installation of a second circuit 380kV OHL and extension of existing substations. Line length:16km. | [10 empty] | design & permitting | mid term | project develops according to the plan
| 52 | Feuillane (FR) | Realtor (FR) | Operation at 400 kV of existing 63km double circuit OHL previously operated at 220kV, creation of a new 400 kV substation and restructuration of the existing 220 kV local network | [10 empty] | under construction | 2012 | To be commissioned by end 2012 - delays due to longer than expected authorization process
| 61 | Moulaine (FR) | Belval (LU) | Connection of SOTEL (industrial grid in LU) to RTE network by mixed (underground cable & OHL) single circuit 220kV line. Parts of the new line use existing ones. | [10 empty] | under construction | short term | Commissioned in 2010 for the French part, the LU part is still pending
| 143 | Kassö (DK) & Ensted (DK) |  | Installation of two PSTs. This step includes also planed strengthening of existing 380kV lines in the grid of TenneT.eu and Energinet.dk . | [10 empty] | commissioned | commissioned | commissioned
| 39 | Avelin (FR) | Warande (FR) | Reconductoring (with ACSS) of both circuits of existing 400kV OHL between Avelin, Weppes & Warande. Total length : 85km | [10 empty] | commissioned | commissioned | Commissioned in 2010
| 43 | Mandarins (FR) |  | Replacement of thyristors in the AC/DC substation (IFA 2000 interconnector, DC voltage 270 kV) | [10 empty] | commissioned | commissioned | Currently under final tests. Will be commissioned in Summer 2012.
| 47 | Tamareau (FR) | Tavel (FR) | Reconductoring with ACCS of both circuits of existing 92km double circuit 400kV OHL to increase its capacity. | [10 empty] | commissioned | commissioned | Commissioned in 2011
| 49 | Cantegrit (FR) | Mouguerre (FR) | Reconductoring (with ACSS) of existing 83km single-circuit 220kV OHL to increase its capacity. | [10 empty] | commissioned | commissioned | Commissioned in 2011
| 50 | Néoules (FR) | Broc-Carros (FR) | The second circuit (formerly operated at 220kV) of a 197km double-circuit 400kV OHL will be operated at 400kV and 400/225 autotransformers installed in relevant substations. | [10 empty] | commissioned | commissioned | Commissioned in 2010
| 56 | Camporosso (IT) |  | New 450 MVA PST in Camporosso (IT) 220kV substation on Camporosso (IT) - Menton (FR) - Trinité-Victor (FR) OHL. | [10 empty] | under construction | 2012 | will be commissioned in 2012
| 59 | Moulaine (FR) | Aubange (BE) | Installation of a second circuit on the existing 220kV cross-border OHL | [10 empty] | commissioned | commissioned | Commissioned in 2010
| 169 | Großgartach (DE) |  | Upgrade the substation for a higher short circuit capacity. New installation includes 10 gas insulated bays, 63 kA, 3 bus-bar and 2 transformers. | [10 empty] | commissioned | commissioned | Commissioned
| 201 | Bärwalde (DE) | Schmölln (DE) | New internal double circuit 380kV-line connecting the substations St. Peter and Salzach new (replacement of the existing 220kV-line). Length: 46km. | [10 empty] | design & permitting | 2014 | Delays due to authorization process.
| 196 | wind farm Baltic 1 (DE) | Bentwisch (DE) | Connection of the offshore wind farm Baltic 1 (AC-cables on transmission voltage level). | [10 empty] | commissioned | commissioned | Commissioned
| 210 | Substations in 5 Hertz Transmission control area |  | Construction of new 380/110kV substations. | [10 empty] | commissioned | commissioned | Freiberg and Stendal/West are commissioned. The remaining substations were transferred to the 44. 209 investment.
| 37. 408 | Kristiansand, Feda (NO) |  | Reactive compensation due to HVDC links NorNed and Skagerak 4. Reactive power devices in 400kV substations. | [10 empty] | design & permitting | 2012/2014 | Feda is in the planning and permitting stage. Kristiansand is under construction(commissioned expected as planned 2012)
| 410 | Kristiansand (NO) |  | Spare transformer for the HVDC Skagerak interconnection transformer. | [10 empty] | under construction | 2012 | Will be commissioned 2012.
| 434 | Fraugde (DK) | Herslev(DK) | New single circuit HVDC-LCC installation including a 56km 450kV DC subsea cable with 600MW capacity. | [10 empty] | commissioned | commissioned | Commissioned Sept. 2010.
| 437 | Grain (GB) | Maasvlakte (NL) | New 1000MW HVDC bipolar installation including 260km of 450kV DC subsea cable | [10 empty] | commissioned | commissioned | The BritNed HVDC interconnection between Grain (UK) and Maasvlakte (NL) was commissioned in 2011 and is now operational providing 1000MW capability between the two countries.
| 464 | Moyhill (IE) | Woodland (IE) | This element of the interconnection project between Ireland and Northern Ireland can now be REMOVED. Previously, the Turleenan - Woodland circuit consisted of a Moyhill - Turleenan and a Moyhill - Woodland circuit. However the planning application for the Moyhill station has been deferred. | [10 empty] | cancelled | cancelled | In TYNDP 2010 the Turleenan – Moyhill – Woodland 400 kV circuit was described by two separate investments; 462 (Turleenan to Moyhill) and 464 (Moyhill to Woodland). Since then plans for Moyhill have been deferred. The project is now Turleenan – Woodland 400 kV; described in the table by investment 462+464 (Project #110/Boundary #49). | In TYNDP 2010 the Turleenan – Moyhill – Woodland 400 kV circuit was described by two separate investments; 462 (Turleenan to Moyhill) and 464 (Moyhill to Woodland). Since then plans for Moyhill have been deferred. The project is now Turleenan – Woodland 400 kV; described in the table by investment 462+464 (Project #110)
| 466 | Flagford (IE) | Srananagh (IE) | The construction of a new 55km single circuit 220kV line connecting the existing Flagford 220/100kV station to a new Srananagh 220/110kV station. | [10 empty] | commissioned | commissioned | This investment is expected to be completed by the time TYNDP 2012-2022 is published
| 448 | Thames estuary (GB) |  | Double-circuit 400kV line upgrade around the Thames estuary. | [10 empty] | cancelled | cancelled | With changes in the scenario backgrounds, the initially proposed new 400kV circuit around the Thames Estuary is no longer deemed necessary compared with the TYNDP 2010 assessment.
| A61 | Samnanger (NO) | Sauda (NO) | Voltage upgrade of existing 300kV line. | [10 empty] | under consideration | 2021 | New project