## Readme
ABOUT THE INFORMATION IN THIS EXCEL TEMPLATE | COST-BENEFIT ANALYSIS RESULTS
Information presented in this excel file has been downloaded from ENTSO-E's TYNDP 2020 projects platform, accessible at https://tyndp2020-project-platform.azurewebsites.net/projectsheets. This excel files contains, for all or part of the projects depending on the filters applied before downloading: - TYNDP 2020 transmission projects data, at project level and at investment level - TYNDP 2020 storage projects data - Results of the cost-benefit analysis performed by ENTSO-E for all TYNDP 2020 projects. About the data All information presented in the tabs Trans.Projects, Trans.Investments and Stor.Projects was submitted by project promoters. CBA results presented in tabs 2025NT, 2030NT, 2030GA, 2030DE and 2030CT are the outcome of the assessment performed by ENTSO-E. ENTSO-E warns that some information may change up until the final release of the TYNDP2020, in particular depending on the recommendations received by ENTSO-E in the TYNDP public consultation and ACER opinion. Part of the information regarding TYNDP 2020 projects is not included in this file but can be accessed in each project's sheet from the TYNDP 2020 projects platform (link above). This includes i.e. project-level benefits submitted by project promoters, and CBA results in countries not belonging to the ENTSO-E perimeter. | Tabs 2025NT, 2030NT, 2030GA, 2030DE and 2030CT present the results of the cost-benefit analysis performed by ENTSO-E, for each scenario studied in the TYNDP 2020. Refer to the following table for information on each indicator.
Indicators
| Shortcut | Full name | Indicator | Unit
| ΔSEW | Annual Socio-Economic Welfare (SEW) increase (excluding Energy Not Served cost) | B1 | M€ / year
| ΔSEW_CO2 | Annual Socio-Economic Welfare variation resulting from CO2 emmisions | B1_CO2 | M€ / year
| ΔSEW_RES | Annual Socio-Economic Welfare increase resulting from RES integration | B1_RES | M€ / year
| ΔCO2_market | Annual CO2 varation from market simulation | B2a | ktonnes / year
| ΔCO2_network | Annual CO2 varation due to network losses | B2b | ktonnes / year
| ΔCO2_market_monetised | Annual Societal cost variation resulting from CO2 variation from market simulation | B2a_€ | M€ / year
| ΔCO2_network_monetised | Annual Societal cost variation resulting from CO2 variation from network simulation | B2b_€ | M€ / year
| ΔRES | Annual avoided curtailment (RES integration) | B3 | GWh / year
| ΔRES_MW | Connected RES | B3a | MW
| ΔNOx | Nitrogen oxides | B4a | kg / year
| ΔNH3 | Ammonia | B4b | kg / year
| ΔSO2 | Sulphur dioxide | B4c | kg / year
| ΔPM5 | Particulate matter 5 | B4d | kg / year
For question on TYNDP 2020 data, contact tyndp@entsoe.eu | ΔPM10 | Particulate matter 10 | B4e | kg / year
| ΔNMVOC | Non-methane volatile organic compounds | B4f | kg / year
| Δlosses | Variation of network losses | B5 | GWh / year
| Δlosses_monetised | Variation of network losses monetised | B5_€ | M€ / year
| ΔSoS | Annual reduction in Energy Not Served | B6 | MWh / year
| ΔSoS_monetised | Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served | B6_€ | M€ / year

## Trans.Projects
TYNDP 2020 - General information on transmission projects | [15 empty] | Needs addressed by the project |  | Expected transfer capacity increase
Project ID | Project Name | Description of the project | Promoters | Country | National development plan(s) | Commissioning Year | Status ID 1 : Under Consideration, 2 : In Planning but not permitting, 3 : In permitting, 4 : Under Construction | Is the project cross-border? | Is the project internal? | Comments on CBA results by the project promoter (to be provided after results are shared) | Type of project - Is it an upgrade of existing infrastructure? | Is the project on the 4th PCI list? | PCI number | Reason for investment clustering | Is the project in the reference grid? | Needs addressed by the project | Explanation by the promoter on how the project addresses the need | Border | Transfer capacity increase A-B (MW) | Transfer capacity increase B-A (MW)
1 | RES in north of Portugal | The main objective of this project consists in introducing the network reinforcements that are needed to allow the connection of new RES generation (hydro with pumping and also wind) that is foreseen in the north of Portugal, where the RES potential is high. The project includes a set of new 400 kV OHL that will form a new axis between V. Minho-R. Pena-Feira (PCI 2.16.3). A new 400 kV OHL Pedralva-Sobrado (PCI 2.16.1) is also included in this cluster, in order to ensure the maintenance of the NTC values between PT and ES that were available prior to the connection of these new power plants. | Rede Elétrica Nacional | PT | NDP 1, Portugal, Draft NDP 2020-2029, pages 136 (https://www.erse.pt/media/harhy1bu/proposta-de-pdirt-e-2019_relat%C3%B3rio.pdf); Appendix 3, page 1 and Appendix 4 page 3 (https://www.erse.pt/media/1mrlurih/proposta-de-pdirt-e-2019_anexos.pdf) | 2021 | 2 | False | True |  | New | True | 2.16.1 and 2.16.3 | Clustering: This project includes a set of new 400 kV OHL that will form a new axis between V. Minho-R. Pena-Feira, ensuring the network capacity to evacuate the new amounts of generation, taking also into consideration the n-1 security criteria. The new substations of R. Pena is also considered in this axis for direct connection of generation. A new line between Pedralva and Sobrado is also included in this cluster, in order to ensure the maintenance of the NTC values between PT and ES that were available prior to the connection of the new generation. | True | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Adequacy needs are identified in Portugal mainly due to the expected decommissioning of old power plants along with increasing levels of variable generation. The integration of Hydro power plants with pumping (included in this project) are necessary in order to comply with national adequacy standards Flexibility is the ability of a power system to respond to changes in power demand and generation. Storage facilities such as pumped storage and hydro storage schemes with peak generation are one of the solutions to cope with high power ramps Project for integration of Hydro power plants with pumping | Internal (Portugal) | 1400 | 1400
4 | Interconnection Portugal-Spain | In order to reach a complete operational Iberian Electricity Market (MIBEL), and strengthen the Internal Energy Market (IEM), the increase of the interconnection between Spain and Portugal is needed. A new OHL 400kV interconnection between Fontefría (Spain) and Ponte de Lima (Portugal). Internal reinforcements complement the cross border section, such as the axis in Spain between Fontefría and Beariz, in order to be able to connect the crossborder project to the existing network, and in Portugal between Ponte de Lima (previously Viana do Castelo) and Vila Nova de Famalicão (previously Vila doConde). This project was included in the 2013, 2015, 2017 and 2019 PCI list (PCI 2.17). | Red Eléctrica de España Rede Elétrica Nacional | ES ;PT | Spanish NDP, Spain, 2015-2020, Project Label TI-1 and Project Sheet in Annex III, page 141 & Portuguese NDP, Portugal,Draft NDP 2020-2029, pages 197 (https://www.erse.pt/media/harhy1bu/proposta-de-pdirt-e-2019_relat%C3%B3rio.pdf); Appendix 4 page 3 (https://www.erse.pt/media/1mrlurih/proposta-de-pdirt-e-2019_anexos.pdf), Spanish NDP, Spain, 2015-2020, Project Label TI-1 and Project Sheet in Annex III, page 141 | 2022 | 3 | True | False |  | New | True | 2.17 | Clustering: the project consists of a set of investments in the same transmission corridor, based on a 400 kV OHL axis linking the substations of Beariz and Fontefría, in Spain, with P. Lima-V. N. Famalicão, in Portugal. These reinforcements are all needed (as they are in series) to achieve the main objectives of the project: reinforcement of the interconnection capacity between Portugal and Spain having in mind the MIBEL targets agreed by the Portuguese and Spanish governments and also to allow Portugal to achieve the 10% interconnection ratio defined by the EC, both contributing for the IEM. | True | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | IoSN report shows that for the 2040NT scenario the yearly average marginal price difference is higher than the 2€/MWh defined by Interconnection Target Expert Group as threshold for developing new interconnections. In addition, Spanish interconnectors nominal transmission capacity is below 30% of the national peak load and RES capacity The increase of interconnection capacity will be essential to cope with the residual load ramps challenge. The increase of interconnection capacity between countries will allow to exchange the power flows from flexibility sources. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity. New interconnections with cross border impact can enable the increase of exchange of balancing energy (Welfare savings through exchanging balancing energy and trough imbalance netting). Balancing energy refers to products such as Replacement Reserve (RR), manual and automatic Frequency Regulation Reserve (FRR). | Spain - Portugal | 1900 | 1000
16 | Biscay Gulf | The project consists of 370 km HVDC-VSC link (2 bipoles of 1000 MW each) mainly subsea in the Biscay Gulf, between Gatica (Basque Country, ES) and Cubnezais (Aquitaine, FR). Included in the Madrid Declaration, this project aims at improving the interconnection ES-FR. This project was included in the 2013,2015 and 2017 PCi list (PCI 2.7) | Red Eléctrica de España RTE | ES ;FR | Spanish NDP, Spain, 2015-2020, Project Label TI-2 and Project Sheet in Annex III, page 144 - French NDP, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), France, 2019, project n°476, page 441, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 | 2027 | 3 | True | False | The project helps to integrate RES generation of the Iberian Peninsula: it mainly allows to replace nuclear in France by RES generation that would have been curtailed without the project. It sometimes also helps to decrease thermal generation in Spain and Portugal and farther in Europe substituting it by available RES. This leads to a considerable reduction of the total generation costs (SEW) in all scenarios. Furthermore SEW benefits are higher in 2040 horizon after nuclear phase out in France (see IoSN report). When analyzing the results of the different scenarios studied, it can be concluded that the higher the penetration of RES in the Iberian Peninsula, especially solar generation, the higher the SEW of the project is. Thus, the SEW is the lowest in scenarios NT 2025 and CT 2030, and the highest in scenario DE 2030. These scenarios frame the results of scenarios NT2030 and GA2030, which are equivalent in terms of SEW results. The TYNDP 2018 showed greater benefits. Indeed, the scenarios used at that time corresponded to a more ambitious objective of nuclear phase-out in France and the French nuclear installed capacity was therefore much lower. Thus, the avoided curtailed energy in the Iberian Peninsula, instead of replacing cheap French nuclear generation, replaced a much larger share of thermal generation. Additionally the Spanish thermal capacity in TYNDP 2018 scenarios was greater than the one considered in these new scenarios in which the forecasted gradual closure of coal-fired power plants is considered. The project shows a significant contribution to avoid ENS. The SOS indicator shows that this interconnection project gives large benefits to use existing thermal generation in the Iberian Peninsula to avoid potential ENS in Western Europe. In addition, an increase of transfer capacity between Iberia and the rest of Europe would improve the system security and its robustness from the dynamic point of view. The project increases flows in both directions, from France to Spain and from Spain to France, and especially from Spain to France in NT 2030. Amount of losses are quite high in all the scenarios as the project allows higher long transit power flows on long distances in order to supply the demand with the cheapest generation available through Western Europe. These results in MWh are aligned with TYNDP2018, however monetization drops sharply mainly due to the decrease of marginal cost. This project helps to integrate the Iberian Peninsula in a full-integrated European internal energy market, as it reduces its historical electric isolation (Spain won't yet fulfill the 10% objective for 2020 in spite of the strong technical and political efforts, as Spain would still be a range of 6-7%. This project also helps to integrate the high RES potential in the Iberian Peninsula. In addition, it also contributes to the security of supply, not only regarding adequacy (especially in tight situations), but also regarding flexibility and stability of the system. The project reduces the congestion rate in a range from 16 to 22% in NT 2030 scenario, depending on the climate year. Nevertheless after the commissioning of the project the congestions are limited to 59-67%. | New | True | 2.7 | This project has interdependence with the internal projects P378 and P379 that reinforce the Gatica area in Spain. These internal reinforcements should be commissioned together with the Biscay Gulf. Although the clustering of all projects would have sense, it was not possible due to ENTSOE clustering rules. A global profitability would have sense considering the 3 projects together. | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The increase of interconnection capacity will be essential to cope with the residual load ramps challenge. The increase of interconnection capacity between countries will allow to exchange the power flows from flexibility sources. IoSN report shows that for the 2040 time horizon there is need for developing projects in the French-Spanish border. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchanges between France and the Iberian Peninsula. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity. | Spain - France | 2200 | 2200
23 | FR-BE: Avelin/Mastaing-Avelgem-Horta HTLS | The project consists in the reconductoring of the existing 80km double-circuit 400kV AC cross-border line between Lille (Avelin/Mastaing, FR) - Avelgem (BE) and onwards to Zomergem (Horta, BE) with High Temperature Low Sag conductors to double its capacity. The main driver is relieving congestion on the French-Belgium border resulting from higher power flows within the CWE area, transporting energy through and to Belgium. Today this axis is occasionally a bottleneck in day-ahead flow-based market coupling. Given the expected increase in power flows, it will become a structural bottleneck. Increasing the interconnection capacity between France and Belgium creates synergies between the export position of France in favorable meteorological conditions and the import position of Belgium with higher flows from south (France) to north (Belgium) appearing more frequently on the French-Belgium border. The reinforcement of the section between Avelgem & Horta is part of the project and needed not only to sustain higher flows from France to Belgium but also to evacuate energy in case of high infeed from offshore wind or import from the UK. | ELIA RTE | BE ;FR | NDP1, Belgium, 2015-2025, p.84, NDP2, France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), 2019, project n°378, page 439, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 | 2022 | 4 | True | False |  | Upgrade | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between Belgium and France. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours yearly and reduces therefore the price differentials. This is also included as key trigger of the 2030 interconnection criteria. France and Belgium face decreasing figures of installed conventionals due to reduction or phaseout of nuclear and bad market conditions for other conventionals. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE-region. Based on IOsN report, 15% IC-target requires higher cross border transmission capacity. This project contributes to satisfy this need, provided that the project benefits outweigh its costs. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | France - Belgium | 1000 | 1000
26 | Reschenpass Interconnector Project | New 220kV interconnector between the substations Nauders (AT) and Glorenza (IT). Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. | Austrian Power Grid TERNA | AT ;IT | Avanzamento piani di sviluppo precedenti Terna 2015/pag.192, Italy; APG Netzentwicklungsplan 2019, AT, 2019, 11-12, 48, https://www.apg.at/de/Stromnetz/Netzentwicklung | 2023 | 4 | True | False | About B2 CO2 emissions: Results relative to CO2 emissions are strictly dependent on scenario assumptions (especially lifetime of lignite and coal power plants, that should be assessed from a perspective consistent with considered time horizons 2030 and 2040). About B6 - Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served monetised): In Italy a different parameter is used for the monetization of the Expected Energy Not Served (EENS) variation due to this project, because the current parameter used by ENTSOE in this project sheet (10 k€/MWh) is not compliant with National regulations in force in Italy n°627/2016 (“Minimum Requirements for the preparation of the Ten Year Development Plan of the National Transmission Network” according to which benefits related to reduction of EENS is monetized through a Value of Lost Load (VOLL) in a range between 20 k€/MWh and 40 k€/MWh. | New | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | This project contributes to lower the price differentials between Italian market zones and Austria This project will improve the integration of italian RES generation This project helps Italy to reach the 15% interconnection target by 2030 This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity. | Austria - Italy | 300 | 300
28 | Italy-Montenegro | The Italy-Montenegro interconnection project includes a new HVDC subsea cable between Villanova (Italy) and Lastva (Montenegro) and the DC converter stations. The second HVDC module (600 MW) of the Italy-Montenegro interconnection project is strictly correlated with the Transbalkan (project 227) and the Mid Continental East (project 144) corridors, and therefore contributes significantly to enable the usage of an increased transmission capacity between Italy and South-Eastern European Countries (especially Romania and Bulgaria) | TERNA CGES |  | Avanzamento Piani di Sviluppo precedenti 2015/Pag.278, Italy | 2026 | 4 | True | False | About B2 - Co2 emissions: Results relative to CO2 emissions are strictly dependent on scenario assumptions (especially lifetime of lignite and coal power plants, that should be assessed from a perspective consistent with considered time horizons 2030 and 2040). About B6 - Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served monetised): In Italy a different parameter is used for the monetization of the Expected Energy Not Served (EENS) variation due to this project, because the current parameter used by ENTSOE in this project sheet (10 k€/MWh) is not compliant with National regulations in force in Italy n°627/2016 (“Minimum Requirements for the preparation of the Ten Year Development Plan of the National Transmission Network” according to which benefits related to reduction of EENS is monetized through a Value of Lost Load (VOLL) in a range between 20 k€/MWh and 40 k€/MWh. | New | False |  | The three investments are necessary for the completion of the entire Interconnection between Italia and Montenegro which will bring a contribute to the cross-border transmission capacity of 1200 MW. However, investments n. 70 and 624 will be eliminated because they will be commissioned in 2019 | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian market zones Italy and Montenegro This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity This project will help to solve important congestions among Italian transmission grid This project will improve the integration of italian RES generation | Italy - Montenegro | 600 | 600
29 | Italy-Tunisia | The project consists in a new interconnection between Tunisia and Sicily to be realized through an HVDC submarine cable. The realization of the project is supported by the Italian and Tunisian Governments to increase the interconnection capacity of the Euro-Mediterranean system. Moreover, the project will contribute to reduce, under specific conditions, present and future limitations to the power exchanges on the northern Italian border, with France, Switzerland, Austria and Slovenia, and therefore it will allow to significantly increase the transmission capacity and its exploitation by at least 500 MW on that boundary. | TERNA STEG | IT ;TN | Avanzamento Piani di Sviluppo precedenti 2015/Pag.13, Italy | 2027 | 3 | True | False | About B2 - Co2 emissions: Results relative to CO2 emissions are strictly dependent on scenario assumptions (especially lifetime of lignite and coal power plants, that should be assessed from a perspective consistent with considered time horizons 2030 and 2040). About B6 - Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served monetised): In Italy a different parameter is used for the monetization of the Expected Energy Not Served (EENS) variation due to this project, because the current parameter used by ENTSOE in this project sheet (10 k€/MWh) is not compliant with National regulations in force in Italy n°627/2016 (“Minimum Requirements for the preparation of the Ten Year Development Plan of the National Transmission Network” according to which benefits related to reduction of EENS is monetized through a Value of Lost Load (VOLL) in a range between 20 k€/MWh and 40 k€/MWh. | New | True | 3.27 |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian market zones and Tunisia This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity This project will improve the integration of italian RES generation | Italy - Tunisia | 600 | 600
33 | Central Northern Italy | The project consists in the strengthening of interconnection between the northern and the central part of Italy. It will involve the upgrading of existing 220 kV over-head line to 400 kV between Colunga and Calenzano substations as well as the removing of limitations on the existing 220 kV network in Central Italy | TERNA | IT | Avanzamento Piani di Sviluppo precedenti 2015/Pag.223-233, Italy | 2022 | 2 | False | True | About B6 - Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served monetised): In Italy a different parameter is used for the monetization of the Expected Energy Not Served (EENS) variation due to this project, because the current parameter used by ENTSOE in this project sheet (10 k€/MWh) is not compliant with National regulations in force in Italy n°627/2016 (“Minimum Requirements for the preparation of the Ten Year Development Plan of the National Transmission Network” according to which benefits related to reduction of EENS is monetized through a Value of Lost Load (VOLL) in a range between 20 k€/MWh and 40 k€/MWh. | Upgrade | False |  | The two investments will closely contribute to reduce congestions and guarantee a major market integration between Italy-North and Italy Center | True | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | In case of failure of the OHL along the Adriatic or Thyrrenic coast the upgraded lines will improve transient stability. The new line will allow congestion reduction on the North Center-Northern border, in order to transport the foreign import to the local loads and to integrate the southern renewable production. | Internal (Italy) | 400 | 400
35 | CZ Southwest-east corridor | A corridor of internal 400 kV overhead lines inside the Czech Republic connecting existing 420 kV substations between Prestice, Kocin and Mirovka in the southwest-east direction. The project consists of buidling a new AC 400 kV overhead line which connects 420 kV substations Kocin and Mirovka with double circuit line of about 120.5 km length and a nominal transmission capacity of 2x1713 MVA, building a AC 400 kV overhead lines that involves changing of a 400 kV existing single-circuit line to double-circuit line with a nominal capacity of 2x1713 MVA between Kocin and Prestice. | CEPS | CZ | 24.5.2019 | 2028 | 3 | False | True |  | New | True | 3.11.3, 3.11.4 | Project 35 that contains investment items 313 and 315 altogether with Project 200 that contains investment items 308 and 309 forms a geographically continuous (uninterrupted) network corridor from a new 420 kV substation Vernerov (already commissioned at the end of 2017), through a new 420 kV substation Vitkov (which is under construction with a commissioning date at the of 2020), existing 420 kV substation Prestice, existing 420 kV substation Kocin and ending up to the existing substation 420 kV Mirovka. It is actually what is referred as a “convoy lines” or "sequantial projects" with all 4 involved 400 kV overhead lines (investment 308 (Vernerov-Vitkov), 309 (Vitkov-Prestice), 315 (Prestice-Kocin) and 313 (Kocin-Mirovka)) connected in series forming a corridor from the northern-western part of the Czech grid related to the DE-CZ border into the south and eastern direction towards the CZ-SK and CZ-AT borders. | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project helps to decrease the curtailed energy in Germany due to extra market transfers (increase of NTC) on the profile DE - CZ which lead to reduction of marginal price. This project besides the increase of NTC also consists of reinforcement of internal lines and therefore facilitates the future need for cross-border flows. The project contains the upgrade of existing 220 kV lines to 400 kV lines which will reduce infrastructure vulnerability and therefore ensure reliable and secure operation of the grid. The project is aiming at facilitation of the power flows from the RES generation in the northern part of Europe and western part of CZ therefore promotes RES integration. | Czechia - Germany | 500 | 500
36 | Kriegers Flak CGS | The Combined Grid Solution (CGS) is a new AC offshore connection between Denmark and Germany with back to back stations placed in Germany. | Energinet.dk 50HERTZ | DE ;DK | Germany: NEP2030 v2017 p.421 Denmark: RUS-plan 2018 p. 24, 26, 32 and 37 | 2020 | 4 | True | False |  | New | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) | Project connects two market areas (DKE and DE) with high price differentials between EU countries. The projects contributes both, generation capacity and interconnection capacity to mitigate challenges in the DKE system. The projects enables direct cost-efficient connection of 936 MW offshore wind. The project increases system voltage stability by usage of VSC technology and facilitates independent control of active and reactive power. | Denmark - Germany | 400 | 400
37 | Norway - Germany, NordLink | NordLink: a new HVDC connection between Southern Norway and Northern Germany. Estimated subsea cable length: 514km. Capacity: 1400 MW. | STATNETT TenneT DE | DE ;NO | National Grid Development Plans 2019 (both Germany and Norway) | 2020 | 4 | True | False |  | New | True | 1.8.1 |  | True |  |  | Germany - Norway | 1400 | 1400
39 | DKW-DE, step 3 | New double circuit 380kV line from Kassoe (DK) to Audorf (DE). As third phase of the Danish-German agreement to upgrade cross border transfere capacity. The project is labelled by the EC as project of common interes (PCI 1.4.1) | Energinet.dk TenneT DE | DE ;DK | NEP2030 v2019 | 2020 | 4 | True | False |  | New | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | contributes to reduction of price spread by 2040 facilitates exchange of RES and reserves increases system size, thus facilitates sharing of ancillary service high RES increase expected on both sides of the border - further connection via P167 connecting to low correlated RES area | Denmark (DKw) - Germany | 720 | 1000
40 | Belgium-Luxembourg-Germany: long-term perspective | An increase of transfer capacity across the BE-LU-DE corridor is envisioned towards the 2030-2040 time horizon. Further studies will determine the appropriate implementation option and timing, taking into account: - the expected evolution on the LU-DE border as presented in project 328 Project motivation: This project increases the degree of interconnectivity between the Belgian - Luxemburg - German corridor. The possibility of higher market exchanges between bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | AMPRION CREOS ELIA | BE ;DE ;LU | NDP1, Belgium, 2020-2030, §4.5.1, NDP2, Luxemburg, 2040, Scenario report 2040 p.43 ( 2nd February 2018) | 2035 | 1 | True | False |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | Project increases the degree of interconnectivity between the Belgian - Luxemburg - German corridor and allows higher market exchanges leading to higher price convergence. Also part of the 2030 ITEG targets. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner Project increases the degree of interconnectivity between the Belgian - Luxemburg - German corridor and allows higher market exchanges leading to higher price convergence. Also part of the 2030 ITEG targets. | Belgium - Luxembourg | 500 | 500
47 | Westtirol (AT) - Vöhringen (DE) | This project will increase the current power exchange capacity between Austria and Germany by an upgrade of the existing overhead line Vöhringen (DE) - Westtirol (AT) to 380 kV and the extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. | AMPRION Austrian Power Grid | AT ;DE | Netzentwicklungsplan 2030 Version 2019, Germany, P74 M96, p. 446, Austria: APG Netzentwicklungsplan 2019, AT, 2019, 13-2, 48, https://www.apg.at/en/Stromnetz/Netzentwicklung | 2027 | 2 | True | False |  | Upgrade | False |  |  | False | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase of German interconnection level. Better utilisation of existing and future pump storage power plants by improved transport capacities. Connecting German RES power with pump storages in Austria. | Austria - Germany | 600 | 600
48 | New SK-HU intercon. - phase 1 | This project will increase the transfer capacity between the Slovak and Hungarian transmission systems, improve security and reliability of operation both transmission systems and support North - South RES power flows in CCE region. Main investments of this project are double circuit AC OHL 400 kV from new Gabcikovo (Slovakia) substation to Gonyu (Hungary) substation, with one circuit connected to the Velky Dur (Slovakia) substation and double circuit AC OHL (preliminary armed only with one circuit on Hungarian side) 400 kV from Rimavska Sobota (Slovakia) substation to Sajoivanka (Hungary) substation. | MAVIR SEPS | HU ;SK | A Magyar Villamosenergia-rendszer Hálózatfejlesztési Terve 2017., Hungary, 2017, Page 5, Desaťročný plán rozvoja prenosovej sústavy na roky 2020-2029 (for the time being only Slovak version is available), Slovakia, 2019, Page 34. | 2020 | 4 | True | False |  | New | True | 3.16, 3.17 | The two cross-border elements are on the Western and Eastern part of the HU-SK profile, and both are needed to ensure the NTC increase potential of the project, taking into account as well as improvement of the N-1 criterion fulfilment at the SK-HU profile. The two Hungarian internal investments in substation Sajóivánka are needed for the connection of cross-border line Sajóivánka-Rimavská Sobota. | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project decreases the marginal costs difference between HU and SK, based on the market simulation results, so it improves market integration. The project increases system flexibility and stability during maintenance periods in North-Eastern Hungary. The project improves operational security at the SK-HU cross-border profile, as without the project cross-border and loop flows in scenarios could violate fulfillment of N-1 security criterion. The project improves accomodation of the north-south flows caused by new RES connections. | Hungary - Slovakia | 800 | 1300
62 | Estonia-Latvia 3rd IC | Project nr 62 is a planned third 330 kV interconnection between Estonia and Latvia. The project consists of 3 investments of which nr 386 is the main inter-area investment, AC 330 kV OHL between Kilingi-Nõmme substation in Estonia and Riga CHP2 substations. | AST ELERING | EE ;LV | It is included in the Latvian National Power Transmission System Development Plan 2020-2029 which has been approved by resolution of the Public Utility Commission Council No.149 of September 2019, Project Nr. 1, Appendix 3. | 2020 | 4 | True | False |  | New | True | 4.2 |  | True | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to allow by 2025 for the synchronisation of the Baltic States with the rest of the EU network |  | Estonia - Latvia | 600 | 600
78 | South West Cluster | New 400kV substation at Hinkley Point. New 400kV transmission route from Hinkley Point to Seabank. Reconstruction of Bridgewater substation for 400kV operation. Uprate Bridgewater - Melksham to 400kV. | National Grid | GB |  | 2024 | 3 | False | True |  | MostlyNew | False |  |  | True |  |  | Internal (UK) | 3200 | 3200
81 | North South Interconnector | A new 400 kV interconnector between Woodland in Ireland and Turleenan in Northern Ireland. | EIRGRID SONI | GB ;IE | • Transmission Development Plan Northern Ireland 2019-2028, page 71: http://www.soni.ltd.uk/media/documents/SONI-TDPNI-2019-2028.pdf • Transmission Development Plan Ireland 2019-2028, page 40: https://www.eirgridgroup.com/site-files/library/EirGrid/TDP-2019-2028-Final-For-Publication.pdf | 2023 | 3 | True | False | The project benefits are driven by a number of factors. The project allows for the efficient functioning of the Single Electricity Market (SEM), allowing a more efficient dispatch of generation capacity across the island of Ireland which would otherwise not have access due to network and operation restrictions. This project allows for a lower must run thermal generation requirement in the SEM and, as a consequence, allows for integration of RES generation that would otherwise have been dispatched down. This is reflected in the results, where the project allows for the integration of between 480 GWh and 560 GWh of renewable generation per year on the island of Ireland by 2030. This RES integration, and associated reduction in thermal generation requirements, results in CO2 savings of between 280 kT and 340 kT per year. The increased cross border capacity the project provides between Ireland and Northern Ireland leads to an improved security of supply within the SEM. The resulting benefits are estimated to be €50m per year by 2030. The north-east area of Ireland in particular has long term security of supply needs that are accommodated by this project, as a result of the increased ability to share generation capacity across the island. | New | True | PCI 2.13.1 |  | True | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | The increased transfer capacity and reduction of system separation risk results in a reduction in must run thermal unit requirements, thus allowing additional renewable generation to be dispatched across the island of Ireland. The project establishes a second interconnector between Ireland and Northern Ireland, effectively eliminating the ongoing risk of system separation, thus allowing an increased transfer capacity. This allows a more efficient generation dispatch across the island, resulting in production cost savings. With only one interconnector between IE and NI, the transfer capacity is limited, to reduce the risk of power failures in the event of the loss of the interconnector. This project resolves the issue by providing security against loss of one interconnector, therefore removing restrictions on cross border energy flows | Ireland - Northern Ireland | 950 | 900
82 | RIDP I | The infrastructure development is required to facilitate connection of renewable generation in the North and West of the Island. It will further integrate the Ireland and Northern Ireland transmission systems and provide capacity for substantial demand growth. | EIRGRID SONI | GB ;IE | • Transmission Development Plan Northern Ireland 2019-2028, page 66: http://www.soni.ltd.uk/media/documents/SONI-TDPNI-2019-2028.pdf • Transmission Development Plan Ireland 2019-2028, page 41: https://www.eirgridgroup.com/site-files/library/EirGrid/TDP-2019-2028-Final-For-Publication.pdf | 2030 | 2 | True | False | The main project benefit is the facilitation of RES and avoiding having to constrain RES due to insufficient transmission capacity. The project will connect the 220 kV network in the North West of Ireland to the 275 kV network in Northern Ireland via new RES collection points in Ireland and Northern Ireland, ensuring that the existing networks can be used to their full capacity. Note that Project 81, the North South Interconnector is required prior to RIDP 1. The project allows for the integration of between 290 GWh and 490 GWh of renewable generation per year on the island of Ireland by 2030. This RES integration, and associated reduction in thermal generation requirements, results in CO2 savings of between 120 kT and 180 kT per year. | New | True | 2.13.2 |  | False | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This development facilitates the connection of renewable generation in the North and West of the island of Ireland. Existing infrastructure in the area is 110 kV; this 220 kV and 275 kV development provides significant additional capacity to allow the secure connection of renewable generation. | Ireland - Northern Ireland | 570 | 570
85 | Integration of RES in Alentejo | The main objective of this project consists in introducing the network reinforcements that are needed to allow the connection of new RES generation (mostly solar but also some wind) that is foreseen for the south region of Portugal, where the solar potential is considerably high. The project includes two new 400 kV OHL that will constitute a new axis between F. Alentejo-Ourique-Tavira substations. It is also included the expansion of the Ourique substation to include the 400 kV voltage level and a new 400KV OHL Alqueva-Divor. | Rede Elétrica Nacional | PT | NDP 1, Portugal, Draft NDP 2020-2029, pages 140 (https://www.erse.pt/media/harhy1bu/proposta-de-pdirt-e-2019_relat%C3%B3rio.pdf); Appendix 3, page 1 and Appendix 4 page 3 (https://www.erse.pt/media/1mrlurih/proposta-de-pdirt-e-2019_anexos.pdf) | 2023 | 2 | False | True |  | MostlyUpgrade | False |  | Clustering: the project consists of a new axis connecting Ferreira do Alentejo and Tavira substations, passing through an intermediate substation (Ourique) that will need to be expanded to include the 400 kV voltage level. All these investments are in series so a lack of any of them will not allow to get the desired GTC increase of the project. Also a new 400 OHL Alqueva-Divor is included in this cluster in order to increase and allow the maximum utilization of the potential of the main investment. | True | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | TYNDP 2018 and 2020 System Needs study showed high level of congestion in the network resulting from the integration of RES (mainly Solar) congestion in the network in the south of Portugal where the solar potential is considerably high. Project for integration of RES (mainly Solar). | Internal (Portugal) | 1000 | 1000
92 | ALEGrO | This project realizes the first interconnection between Belgium (Lixhe) and Germany (Oberzier) as a 100 km HVDC link with a bidirectional rated power of 1.000 MW capacity. Project motivation: This project increases the degree of interconnectivity between the Belgian and German bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. Due to the future RES increase in whole CWE, the RES spillage will rise significantly especially beyond 2030. This interconnector project allows a better integration of RES in the entire region and especially in Germany. Belgium and Germany face decreasing figures of installed conventionals especially due to the nuclear phaseout in both countries and bad market conditions for other conventionals. The interconnector contributes to meet adecacy not only in both countries but also in the entire CWE-region. Based on the above, the project also directly contributes to the 2020 interconnection targets. | AMPRION ELIA | BE ;DE | NDP1, Belgium, 2015-2025, p85; NDP2, Germany, Netzentwicklungsplan 2030 Version 2019, Project AMP-P65, p. 306 | 2020 | 4 | True | False |  | New | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and German bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. Belgium and Germany face decreasing figures of installed conventionals especially due to the nuclear phase out in both countries and bad market conditions for other conventionals. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE-region. Due to the future RES increase in whole CWE the RES spillage will rise significantly especially beyond 2030. This interconnector project allows a better integration of RES in the entire region. | Belgium - Germany | 1000 | 1000
94 | GerPol Improvements | Upgrade of the existing 220 kV double interconnection line between Krajnik and Vierraden to 400 kV together with installation of Phase Shifting Transformers (PST) on the two existing interconnection lines (Krajnik-Vierraden by 50Hertz Transmission GmbH in Vierraden and Mikulowa-Hagenverder by PSE S.A. in Mikulowa) including an upgrade of substations Vierraden, Krajnik and Mikulowa. The new PST in Mikulowa on the 400 KV double line Mikulowa–Hagenwerder were already finally commissioned in June 2016. The first two PST in Vierraden have been commissioned in August 2018. The updated 400 kV double line Krajnik – Vierraden is in operation with one system and these two PST in series. On the German side there is a link to the existing 220 kV lines using two 380/220 kV transformers as an intermediate step. Two further PST will replace these two 380/220 kV transformers after the upgrade of the existing German Uckermark-line to 380 kV. This necessary upgrade of the connecting Uckermark-line is delayed due to the lack of an enforceable building permission. | 50HERTZ | DE ;PL | Germany: NEP2030 v2017 p. 188 | 2022 | 4 | True | False |  | Upgrade | False |  |  | True | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | This project contributes a reduction of unscheduled flows DE-PL, PL-CZ and PL-SK by increasing the controllability of the power flow on the DE-PL border. This project enables the integration of additional RES in the area of western and north-western Poland as well as in the eastern part of Germany. Finalization of the project GerPol Improvements allows to increase cross-border capacity on the Polish-German border and thus allows to exchange more energy. Project contributes to mitigate the risk of adequacy deficiencies in Germany and Poland by connecting areas with different mix of generation. | Germany - Poland | 500 | 1500
103 | Reinforcements Ring NL phase I | Upgrade of existing 380kV circuits in the Dutch main ring from 2,5 kA to 4 kA. | TENNET-NL | NL | Samenvatting KCD 2017, The Netherlands, https://www.tennet.eu/fileadmin/user_upload/Company/Publications/Technical_Publications/Dutch/TenneT_KCD2017_samenvatting.pdf | 2025 | 3 | False | True |  | Upgrade | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Upgrade of the internal grid via this project will help facilitated increase of cross-border exchange capacity between different bidding zones reducing thus the price differentials The upgrade of the internal grid will solve congestions due to new power flow patterns for which the grid was not designed for. Connection of high volumes of RES in the future will create high flows for which the grid was not designed for. Upgrading the grid via this project will help transport power from the generation sites to the load centers | Germany - Netherlands | 600 | 600
107 | Celtic Interconnector | Celtic Interconnector will be the first interconnection between Ireland and France. A survey of the route of the HVDC (VSC) link with 700 MW capacity has been done from the southern coast of Ireland to La Martyre (Finistère) in France. Motivation for the project : The CELTIC project will improve security of supply in both Ireland and France. It will facilitate increased electricity trading that will result in increased competition and downward pressure on electricity prices. The CELTIC project will also support the development of renewable sources of energy. | EIRGRID RTE | FR ;IE | NDP1, Ireland, n°107, 2016, page 92 - NDP2, France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), 2019, project n°437, page 442, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 | 2026 | 3 | True | False | Project benefits mainly come from avoided RES curtailment in Ireland and Northern Ireland replacing conventional generation. This reduction in renewable energy curtailment is facilitated by the new connection with the continent which gives the Irish island system access to the generation mix and the enlarged opportunities of the continental market. Thus, the main drivers of the benefits are the level of installed RES capacity in Ireland and Northern Ireland, and the fuel prices of the replaced generation, including the CO2 price. The project allows for the integration of an additional 400 GWh per year of RES at the commissioning date and an additional 1400 GWh per year in 2030. It also facilitates exports from the continent during periods of low RES generation in Ireland. Depending on the merit order and the generation fleets of each scenario, the technology of conventional generation replaced by Irish RES may vary and the project may also enable some substitutions between the different categories of fuels. This leads to different amounts of reduction of market CO2 emissions: from 400k tons per year in 2030 CT (Current Trend) scenario, up to 1000k tons per year in 2030 DE (Distributed Energy). Those values does not include the increase of the CO2 emissions due to the losses of the project which has only been evaluated for NT scenario (+152 k tons per year). In all the scenarios, the project increases market integration by enabling the reduction of price differentials between Irish and continental systems. It also increases security of supply by offering mutual support between Irish and French systems which will have to face significant changes in their generation mix. | New | True | 1.6 |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | Figures 2.12 and 2.13 of IoSN Report show that average marginal price difference would be higher than 10€/MWh between France and Ireland in future scenarios if no investment is done, and only between 5 and 10€/MWh with the investment. IoSN Report Chapter 5 (Flexibility aspect, Transient and voltage stability related aspects): the ramp increases from NT2025 to NT2040. The project allows Ireland to take benefits from the more stable continental grid, participates in reactive power management and frequency management by quickly changing its active power. IoSN report 2020, figures 2.8-2.11: main drivers of NT scenarios are better access to RES generation (avoiding curtailment) which replaces expensive thermal generation. Figures 2.2-2.3: in Ireland, curtailment decreases by half with the IoSN SEW needs in 2030 compared to 2020. Same for 2040 compared to 2025. Based on IoSN report, 15% IC-target requires higher cross border transmission capacity. This project P107 contributes to satisfy this need (especially for Ireland, by increasing the transmission capacity while the installed RES generation is going higher too). | France - Ireland | 700 | 700
110 | Norway-Great Britain, North Sea Link | North Sea Link is a 720 km long subsea interconnector between Norway and Great Britain which is planned to be commissioned in 2021. When realised, it will be the world's longest subsea Interconnector. The main driver for the project is to integrate the hydro-based Norwegian system with the thermal, nuclear and wind-based British system. The interconnector will improve security of supply both in Norway in dry years and in Great Britain in periods with negative power balance (low wind, high demand etc.). In addition, the interconnector will be positive for the European market integration, whilst also facilitating renewable energy in preparation for a power system with lower CO2-emissions. The interconnector is planned to be a 515 kV 1400 MW HVDC subsea interconnector between western Norway (Kvilldal) and eastern England (Blyth). | National Grid STATNETT | GB ;NO | National Grid Electricity Ten Year Statement, GB, 2018, Appendix C, Pg 3, Figure C2 [Interconnector to Norway] https://www.nationalgrideso.com/insights/electricity-ten-year-statement-etys | 2021 | 4 | True | False |  | New | True | 1.10.1 |  | True |  |  | United Kingdom - Norway | 1400 | 1400
111 | 3rd AC Finland-Sweden north | Third AC 400 kV overhead line interconnector between Finland north and Sweden SE1. Strengthening the AC connection between Finland and Sweden is necessary due to market needs, security of supply in Finland, new wind power generation and larger conventional units. | FINGRID Svenska Kraftnät | FI ;SE | Kantaverkon kehittämissuunnitelma 2019-2030 (currently in Finnish, will be available in english later), Finland, 2019, page 39, FI-XB-FISEAC3; System Development Plan 2018-2027, Sweden, 2017, p.60 | 2025 | 3 | True | False |  | New | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. |  | Finland - Sweden | 900 | 800
120 | MOG II: connection of up to 2 GW additional offshore wind Belgium | Following the concept of MOG (project 75), the MOG II aims at centralizing the offshore wind farms in an offshore hub and transporting it via 220 kV AC cables to a substation along a new corridor Stevin-Avelgem (see project 329). The number of hubs is subject to further studies - whereas current working hypothesis indicate 2 or 3 platforms and cable sets. Structure, capacity, timing etc. are all subject to the identification of new offshore concession zones in the Belgian part of the North Sea and subsequent proces to translate this into an implementation plan with all involved stakeholders. Project motivation: Project consists of offshore grid investments that allows to connect the new wave of offshore energy to the mainland(on top of scheduled 2,3GW) in an efficient & reliable way - hence strongly facilitates RES integration for Belgium. A Belgian law has been approved on 4th of April 2019 (DOC 54 3581/008) creating a legal framework for a second Modular Offshore Grid. | ELIA | BE | NDP1, Belgium, 2020-2030, §4.3.2 | 2028 | 2 | False | True |  | New | False |  |  | True | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project consists of offshore grid investments that allows to connect a new wave of offshore energy to the mainland (on top of the scheduled 2,3GW) in an efficient and reliable way - hence strongly facilitates RES integration for Belgium. | Internal (Belgium) | 2000 | 2000
121 | Nautilus: multi-purpose interconnector Belgium - UK | This project considers the possibility of a multi-purpose HVDC interconnection between GB and Belgium, that combines the benefits of connecting electricity markets and offshore wind generation in GB and Belgium. The capacity of the interconnection is still under review, but is likely to be in the range of 1 GW – 2GW, with the reference NTC contribution remaining 1,4GW at this stage. Project motivation: Increasing commercial market exchange capacity between Belgian and GB bidding zones will increase overall EU social welfare. An important security of supply contribution is also achieved through implementation of this project, both from avoided alternative investments as from a reduction in loss of load expectancy. Such adequacy contribution can be linked to the decreasing figures of installed conventionals and increasing RES. Finally, significant benefits related to integration of XB redispatching, balancing markets, and exchange or sharing of ancillary services (frequency coupling, frequency reserves, blackstart, reactive power) across the HVDC-IC between synchronous areas can be obtained. Considering the above, the project therefore also contributes directly to the 2030 interconnection criteria. Additionally, integrating offshore wind capacity on to the interconnector could lead to increased benefits and/or investment savings. | ELIA National Grid | BE ;GB | NDP1, Belgium, 2020-2030, §4.2.3.3;NDP2, UK, 2017, p.23 §2.3 | 2028 | 1 | True | False |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and UK bidding zone and possibility of higher market exchanges which leads to higher price convergence. This is also a key trigger of the 2030 ITEG targets. This project has an important adequacy contribution due to decreasing figures of installed conventionals and increasing RES. This is also a key trigger of the 2030 ITEG targets. This interconnector project between Belgium and UK is designed as a HVDC-link. The full controllability of the HVDC link facilitates the balancing of active and reactive power in the Belgian and UK grid. RES integration implies higher flows within & between AC-grid(s) and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. This is also a key trigger of the 2030 ITEG targets. | Belgium - United Kingdom | 1400 | 1400
123 | LitPol Link Stage 2 | Construction of new 400 kV AC double-circuit OHL line with a length of 108 km and capacity of 2x1870 MVA between Ostrołęka and Stanisławów. Temporary one circuit will use part of the existing 220 kV single-circuit line between Ostrołęka and Miłosna. In one circuit of 400 kV line, the Wyszków substation will be constructed. After the construction of 400 kV line, the 220 kV line will be disconnected. Extension of 400 kV Ostrołęka and Stanisławów substations for connection of new Ostrołęka - Stanisławów line. | Polskie Sieci Elektroenergetyczne S.A. | LT ;PL | Plan rozwoju w zakresie zaspokojenia obecnego i przyszłego zapotrzebowania na energię elektryczną na lata 2021-2030", Poland, Year 2020, Project 123, Page 10, https://www.pse.pl/documents/20182/8c629859-1420-432f-8437-6b3a714dda9c?safeargs=646f776e6c6f61643d74727565. | 2023 | 4 | False | True |  | MostlyNew | True | 4.5.2 |  | True | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to allow by 2025 for the synchronisation of the Baltic States with the rest of the EU network | The LitPol Link capacity is planned to be served as a technical exchange as well as backup infrastructure. This is increase system adequacy in Baltic States and Poland. Target capacity of LitPol Link will improved significantly residual load ramp rate in Poland and Baltic States. The AC interconnector LitPol Link between Lithuania and Poland will enable to establish synchronous operation of Baltics States with EU network. Strengthening the internal network in Poland is necessary for achieved this target. | Lithuania - Poland | 500 | 500
124 | NordBalt phase 2 | Second phase includes the internal network reinforcement in Sweden, a key investment to accomplish full utilization of the NordBalt cable between Lithuania and Sweden. The rest of internal investments already commissioned. | AST Lietuvos energijos gamyba, AB Svenska Kraftnät LITGRID AB | LT ;LV ;SE | System Development Plan 2018-2027, Sweden, 2017, p. 64 | 2026 | 3 | True | False |  | New | True | 4.4 | The investment Grobina (LV) - Imanta (LV) in Latvia is commissioned. | True | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This line ensures the long-term safe operation of 700 MW interconnector Nordbalt which is vital for integration of the Baltic power market as well as the Baltic synchronization project. | Lithuania- Sweden | 0 | 0
126 | SE North-south short-term reinforcements | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. | Svenska Kraftnät | SE | System Development Plan 2018-2027, Sweden, 2017, p. 62. Nordic Grid Development Plan 2019, p. 14. | 2030 | 2 | False | True |  | Upgrade | False |  |  | False | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. |  | Internal (Sweden) | 2000 | 2000
127 | Central Southern Italy | The project consists in the reinforcement of southern Italy 400 kV network through new 400 kV lines. The activities will involve the network portions between the substation of Villanova and Foggia, Deliceto and Bisaccia as well as Laino and Altomonte | TERNA | IT | Avanzamento Piani di Sviluppo precedenti 2015/Pag.280-336-345, Italy | 2024 | 3 | False | True | About B6 - Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served monetised): In Italy a different parameter is used for the monetization of the Expected Energy Not Served (EENS) variation due to this project, because the current parameter used by ENTSOE in this project sheet (10 k€/MWh) is not compliant with National regulations in force in Italy n°627/2016 (“Minimum Requirements for the preparation of the Ten Year Development Plan of the National Transmission Network” according to which benefits related to reduction of EENS is monetized through a Value of Lost Load (VOLL) in a range between 20 k€/MWh and 40 k€/MWh. | New | False |  | The three investments will closely contribute to reduce congestions and guarantee a major market integration between Italy-center South and Italy South. | True | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | In case of failure of the first OHL Foggia-Villanova the new line will improve transient stability. The new line will allow congestion reduction in the Southern-Northern border, and the integration of the local renewable production. Reduction of expected RES curtailment | Internal (Italy) | 1000 | 1000
130 | HVDC SuedOstLink Wolmirstedt to area Isar | 2 GW HVDC-connection from North-East Germany (Area of Wolmirstedt), an area with high installed capacities of RES, to the South of Bavaria (area of Isar), an area with high consumption and connections to storage capabilities. A Capacity extension to 4 GW is under investigation. | 50HERTZ TenneT DE | DE | NEP2030 version 2019, page 374 | 2025 | 3 | False | True | CBA results have been determined in compliance with the draft 3rd CBA guideline and its respective Implementation Guideline for the TYNDP 2020 using a redisptach methodology based on a combination of Market and Network simulations. On top of these results, additional benefits may apply depending on the nature of the project. | New | True | 3.12 |  | False | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Infrastructure improves system flexibility and stability. Controllable HVDC connections stabilize the increasingly stressed German system. DC power lines can provide better controllability in the power grid and support especially voltage stability in the system, as the converters can provide both capacitive and inductive reactive power. In situations with high wind infeed or high pan-European market driven flows, unscheduled load flows from North of Germany over Poland and Czech Republic to Bavaria or Austria can occur. The project will reduce unintended load flows significantly and will relieve the transmission grids of neighboring countries. The project will connect the North-East of Germany, a region with a high amont of renewables covering the annual total energy consumption of the area, with Bavaria, a region with high consumption and structural import need as well as access to large hydro storage capabilities in Alps. | Germany - Poland Czechia - Germany Austria - Germany Internal (Germany) | 400 150 100 2000 | 400 150 100 2000
132 | HVDC Line A-North | Project 132 consists of two new HVDC cable from Emden-East to Osterath. The HVDC has a transfer capacity of 2 GW. The project is a grid expansion project for low-loss transmission of high power over long distances from Northern Germany to the Rhineland. Northern Germany is characterized by a large number of regenerative onshore and offshore energy sources which exceed the demand of Northern German loads. The Rhineland, however, is a high-production region with large conventional generation capacity that has to be substituted by renewable generation capacity due to the German coal phase-out. | AMPRION | DE | NDP, Germany, Netzentwicklungsplan 2030 Version 2019, Project DC1, p. 360 | 2025 | 3 | False | True |  | New | False |  |  | False | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) | The project contributes significantly to security of supply and grid stability through the widespread integration of renewable energies in northern Germany. In particular, the system flexibility is increased by the use of HVDC converter. The project enables the integration of offshore wind energy and prevents potential bottlenecks in the adjacent 380/220 kV grid. With long-range energy transport, the use of DC technology reduces the reactive power demand considerably. For this purpose, the HVDC converters additionally provide reactive power. This helps P132 to comply with the AC voltage bands and thus makes an important contribution to the voltage stability. | Internal (Germany) | 2000 | 2000
138 | Black Sea Corridor | The project consists of one 400kV double circuit OHL Cernavoda-Stalpu with in/out connection of one circuit in Gura Ialomitei, one 400 kV double circuit OHL Smardan-Gutinas in Romania and also the new 400 kV OHL Dobrujda-Burgas in Bulgaria. This project allows transfer of generation from Western cost of the Black Sea towards consumption and storage centers in Central Europe and South-Eastern Europe. | ESO TRANSELECTRICA | BG ;RO | Planul de dezvoltare a RET perioada 2020-2029 - draft version- was submitted in October 2020 for approval to the Romanian NRA -page 15, https://web.transelectrica.ro/noutati/noutati/55_2020.08.17_14-30-42.pdf ; http://www.eso.bg/fileObj.php?oid=1179, Bulgaria,NDP2017,page 19 | 2024 | 3 | False | True |  | MostlyNew | True | 3.8 | These investments are completely dependent on each other as the main enhancements in Romania and Bulgaria which remove bottlenecks and integrate RES to the network. Clustering of investments had the purpose to identify investments contributing to the increase of transfer capacity on the same corridor. Proposed Project supports market development in South East Europe which is less developed. Based on upper mentioned information it is crucial to cluster all these investment together, to fully utilize the possible benefits. | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increased cross-border capacities allow European countries to exchange more energy and this will have an impact on reducing the marginal costs. The project contributes to the increase of the transfer capacity across the border between Bulgaria and Romania. The project contributes to reach the 15% interconnection target for 2030 and also will help to reduce the price differentials between the countries. Increase of transfer capacity in the predominant North-South direction at the boundary between Romania and Bulgaria, will support the large scale integration of new RES in the area of Black Sea coast, in both countries and especially Romania. | Bulgaria - Romania | 600 | 600
142 | CSE4 | The project concerns the construction of a new AC 400kV interconnection between Bulgaria and Greece and new AC 400kV overhead lines at the south part of Bulgaria. This project will increase cross border transfer capacity between Bulgaria and Greece | ESO Admie | BG ;GR | http://eso.bg/fileObj.php?oid=2185, Bulgaria,NDP2019, page 20,http://www.admie.gr/fileadmin/user_upload/Files/masm/2018_2027/DPA_2018_2027.pdf, Greece, NDP 2018-2027,page 17193 | 2023 | 4 | True | False |  | New | True | 3.7.1, 3.7.2, 3.7.3 and 3.7.4 |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project contributes in reducing price differentials indicated in the south part of the region by providing access to more competitive generation sources located in the northeast part. The project will allow further RES integration in northeast part of Greece and in northeast and south Bulgaria. | Bulgaria - Greece | 930 | 600
144 | Mid Continental East corridor | The project consists of one double circuit 400 kV interconnection line between Serbia and Romania and reinforcement of the network along the western border in Romania: one new simple circuit 400 kV line from Portile de Fier to Resita and upgrade from 220 kV double circuit to 400 kV double circuit of the axis between Resita and Arad, including upgrade to 400 kV of three substations along this path: Resita, Timisoara, Sacalaz. The main aim of this project is increasing the transmission capacity along the East-West corridor in the South-Eastern and Central Europe, simultaneously contributing to the market integration in the region of interest and enhancing the integration of large renewable sources in the Banat region, located in the close proximity of the Serbian-Romanian border. Along with that, the commissioning of the project will strongly improve the security of supply in the mentioned area, thus fulfilling one of the primary postulates of the modern transmission systems' reliable operation. | EMS TRANSELECTRICA | RO ;RS | Planul de dezvoltare a RET perioada 2020-2029 - draft version- was submitted in October 2020 for approval to the Romanian NRA -page 16, https://web.transelectrica.ro/noutati/noutati/55_2020.08.17_14-30-42.pdf; Plan razvoja prenosnog sistema Republike Srbije za period 2019 - 2028, Serbia, 2019-2027, page 115 | 2025 | 3 | True | False |  | MostlyNew | True | 3.22 | This Project aims to enhance the transmission capacity along the East-West corridor in the South-Eastern and Central Europe. The investments are complementing each other as the main enhancements in Romania which remove bottlenecks and integrate RES to the network. Clustering of investments had the purpose to identify investments contributing to the increase of transfer capacity on the same corridor. Based on upper mentioned information it is crucial to cluster all these investments together, to utilize the possible benefits. | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project contributes to the increase of the transfer capacity across the border between Serbia and Romania. Increased cross-border capacities allow countries to exchange more energy and this will have an impact on reducing the marginal costs. The project contributes to reach the 15% interconnection target for 2030 and also will help to reduce the price differentials between the countries. The project enhances the transmission capacity along the East-West corridor in the South-Eastern and Central Europe. The project supports the large scale integration of new RES in the region of South-West Romania and North-East Serbia. | Hungary - Romania Romania - Serbia | 617 844 | 335 600
150 | Italy-Slovenia | The project consists in a new HVDC link between Salgareda (Italy) and Divaca/Bericevo (Slovenia) which will strengthen the connection between Slovenia and Italy. On Italian side the project is under permitting since 2012, on Slovenian side the project is under consideration (under study). Terna and ELES are evaluating the opportunity to implement the project according to the following two phases: • reinforcement of existing grid (PSTs, upgrade of existing lines) o Delta GTC contribution: 400 MW • HVDC link (two separate investments: one for the IT side and one for the SI side) o Rated power: 800/600 MW o Commissioning date: 2028 (or later, depending on the Study Phase results in Slovenia) o Delta GTC contribution: 600 MW Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. | ELES TERNA | IT ;SI | Avanzamento Piani di Sviluppo precedenti 2015/Pag.190, Italy | 2028 | 3 | True | False | About B2 - CO2 emissions: Results relative to CO2 emissions are strictly dependent on scenario assumptions (especially lifetime of lignite and coal power plants, that should be assessed from a perspective consistent with considered time horizons 2030 and 2040). About B6 - Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served monetised): In Italy a different parameter is used for the monetization of the Expected Energy Not Served (EENS) variation due to this project, because the current parameter used by ENTSOE in this project sheet (10 k€/MWh) is not compliant with National regulations in force in Italy n°627/2016 (“Minimum Requirements for the preparation of the Ten Year Development Plan of the National Transmission Network” according to which benefits related to reduction of EENS is monetized through a Value of Lost Load (VOLL) in a range between 20 k€/MWh and 40 k€/MWh. | New | True | 3.21 |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian market zones and Slovenia This project helps Italy to reach the 15% interconnection target by 2030 This project will contribute to overcome flexibility/stability problems due to scarcely meshed grid This project will improve the integration of Italian RES generation | Italy - Slovenia | 1000 | 1000
153 | France-Alderney-Britain | France-Alderney-Britain (FAB) is a new HVDC subsea interconnector between Exeter (UK) and Menuel (France) with 1,4 GW capacity. Motivation for the project : The project has two main objectives. The first one is to increase the interconnection capacity between France and Great Britain, to answer the market needs. The second objective is to integrate additional RES generation : Wind generation in Great Britain and the project is also designed to provide a route to connect future marine renewable energy planned to be constructed in the seas around Alderney. This could form part of future offshore meshed grids (e.g. North Sea Offshore Grid) and operate with multi-terminal capability. | FABLINK limited RTE Transmission Investment | FR ;GB | NDP1, UK, n°153, 2017 , page 21 - NDP2, France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), France, 2019, project n°127, page 442, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 | 2025 | 3 | True | False |  | New | True | 1.7.1 |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | FAB Link will provide cross border capacity facilitating further access between French and GB markets thereby converging GB and French prices. The GB and French generation mixes are fundamentally different and both are forecast to undergo significant change over the assessment period. FAB Link will provide further capacity between these two markets enhancing security of supply and reducing the risk of power failures. With increasing levels of RES forecast for both France and GB, FAB Link will support the integration and provide these generators access to wider markets thereby reducing the chance of curtailing these carbonised sources of power. FABLink will further contibute to the GB 15% interconnection target and support reducing price differentials. | France - United Kingdom | 1400 | 1400
167 | Viking DKW-GB | 2x700 MW HVDC subsea link across the North Seas. New substations on both sides; Bicker Fen (GB); Revsing (DK) | Energinet.dk National Grid | DK ;GB | Denmark: RUS-plan 2018 p. 24 and 37 | 2023 | 4 | True | False |  | New | True | 1.14 |  | True | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | facilitates exchange of RES and reserves project connects two market areas Uses VSC technology, facilitating independent control of active and reactive power connects two low correlated wind areas | Denmark (DKw) - United Kingdom | 1400 | 1400
170 | Baltic States Synchronization with Continental Europe | Goal of the project is to prepare Baltic states electrical networks for synchronous operation with Continenatal Europe. This project covers a lot of new investments for internal grid reinforcements - new 330 kV and 400 kV AC lines, voltage stabiliser units, synchronous compensators, upgrades of PSS in power stations, internal 110 kV network reinforcement required for synchronization and separation of 110 kV Baltic grid from IPS/UPS system, additional studies. As part of the project, after the synchronization, a new HVDC connection will be established between LT-PL (investment No. 1034) allowing for a commercial exchange of the Baltic States with Continental Europe in the amount of 700 MW. | AST ELERING Polskie Sieci Elektroenergetyczne S.A. LITGRID AB | EE ;LT ;LV ;PL | Lithuania: "Development of the Lithuanian electric power system and transmission grids. 2017-2026" (http://www.litgrid.eu/uploads/files/dir417/dir20/dir1/12_0.php), 2017, page 51. Latvia: NDP "The Power Transmission System Development Plan 2020-2029", approved by resolution of the Public Utilities Commission Council No.149 of 19 September 2019, Projects No. 3 and 4, Annex 3. Poland: Plan rozwoju w zakresie zaspokojenia obecnego i przyszłego zapotrzebowania na energię elektryczną na lata 2021-2030", Poland, Year 2020, Project 170, Page 10, https://www.pse.pl/documents/20182/8c629859-1420-432f-8437-6b3a714dda9c?safeargs=646f776e6c6f61643d74727565. | 2025 | 4 | True | False |  | New | True | 4.8 | After desynchronisation of Baltic States from Russia and Belarus electricity networks, electricity system in Baltic States should be ready for reliable and secure operation having one synchronous double-circuit 400 kV AC line on border with Poland. This goal could be achievable only when eliminating all negative contingency (n-1) factors and eliminating internal bottlenecks in Baltics and Poland. All investments in this project serves one or another goal from above. | False | Infrastructure to allow by 2025 for the synchronisation of the Baltic States with the rest of the EU network Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | New 700 MW HVDC interconnector "Harmony Link" between Lithuania and Poland, upgrades in Alytus (LT) substation, other internal network strenghtening in Poland, Lithuania, Latvia and Estonia will enable to establish synchronous operation of Baltics States with EU network. New investments HVDC Harmony Link, common Baltic Frequency Stability Assessment System (FSAS), upgrading of monitoring and control systems, new voltage stabiliser units, new synchronous condensers will improve transient and frequency stability in Baltic States. New 700 MW HVDC Harmony Link will be used for trading between Baltic States and this will reduce price differentials between Baltic States and EU. New 700 MW HVDC Harmony Link will increase system adequacy in Baltic Staes, will mitigate risk of power failures and has black start capabilities. | Lithuania - Poland | 500 | 1000
172 | ElecLink | ElecLink is a new FR – UK interconnection cable with 1000 MW capacity through the Channel Tunnel between Sellindge (UK) and Mandarins (FR). Converter stations will be located on Eurotunnel concession at Folkestone and Coquelles. This HVDC interconnection is a PCI project (Project of Common Interest) no. 1.7.3 | ElecLink | FR ;GB | French SDDR 2019, page 40 | 2021 | 4 | True | False |  | New | True | 1.7.3 |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to offer more supply options to isolated areas |  | France - United Kingdom | 1000 | 1000
173 | FR-BE: PSTs Aubange-Moulaine | Installation of two phase shifting transformers in Aubange, one on each of the 225kV circuits of the Aubange-Moulaine interconnector. Project motivation: The main driver is relieving congestion on the French-Belgium border resulting from higher bulk power flows within the CWE area, transporting energy through and to Belgium. The 225kV axis between Aubange and Moulaine is electrically speaking highly influenced by both France - Belgium and France - Germany cross border flows. Today this axis is occasionally a bottleneck in day-ahead flow-based market coupling. Given the expected increase in power flows, it will become a structural bottleneck. Solving this bottleneck is complementary to project 23 (HTLS upgrade Avelin/Mastaign - Horta) in developing the potential for additional market exchange capacity on the FR-BE border.The investment in PSTs continues to build upon the investment done in 2009/2010 when a second circuit has been installed, as it allows to continue to use the capacity of this 225kV axis in an efficient way. | ELIA RTE | BE ;FR | NDP1, Belgium, 2015-2025, p.102 | 2021 | 4 | True | False |  | New | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between Belgium and France. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours yearly and reduces therefore the price differentials. This is also included as key trigger of the 2030 interconnection criteria. Based on IOsN report, 15% IC-target requires higher cross border transmission capacity. This project contributes to satisfy this need, provided that the project benefits outweigh its costs. These PSTs will help to balance the flows over the different cross border lines of the French Belgian interconnector. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | Belgium - France | 500 | 500
174 | Greenconnector | Greenconnector is an HVDC interconnector project between Italy and Switzerland for power transport using DC cables rather than overhead lines. The route length is about 165 km. The design power is 1000 MW (1200 MW in overload condition), while the DC voltage is +/- 400 kV DC. Two cables will be installed, working with a bipolar scheme. Great part of the cables route will exploit a section of an existing oil pipeline, no longer in service since January 1997. This pipeline crosses the Italian and Switzerland border at Splügenpass and is running close by the two end stations of the Greenconnector project (Bonaduz in Graubunden Canton and Verderio Inferiore, Lecco). The cables will be pulled inside the pipeline itself, reducing the amount of civil works required before and after cable laying and therefore limiting even temporary environmental impact. For about 47 km the cables will run across the Como lake. The selected technology and voltage level make it possible to build a very efficient interconnector with very low losses. | Worldenergy SA | CH ;IT | Terna Piano di Sviluppo 2019, Italy, page 162, https://download.terna.it/terna/0000/1188/36.PDF | 2024 | 3 | True | False |  | New | True | 2.14 |  | False | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project increases the existing NTC at this border by more than 10% in import towards Italy, by more than 20% in export from Italy. The project contributes towards the target of at least 15% of interconnection capacity in 2030 An HVDC line can contribute to system flexibility and stability, thanks to its fast control. Ancillary services can also be exchanged over the link (e.g. capacity reserve, frequency support) as well as locally at the end points of the link (voltage support). Debottlenecking of the Italian Northern border will contribute to reduce the price differential at the Northern Italian border, which currently exceeds the recommended value. The increase in power exchange across the North-South axis will contribute to the integration of more renewables across loosely correlated weather areas. | Switzerland - Italy | 1000 | 1000
176 | Hansa PowerBridge I | New HVDC interconnector between Sweden (SE4) and Germany (50 Hertz, Continental) aiming to enhance the integration of the Nordic and the continental power market. Moreover the interconnector facilitates RES integration and increases the system adequacy in both systems. | Svenska Kraftnät 50HERTZ | DE ;SE | NEP2030, Germany, v2019, p.527 , System Development Plan 2018-2027, Sweden, 2017, p.64 | 2026 | 3 | True | False |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The main driver is market integration of the Nordic hydro/nuclear/RES dominated system with the German thermal/RES based system. The infrastructure will reduce price differentials between EU countries. The system adequacy is enhanced in Germany which will increase the import potential in period of low wind and solar generation. Also the system adequacy in southern Sweden is enhanced since it given more import capacity in a future with less available nuclear generation capacity. Increase of RES in both countries leads to higher need for trade with high surplus during high wind power production. Flows are to be balanced with southbound flow during peak hours and when hydro inflow in Sweden are high and northbound in periods of high German RES generation by night | Germany - Sweden | 700 | 700
179 | DKE - DE (Kontek2) | This project includes a HVDC subsea interconnector between Denmark-East (DKE) and Germany (DE) and is called Kontek-2. A final grid-connection solution is not prepared yet. | Energinet.dk 50HERTZ | DE ;DK | Denmark: Not in NDP, as this project is in a preliminary phase under consideration. | 2030 | 1 | True | False |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project will serve as connection between the Nordic and central European power systems either transporting hydro power from the Nordic area to continental Europe or transporting wind and thermal power from the continent to the Nordics in times of low hydro levels. The project contributes new interconnection capacity to mitigate challenges in the DKE system. The project will enable the reduction of market price differential to below 2 EUR/MWh. The project will enable the integration of RES. More interconnection capacity will improve capability of balancing the system. | Germany - Denmark | 600 | 600
183 | DKW-DE, Westcoast | New 400 kV line from Endrup (DK) to Klixbüll (DE), increasing the transfer capacity at the West Coast between these countries. The project is labelled by the EC as project of common interest (PCI 1.3.1). | Energinet.dk TenneT DE | DE ;DK | German NDP 2030 v2019: P25 M45 ; Denmark: RUS-plan 2018 p. 24 and 37 | 2023 | 3 | True | False |  | New | True | 1.3.1 |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | contributes to reduction of price spread by 2040 facilitates exchange of RES and reserves increases system size, thus facilitates sharing of ancillary service high RES increase expected on both sides of the border - further connection via P167 connecting to low correlated RES area | Germany - Denmark | 1000 | 1000
186 | East of Austria | To allow the grid integration of the planned renewable energy generation (mainly wind power) in the north-eastern part of Austria ("Weinviertel") the transmission grid infrastructure (currently a rather weak 220kV line) has to be enforced and new substation for the connection needs to be erected. | Austrian Power Grid | AT | APG Netzentwicklungsplan 2019, AT, 2019, 11-8, 48, https://www.apg.at/de/Stromnetz/Netzentwicklung | 2022 | 4 | False | True |  | New | False |  |  | True | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Projects improves connection of wind generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind generation with sufficient capacity to the transmission system and enables future RES development. | Internal (Austria) | 2000 | 2000
187 | St. Peter (AT) - Pleinting (DE) | Increase of the cross border transmission capacity by erecting a new 380kV line between St. Peter (Austria) and Pleinting (Germany). This leads to an improved connection of the very high amount of RES in Germany and the pump storages in the Austrian Alps. | Austrian Power Grid TenneT DE | AT ;DE | DE:2017; APG Netzentwicklungsplan 2019, AT, 2019, 11-7, 48, https://www.apg.at/de/Stromnetz/Netzentwicklung | 2028 | 3 | True | False |  | New | False |  |  | False | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | helps to reach the target in Germany high RES generation connected to pump storage high RES generation connected to pump storage | Austria - Germany | 1500 | 1500
190 | NorthConnect | A 665 km long subsea interconnector between Norway and Scotland is planned to be realised in 2024. The interconnector is planned to be a 1400 MW HVDC subsea interconnector between western Norway (Simadalen) and eastern Scotland (Peterhead), UK. | NorthConnect | GB ;NO | (1) Nordic Grid Development Plan 2019 https://www.statnett.no/contentassets/61e33bec85804310a0feef41387da2c0/nordic-grid-development-plan-2019-for-web.pdf (2) National Grid NOA (Network Options Assessment Plan 2018/2019) https://www.nationalgrideso.com/document/137321/download (3) National Grid ETYS (Electricity Ten Year Statement) nov 2018 https://www.nationalgrideso.com/document/133836/download | 2024 | 3 | True | False |  | New | True | 1.10.2 | NA | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | NorthConnect reduce price spread between the hydropower dominated in bidding zone NO3 in and UK according to IoNS. The landing point Peterhead in Scotland has the highest share of RES in the UK and willl relieve internal congestion towards England (Price differentials are among the highest ) The UK ratio between nominal transmission capacity and installed RES is 14-18% in the TYNDP 2030 reference scenario (including NorthConnect), and the ratio between nominal transmission capacity and peak load is 20-21%. NorthConnect will contribute to improve the above mentioned ITEG indicators Curtailments in UK already exceeded 2.4 TWh (Sep 2020) and are expected to exceed 3 TWh by end of year. Norway also curtails hydropower in wet years. NorthConnect reduces RES curtailments both in UK and Norway. NorthConnect help utilise the complementaries of wind in UK and Norways 86.5 TWH of fhydropower reservoirs, which is about 50% of Europe's total storage capacity. NorthConnect will provide balancing power in periods of calm wind, and store energy in windy periods for RES in the UK | United Kingdom - Norway | 1400 | 1400
197 | N-S Finland P1 stage 2 | This project is fifth 400 kV overhead line connecting North Finland to South Finland and required compensation investments. The project is to be built to increase the North-South transmission capacity thus enabling the integration of new renewable and conventional generation in northern Finland. | FINGRID | FI | Kantaverkon kehittämissuunnitelma 2019-2030 (currently in Finnish, will be available in english later), Finland, 2019, codes: FG-NS-5P1 and FG-NS-PECOMP | 2022 | 4 | False | True |  | New | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. |  | Internal (Finland) | 1000 | 1000
200 | CZ Northwest-South corridor | A corridor of internal 400 kV overhead lines inside the Czech Republic connecting new 420 kV substations between Vernerov, Vitkov and existing substation Prestice in the northwest-south direction. The project consists building of two 400 kV overhead lines involving changing a 220 kV double-circuit lines to 400 kV double-circuit lines with a capacity of 2x1713 MVA each between Vernerov and Vitkov and Vitkov and Prestice. Part of the project is also a construction of a new 420 kV substation Vitkov and upgrading and extension of the existing 420 kV substation Kocin. | CEPS | CZ | 24.5.2019 | 2024 | 3 | False | True |  | MostlyNew | True | 3.11.1, 3.11.2, 3.11.4 | Project 200 that contains investment items 308 and 309 altogether with Project 35 that contains investment items 313 and 315 forms a geographically continuous (uninterrupted) network corridor from a new 420 kV substation Vernerov (commissioned the end of 2017), through a new 420 kV substation Vitkov (which is under construction with a commissioning date at the end of 2020), existing 420 kV substation Prestice, existing 420 kV substation Kocin and ending up at the existing substation 420 kV Mirovka. It is actually what is referred as a “convoy lines” or "sequantial projects" with all 4involved 400 kV overhead lines ( investment 308 (Vernerov-Vitkov), 309 (Vitkov-Prestice), 315 (Prestice-Kocin) and 313 (Kocin-Mirovka)) connected in series forming a corridor from the northern-western part of the Czech grid related to the DE-CZ border into the south and eastern direction towards the CZ-SK and CZ-AT borders. | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project helps to decrease the curtailed energy in Germany due to extra market transfers (increase of NTC) on the profile DE - CZ which lead to reduction of marginal price. This project besides the increase of NTC also consists of reinforcement of internal lines and therefore facilitates the future need for cross-border flows. The project contains the upgrade of existing 220 kV lines to 400 kV lines which will reduce infrastructure vulnerability and therefore ensure reliable and secure operation of the grid. The project is aiming at facilitation of the power flows from the RES generation in the northern part of Europe and western part of CZ therefore promotes RES integration. | Czechia - Germany | 500 | 500
207 | Reinforcement Northwestern DE | Integration of on- and offshore RES in Lower Saxony | TenneT DE | DE | NEP2030 v2019 | 2023 | 4 | False | True |  | New | False |  | The main aim of the project is to integrate huge amounts of RES in the north-western part of Germany. It thus strengthens the north-western grid helping to transfer the RES energy from that region to the connection points to the south. The two serial investments Emden-Halbemond and Conneforde-Emden and the investment Dollern-Elsfleth/West help to transfer the energy from RES sources to the connection points to the south. All three investments therefore significantly contribute to decreasing the RES curtailment in the coastal region and only together the full potential of the project can be achieved. | True |  |  | Internal (Germany) | 0 | 0
208 | N-S Western DE_section North_1 | Project 208 consists of a new 380 kV overhead line (partly in an existing corridor) for up to four 380 kV systems. The project is needed for integration of on- and offshore wind energy and transport to the load centres in western and southern parts of Germany. | AMPRION TenneT DE | DE | Netzentwicklungsplan 2030 Version 2017, Germany | 2021 | 4 | False | True |  | MostlyNew | False |  | The main aim of the project is to integrate huge amounts of RES in the north-western part of Germany. It thus connects the areas of the north-western German, i.e. the coastal areas where the infeed mainly coming from on- and offshore wind energy exceeds the local load, to the areas in the south of Germany with its high load consumption. The investment Niederrhein-Dörpen and in parallel the investments Conneforde-Wilhelmshaven and Ganderkesee-Wehrendorf support to strengthen the western section of the North-South corridor in Germany helping transmit RES from north to south. All three investments therefore significantly contribute to decreasing the RES curtailment in the coastal region and only together the full potential of the project can be achieved. | True |  |  | Internal (Germany) | 0 | 0
210 | Wurmlach (AT) - Somplago (IT) interconnection | Somplago - Wurmlach interconnection is a cross-border electrical line promoted by Alpe Adria Energia Srl. The project concerns a 220kV a.c. merchant line, about 300 MW thermal capacity from Somplago substation to new Wurmlach substation, including Phase Shifter Transformer located in Austria. | Alpe Adria Energia Srl | AT ;IT | The Italian TSO "Terna" declared in its NDP 2019 that it includes only merchant line projects exempted and with a connection agreement signed. The Somplago - Wurmlach interconnection project has a connection authorization but it has not yet obtained the exemption under the Reg. (EC) 943/2019. For this reason this projects is not included in its NDP. Terna mentions the project in the table n. 165 at page 162 of the NDP 2019 (https://download.terna.it/terna/0000/1188/36.PDF) | 2023 | 3 | True | False |  | New | True | PCI 3.4 |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to offer more supply options to isolated areas | The Project will enhance the interconnection capacity between the interconnected Countries and will allow a progressive alignment of the Italian border price differentials also in line with the interconnection target recommendations (Nov 2017) by EC Expert Group. The project will enhance the adequacy of the interconnected systems in the mid/long-term scenarios. In particular, it improves the share of the renewable energy sources and new flexible thermal generation in the electricity systems. The Project contributes to increase the Italian cross-border capacity in the medium-long term objectives (2030) as also reported in the Italian Implementation Plan for the requirements set in article 20 of Regulation 2019/943 of 5th June 2019 on the Internal Electricity Market (IEM). Considering that the Italian Peninsula is one of the most European isolated area, the Project will increase the Italian cross-transfer capacity contributing to reduce the gap with the other European Countries. | Austria - Italy | 150 | 150
219 | EuroAsia Interconnector | The Euro Asia Interconnector consists of a 500 kV DC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot, Israeli and the Greek transmission networks (offshore). The Interconnector will have a capacity of 2000 MW and a total length of around 1200 km (approx. 310 km between CY and IL, 898 km between CY and Crete) and allow for reverse transmission of electricity. | EuroAsia Interconnector Interconnector | CY ;GR ;IL | ΔΕΚΑΕΤΕΣ ΠΡΟΓΡΑΜΜΑ ΑΝΑΠΤΥΞΗΣ ΣΥΣΤΗΜΑΤΟΣ ΜΕΤΑΦΟΡΑΣ 2019-2028. (Transmission System Ten year development plan 2019-2028), Cyprus, 2019 Project number: Paragraph 3.1.1, Page 7 | 2022 | 3 | True | False | The lower gas price of Israel is not considered, so the benefit from the gas price differential is not calculated in the results. The benefit due to the implementation of the EuroAsia Interconnector will increase if the gas price of Israel is taken based on the projections of the Israeli Authorities. Additionally, the NT scenario considers Lignite a cheap technology however ignoring the fact that it increases the CO2 emissions, this fact makes all transmission investments in areas where Lignite exists have a negative impact towards decarbonization. Maybe the above can be rectified by other means such as increasing the price of CO2, by imposing carbon taxes, or by aiming to reduce generation from high-emission sources. Concluding the way the NT scenario is structured it does not encourage developments and reinforcements of the network. | New | True | 3.10 |  | False | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to offer more supply options to isolated areas Capability for Black Start & Islanding Operation | End the Physical Isolation of Cyprus, last Member State totally energy isolated | Cyprus - Greece Cyprus - Israel | 1000 1000 | 1000 1000
225 | 2nd interconnector Belgium - Germany | This project considers the possibility of a second ~1GW HVDC interconnection between Belgium and Germany at the earliest by 2035 (indicative timing). The timing as well as location, routing, capacity are subject to further studies. Project motivation: Preliminary studies have indicated potential for further regional welfare increase by further increasing the interconnection capacity between Belgium and Germany. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This interconnector project is designed as a HVDC-link. The full controllability of the HVDC link facilitates the balancing of active and reactive power in the Belgian and German grid. Belgium and Germany face decreasing figures of installed conventionals due to bad market conditions. The interconnector contributes to meet adecacy not only in both countries but also in the entire CWE-region. Due to the future RES increase in whole CWE the RES spillage will rise significantly especially beyond 2030. This interconnector project allows a better integration of RES in the entire region. | AMPRION ELIA | BE ;DE | NDP1, Belgium, 2020-2030, §4.2.3.4; NDP2, Germany, Netzentwicklungsplan 2030 Version 2019, Project 313, p. 563 | 2035 | 1 | True | False | For indicator B6 – Security of supply, in the NT2030 scenario the following subsequent information was calculated by the project promoter in line with CBA 3.0 method with the Antares market modelling tool: annual reduction in energy not served = 1,590MWh/year and a corresponding annual socio-economic welfare increase resulting from the energy not served (monetized) of 15.90 M€/yr. | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and German bidding zones. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. Belgium and Germany face decreasing figures of installed conventionals due to bad market conditions. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE-region. This interconnector project between Belgium and Germany is designed as a HVDC-link. The full controllability of the HVDC link facilitates the balancing of active and reactive power in the Belgian and German grid. Due to the future RES increase in whole CWE the RES spillage will rise significantly especially beyond 2030. This interconnector project allows a better integration of RES in the entire region. | Belgium - Germany | 1000 | 1000
227 | Transbalkan Corridor | This project contains seven investments, with the new corridor spanning from Central (SS Kragujevac 2 and SS Kraljevo 3) and Western Serbia (SS Obrenovac and SS Bajina Basta) all the way to SS Visegrad in Bosnia and Herzegovina and SS Lastva (across SS Pljevlja 2) in Montenegro. As can be seen from the brief list of the investments, the project aims to increase both the transmission capacity within Serbian transmission system and the transfer capacities on the borders between the mentioned countries. Thus, it is expected that it will largely facilitate the energy exchange between the north-east and south-west parts of Europe, setting a foundation for the enhanced market integration and leveling of the marginal energy costs and guaranteeing the security of supply throughout the region. This project is tightly connected to the projects 28 (Italy - Montenegro) and 342 (Central Balkan Corridor). | EMS NOS-BIH CGES | BA ;IT ;ME ;RS | Plan razvoja prenosnog sistema Republike Srbije za period 2019 - 2028 (Serbian national TYNDP 2019-2028), p205, https://www.aers.rs/FILES/JavnaKonsultacija/2019-02-13_Plan%20razvoja%20prenosnog%20sistema%20Republike%20Srbije%202019-2028.pdf | 2026 | 3 | True | False |  | MostlyNew | False |  | These investments will form new HV AC and DC corridor from Serbia, through Montenegro to Italy, enhancing energy exchange and further market integration in SEE region | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | As the Tranbalkan Corridor encompasses the infrastructure needed for the energy transfer across the Balkan Peninsula and towards Italy, it is envisaged as an invaluable tool for the market integration and consequential reduction of price differentials between Italy and the countries in Continental Southeast Europe region. As the grid in Western Serbia is rather old, which might put its reliability in question, one of the aspects that will also be affected by this project's commissioning is the increase of security of supply by replacing the numerous old power lines with the new ones. As the systems in this region are envisaged to heavily rely on the variable renewable sources in the not-so-distant future, the importance of new interconnections, such as those included in this project, for providing the additional system flexibility cannot be overstated. Even though the importance of this project for the RES integration might not be obvious, Drina river, located near the route of the lines enveloped by the project, offers huge potential for the future environmentally friendly Hydro Power Plants, amplifying the significance of Transbalkan Corridor for this system need. | Montenegro - Serbia Bosnia and Herzegovina - Serbia | 20 850 | 500 700
228 | Muhlbach - Eichstetten | Reinforcement of the existing 400kV OHL. Deployment of a second 400kV circuit at existing double circuit OHL Muhlbach - Eichstetten, instead of the currently operated circuit Eichstetten - Vogelgrun (currently operated with 225kV). Some topological adjustments of the existing grid in the area might prove to be necessary. This also include a transformer in Sierentz substation to balance flows between 225kV and 400kV grid in the area. Motivation for the project : Germany and also the CCS-Region is characterised by a significant increase in RES generation. The grid has to be developed in order to support these new exchange possibilities, facilitating the access to the most economic energy mix, while minimising grid congestions. High flows in both directions West-East and North-South are expected. The project strengthens the European single market. This project increases the interconnector capacity between France and Germany and therefore also the security of supply. | RTE TRANSNET-BW | DE ;FR | NDP1; Netzentwicklungsplan 2030 Version 2019, Germany, Project n°176, p.458 ; NDP2, France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), 2019, project n°880, page 442, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 | 2025 | 2 | True | False | The German-French border belongs to a very densely meshed region (CWE region: Belgium, Netherlands, Germany, France) where exchange capacities between countries are highly dependent on each other. Delta NTC calculation performed within the framework of this TYNDP show several interactions between the reinforcement projects of the German-French border –projects 228 and 244 – and also with other boundaries. Thus: • in the direction France to Germany, the main critical branches are Vigy-Ensdorf-Uchtelfangen lines. The implementation of Dynamic line ratings (DLR) on these lines as a first step and of project 244 as a longer term step will directly increase the exchange capacity. The project 228 will first have a more indirect effect by alleviating the flows on the main critical branches. After the commissioning of several internal reinforcements and PSTs in Germany and the implementation of the DLR on Vigy-Ensdorf-Uchtelfangen lines, which are all scheduled within the same timeframe, the project 228 will achieve its full potential. Indeed it will have a more direct impact on exchange capacity as Mulhbach-Eichstetten will become more often the critical branch. • in the direction Germany to France, the congestions are more widespread between the French, German, Belgium and Netherlands borders. Thus, to reach their full potential, project 228 and 244 need to alleviate congestions in the West corridor of the CWE region. The implementation of dynamic line ratings, the use of controllable devices such as PSTs, as well as other TYNDP projects scheduled within the same timeframe, will allow to capture the full potential of these projects to increase exchange capacity. | Upgrade | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL, BE-LU, FR-DE | Although this is not the main driver for this project, increase the interconnectivity between the German and French bidding zone give the possibility of higher market exchanges between these two bidding zones leading to a higher price convergence in more hours of the year. France and Germany face decreasing figures of installed conventionals due to reduction or phaseout of nuclear and bad market conditions for other conventionals. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE region. Rising figures of RES capacities especially in Germany lead to increasing RES-curtailment in the coming decades. This interconnector project allows a higher export in hours of high RES infeed particularly in Western Germany. Flows on 380kV OHL could be adjusted with both PSTs installed in Muhlbach substation rather than current 220kV interconnector. | Germany - France | 300 | 300
229 | GerPol Power Bridge II | Project consist from following investments: indentation to the one circuit of 400 kV line Baczyna-Plewiska (new routes 400 kV: Baczyna-Zielona Góra, Zielona Góra-Plewiska), crossborder line 2x400 kV line Zielona Góra (PL)-Eisenhuettenstadt (DE), new station Zielona Góra (with Phase Shifting Transformers), new 2x400 kV line Zielona Góra - Polkowice. | Polskie Sieci Elektroenergetyczne S.A. 50HERTZ | DE ;PL | Germany: NEP2024 p.153 // Poland: Link to PSE S.A. Development Plan where investments of this project are included: https://www.pse.pl/documents/20182/8c629859-1420-432f-8437-6b3a714dda9c?safeargs=646f776e6c6f61643d74727565 Pages : 54, 58. | 2035 | 1 | True | True |  | New | False |  | All investments in the 229 project complement each other in bringing the desired increase of Grid Transfer Capability on the Polish-German border. Majority of investents in this cluster connect directly to border substation Zielona Góra and have direct impact on border flows. | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | Finalization of the GerPol Power Bridge II project allows to increase cross-border capacity on the Polish-German border and thus allows to exchange more energy. This project contributes to a reduction of unscheduled flows DE-PL, PL-CZ and PL-SK by increasing the controllability of the power flow on the DE-PL border. This project enables the integration of additional RES in the area of western and north-western Poland as well as in the eastern part of Germany. Project contributes to mitigate the risk of adequacy deficiencies in Germany and Poland by connecting areas with different mix of generation. | Germany - Poland | 1500 | 1500
230 | GerPol Power Bridge I | The reinforcements in the Polish transmission network in western part of the country near Polish/German border. Construction new AC 2x400 kV lines Mikułowa - Świebodzice, Krajnik - Baczyna and Baczyna - Plewiska. | Polskie Sieci Elektroenergetyczne S.A. | PL | Poland, Link to PSE S.A. Development Plan where investments of this project are included: https://www.pse.pl/documents/20182/8c629859-1420-432f-8437-6b3a714dda9c?safeargs=646f776e6c6f61643d74727565 Pages : 42, 50.” | 2024 | 3 | False | True |  | New | True | 3.14 (including 3.14.2, 3.14.3, 3.14.4) | All investments in the 230 project complement each other in bringing the desired increase of Grid Transfer Capability on the Polish-German border. Vast majority of investents in this cluster connect directly to border substations and have direct impact on border flows. | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | Finalization GerPol Power Bridge I project allows to increasing cross-border capacity on Polish-German border and thus allows to exchange more energy. This project enables the integration of additional RES on the area of western and north-western Poland as well as eastern part of Germany This project contributes to accommodate future scenarios and cross-border flows. | Germany - Poland | 1500 | 500
231 | Beznau - Tiengen | This project comprises the upgrade of a 220 kV crossborder line to 380 kV between the substations of Tiengen (DE) and Beznau (CH). | AMPRION SWISSGRID | CH ;DE | NDP1, Germany, Netzentwicklungsplan 2030 Version 2019, Project 204, p. 515 | 2030 | 1 | True | False |  | Upgrade | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to lowering the price differentials between Switzerland on the one hand and Germany and Austria on the other hand. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | Switzerland - Germany | 100 | 600
233 | Connection of Aragon Pumping hydro | Potential necessary transmission development for the connection of 3rd party storage project (pumping hydro) that has received a PCI label in the 3rd list 2017. No details about the required network are known yet (P1011 and P1019 in this TYNDP; take into consideration that these projects compete with each other as they use the same hydro resources). | Red Eléctrica de España | ES | This is a conceptual project that has not been defined yet. Only the Nueva Mequinenza subestation that allows to integrate 1100 MW of pumping hydro is included in the Spanish NDP, Spain, 2015-2020, Page 199 | 2027 | 1 | False | True | Savings in variable generation costs are the result of the full integration of a new pumping storage power plant in the area of Aragón, without any network restriction. Therefore, thanks to the flexibility that the pumping offers to the network, the values of RES integration, CO2 reduction and savings in variable generation costs are high, especially in the 2030 scenarios and particularly in the 2030 DE scenario. Values in 2025 are lower as the installed RES and the flexibility that the project provides is lower. This project helps to integrate the high RES potential in the Iberian Peninsula, in particular in an area where the existing transmission network, is not sufficient to accommodate all the expected future RES connection. | New | False |  |  | False | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project consists of the transmission network required for the connection of new pumping power plants that would give more flexibility to the system as the new pumping units will do. This project consists of the transmission network required for the connection of new pumping power plants that would allow RES integration | Internal (Spain) | 3300 | 3300
234 | DKE - PL-1 | The first HVDC connector between Denmark-East and Poland. | Energinet.dk Polskie Sieci Elektroenergetyczne S.A. | DK ;PL | Denmark: Not in NDP, as this project is in a preliminary phase under consideration. Poland: "Plan rozwoju w zakresie zaspokojenia obecnego i przyszłego zapotrzebowania na energię elektryczną na lata 2021-2030", Poland, Year 2020, Project 234, Page 10, https://www.pse.pl/documents/20182/8c629859-1420-432f-8437-6b3a714dda9c?safeargs=646f776e6c6f61643d74727565. | 2033 | 1 | True | False |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project connects two market areas (DKE and PL) with high price differentials between EU countries. The project will enable the integration of RES. More interconnector capacity improves capability of balacing the system. | Denmark - Poland | 600 | 600
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Grafenrheinfeld | 4 GW HVDC connection from Northern Germany (areas of Brunsbüttel/Wilster) to Bavaria / Baden-Württemberg (areas of Großgartach/Grafenrheinfeld). North Germany is characterised by a high amount of RES, the feed-in exceeds the local load and therefore there is a high demand for transfer to the load centres in southern parts of Germany. With the further installation of additional renewable energy, the relevance of this projects increases. | TRANSNET-BW TenneT DE | DE | NEP2030 v2019 | 2026 | 3 | False | True | CBA results have been determined in compliance with the draft 3rd CBA guideline and its respective Implementation Guideline for the TYNDP 2020 using a redisptach methodology based on a combination of Market and Network simulations. On top of these results, additional benefits may apply depending on the nature of the project. | New | False |  |  | False | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Reducing the redispatch leading to more flexibility and increasing the stability of the system. In critical grid situations, costly congestion management measures are taken to avoid overload of grid elements. The project will reduce the demand for re-dispatching, countertrading and curtailment of renewable energy producers by adding significant transmission capacity between the congested routes in the North-Western part of Germany integration of huge amounts of offshore and onshore wind. | Internal (Germany) | 4000 | 4000
239 | Fenno-Skan 1 renewal | Replacement of the existing 400 kV HVDC cable interconnection between Finland and Sweden. Fennoskan 1 will be decomissioned at the same time with this project being commisioned. | FINGRID Svenska Kraftnät | FI ;SE | Kantaverkon kehittämissuunnitelma 2019-2030 (currently in Finnish, will be available in english later), Finland, 2019; System Development Plan 2018-2027, Sweden, 2017, p. 60 | 2035 | 1 | True | False |  | Upgrade | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. |  | Finland - Sweden | 800 | 800
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines | Upgrading of existing 220 kV lines between SS Dakovo (HR) and SS Tuzla/Gradacac (BA) to 400 kV lines. The project 241, has been proposed assessed in the TYNDP 2016, based on the results of common planning studies performed in the CSE Region during preparation of Regional investment plan 2015. The project assumes upgrade of existing 220 kV lines between SS Dakovo (HR) and SS Tuzla (BH) and SS Gradacac (BH) to 400 kV, with additional internal new double 400 kV line connecting SS Dakovo to existing 400 kV line Žerjavinec - Ernestinovo. This project is under consideration and there is a need for pre-feasibility study. | HOPS NOS-BIH | BA ;HR | Desetogodišnji plan razvoja hrvatske prijenosne mreže 2019.-2028. s detaljnom razradom za početno trogodišnje i jednogodišnje razdoblje, Croatia, 2019, Page 74 | 2032 | 1 | True | False |  | MostlyUpgrade | False |  | The Project implies upgrading of existing 220 kV substations and transmission lines between HR and BA to 400 kV lines, which will enable further connection to the existing 400 kV network in HR and BA and increase security of supply of broader region. | False |  |  | Bosnia and Herzegovina - Croatia | 500 | 500
243 | New 400 kV interconnection line between Serbia and Croatia | Construction of new 400 kV interconnection line Sombor (RS) - Ernestinovo (HR), expected to provide a significant asset in terms of increasing the NTC between Serbia and Croatia, hence allowing the more prominent energy flow in the East-West direction across the CSE region, improving the market integration among the beneficiary countries and further ensuring the security of supply primarily in Serbia and Croatia, but, under certain circumstances, contributing to the reliable functioning of the systems in the rest of the countries in the region as well. Alongside that, it should be mentioned that the project will have a rather positive impact related to the possibility of integration of renewable energy sources in the Backa region. | EMS HOPS | HR ;RS | Plan razvoja prenosnog sistema Republike Srbije za period 2019 - 2028, page 157 (Serbian national TYNDP 2019-2028) | 2035 | 1 | True | False |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Since this interconnection means the increase of NTC between Croatia (EU country) and Serbia (non-EU country), it is seen as a mean of reaching the market integration goals and reducing the price differentials in the Continental Southeast Europe region. As the future scenarios, taken into account in the scope of TYNDP, predict rather high energy flow across the borders in the CSE region, each of the new interconnections in that area can be seen as an additional step towards guaranteeing the timely reaching of the set goal. In the conditions of ever higher needs for the intensive cooperation between the neighboring TSOs, every new interconnection, such as the one included in this project, can be seen as the asset regarding the improvement of systems' flexibility and reliability of operation. According to the currently available information, the Bačka region in Northern Serbia is predicted to host several wind power plants of sustainable installed capacity, with the line between SS Sombor 3 and SS Ernestinovo ensuring the uninterrupted and secure evacuation of the produced energy. | Croatia - Serbia | 600 | 600
244 | Vigy - Uchtelfangen area | An upgrade of the existing over headline between the substations Ensdorf, Uchtelfangen and Vigy is planned to increase the thermal cross-border capacity. For this reinforcement the options are either the implementation of High Temperature Low Sag (HTLS) conductors or a reconstruction of the tie-line in the existing route. To allow an optimal use of the capacity increase the installation of phase shifter transformers (PSTs) is necessary. For these measures the substations have to be adjusted accordingly. Motivation for the project : Germany and also the CCS-Region is characterised by a significant increase in RES generation. The grid has to be developed in order to support these new exchange possibilities, facilitating the access to the most economic energy mix, while minimising grid congestions. High flows in both directions West-East and North-South are expected. The project strengthens the European single market. This project increases the interconnector capacity between France and Germany and therefore also the security of supply. | AMPRION RTE | DE ;FR | NDP1; Netzentwicklungsplan 2030 Version 2019, Germany, Project 170, p. 492, Project 314, p. 567 - NDP2; France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), 2019, project n°444, page 442, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 | 2028 | 2 | True | False | The German-French border belongs to a very densely meshed region (CWE region: Belgium, Netherlands, Germany, France) where exchange capacities between countries are highly dependent on each other. Delta NTC calculation performed within the framework of this TYNDP show several interactions between the reinforcement projects of the German-French border –projects 228 and 244 – and also with other boundaries. Thus: • in the direction France to Germany, the main critical branches are Vigy-Ensdorf-Uchtelfangen lines. The implementation of Dynamic line ratings (DLR) on these lines as a first step and of project 244 as a longer term step will directly increase the exchange capacity. The project 228 will first have a more indirect effect by alleviating the flows on the main critical branches. After the commissioning of several internal reinforcements and PSTs in Germany and the implementation of the DLR on Vigy-Ensdorf-Uchtelfangen lines, which are all scheduled within the same timeframe, the project 228 will achieve its full potential. Indeed it will have a more direct impact on exchange capacity as Mulhbach-Eichstetten will become more often the critical branch. • in the direction Germany to France, the congestions are more widespread between the French, German, Belgium and Netherlands borders. Thus, to reach their full potential, project 228 and 244 need to alleviate congestions in the West corridor of the CWE region. The implementation of dynamic line ratings, the use of controllable devices such as PSTs, as well as other TYNDP projects scheduled within the same timeframe, will allow to capture the full potential of these projects to increase exchange capacity. | MostlyUpgrade | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL, BE-LU, FR-DE | Although this is not the main driver for this project, increasing the interconnectivity between the German and French bidding zone gives the possibility of higher market exchanges between these two bidding zones leading to a higher price convergence in more hours of the year. France and Germany face decreasing figures of installed conventionals due to reduction or phaseout of nuclear and bad market conditions for other conventionals. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE region. Rising figures of RES capacities especially in Germany lead to increasing RES-curtailment in the coming decades. This interconnector project allows a higher export in hours of high RES infeed particularly in Western Germany. RES infeed in the north of Germany often bypasses via Netherlands, Belgium and France. The project allows a better limitation of these loop flows via new PSTs on the French-German border. | Germany - France | 1500 | 1500
245 | Upgrade Meeden - Diele | Increase of the interconnection capacity between The Netherlands and Germany by adding one new phase shifting transformer and apply dynamic line rating on the existing 380 kV double circuit tie line between Meeden and Diele. | TENNET-NL TenneT DE | DE ;NL | Samenvatting KCD 2017 (The Netherlands) page 19 | 2021 | 4 | True | False |  | New | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project helps increase the cross-border capacity between Netherlands and Belgium. This will help reduce the price differentials between these different bidding zones This project increases phase shifting transformer capabilities helping reduce loop flows and distributing cross-border flows better Project increases phase shifting transformer capabilities which increases controlability of the power flows and optimizes further use of existing grid infrastructure Optimized use of existing internal and cross-border infrastructure to better accommodate high volumes of RES and reduce RES curtailment | Germany - The Netherlands | 300 | 300
247 | AQUIND Interconnector | AQUIND Interconnector is a proposed High Voltage Direct Current (HVDC) subsea and underground electric power transmission link between Great Britain (Lovedean substation, Hampshire) and France (Barnabos switching station, Seine-Maritime) with a net transmission capacity of 2,000 MW. The interconnector is designed as two parallel monopole 1000 MW circuits employing Voltage Source Converter technology. The project will be able to: • Boost competition by providing access to wider electricity markets; • Help improve security of supply by creating additional source of supply and by providing ancillary services to the respective national grids; and • Increase sustainability of energy supply by helping to integrate more renewable energy sources. The project will consist of the following elements: • One converter station on each end of the link, • The 320 kV DC subsea cable route will be approximately 182 km in length between Eastney (UK) and Pourville (France). • The British 320 kV DC terrestrial cable route will be approximately 20 km long. • The French 320 kV DC terrestrial cable route will be approximately 36 km long. • The 400 kV AC cable routes are several hundred meters in France and UK. | Aquind Limited | FR ;GB | France – Schéma Décennal de Développement du Réseau 2019, project number 991 (page 442) - https://www.rte-france.com/sites/default/files/sddr2019_chapitre_annexe2.pdf. AQUIND Interconnector is also included in Programmations pluriannuelles de l'énergie of France (page 194) - https://www.ecologique-solidaire.gouv.fr/sites/default/files/0-PPE%20English%20Version%20With%20Annex_0.pdf. Great Britain - Future Energy Scenarios 2019, (FES Modelling Methods 2019, page 16 - http://fes.nationalgrid.com/media/1417/fes-modelling-methods-2019.pdf). AQUIND is also included in latest available Electricity Ten Year Statement 2018, as it is part of National Grid's TEC Register (page 4 - https://www.nationalgrideso.com/document/133211/download and https://www.nationalgrideso.com/document/156486/download) | 2023 | 3 | True | False | The draft TYNDP 2020 project results are very encouraging and indicate that AQUIND is highly beneficial. For example, by 2030, AQUIND is estimated to generate €149m/year socio-economic welfare. This is much higher than TYNDP 2018 results and closer to TYNDP 2016 results. However, we remain concerned about the TYNDP 2020 results for year 2025. Taking into account that the France-GB border has some of the widest price spreads in Europe, the NT 2025 results seem lower than could have been expected and AQUIND’s own forecasts. It is not clear to us why this should be the case. Nevertheless, I am very glad to see that the results of this TYNDP confirm, as well as AQUIND’s forecasts, that the interconnector will play an important role in implementing Net Zero targets and help reduce the cost of energy transition. In addition to the SEW benefits, we welcome ENTSO-E’s findings that AQUIND contributes positively to the security of supply by reducing the total amount of energy not served (estimated at €51m/year), which significantly offsets any potential increases in the network losses (€31m/year). Losses The result for losses variation B5 in GWh in NT 2030 seems too high. The AQUIND’s analysis shows that in 2030 the flows will still be primarily from France to GB. Normandy, the region where AQUIND connects to the French national transmission system, is also a net exporter within France, while Lovedean in England is located in the area near large consumption centres, including London. We note that the level of detail of the available information is not sufficient for third-party promoters to be able to replicate the ENTSOe losses analysis precisely. Process: As AQUIND has indicated to the ENTSO-E in the past, it is critical for the transparency and the robustness of the TYNDP development process to ensure that all prospective developers have equal access to the relevant information that underpins the modelling. In particular, it is important that all the data that ENTSOe uses in preparing the analysis are made available to prospective developers, such that the analysis can be replicated through the use of an appropriate modelling tool (e.g. Plexos®). This information also needs to be available at the appropriate degree of granularity – again, to enable a reasonable degree of scrutiny and to enable modelling results to be replicated. | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | Structural differences in the wholesale electricity prices between the electricity markets in GB and France clearly demonstrate the need for more capacity. By providing additional 2GW of interconnection capacity AQUIND Interconnector will reduce price differentials on a congested France - GB border. AQUIND will provide an opportunity for the efficient dispatch of renewables in GB, France and across connected markets. The additional cross-border capacity provided by AQUIND offers the opportunity to export additional power, that otherwise could be curtailed, during periods of high renewable generation. AQUIND Interconnector will facilitate more efficient generation dispatch in the connected markets required for cross-border balancing services By providing additional 2GW of interconnection capacity AQUIND will contribute to reaching the objectives of the European ITEG indicators in France and GB. | France - United Kingdom | 2075 | 2075
250 | Merchant line Castasegna (CH) - Mese (IT) | The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Rationalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200-250 MW. | Repower MERA SRL | CH ;IT | In Italy the new Substation in Mese is included. https://download.terna.it/terna/0000/1188/36.PDF, pg 113, 162, 166 | 2024 | 3 | True | False |  | New | False |  | The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Ra-tionalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200-250 MW. The Investement is composed by the purly Merchant line Project, around 45M€ and the TERNA Investment part for the rationalisation of the existing 380/132-kV Network and the Realisation of a new 380/132-kV Substation in Mese, other 45M€ Investment. | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Reduce price differential between CWE and Italy by increasing NTC Mitigate RES (hydro Valchiavenna) curtailment | Switzerland - Italy | 200 | 200
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | This project structurally strenghtens the central & eastern part of the internal Belgian backbone. The current conductors on the 380kV ring Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator-Massenhoven will be replaced by HTLS conductors. The implementation starts with the upgrade of the Massenhoven-VanEyck section by 2024 as this is the weakest link only having 1 conductor at the moment. It then follows a phased approach running up to 2035. Phasing is subject to optimalisation in function of outage constraints (operational secutiry) and the evolution of the production park. Project motivation: This upgrade will be key to sustain price convergence whilst the power flows become increasingly more volatile and international. Where in the past the location of generation and load centers was quite stable over time, this will be much less the case with the future energy mix characterized by RES geographically spread out over Europe. Depending on the climatic conditions, flows can come from the north, east, south or west, and even change several times per day as wind fronts and clouds move from one hour to the next. Upgrading the existing internal corridors also ensures the potential to integrate new large power plants domestically. RES integration implies higher flows in the meshed AC-grid and thus increases the need for internal transmission capacity. This project satisfies this need in a cost-efficient manner.This project contributes to adequacy, as both new grid hosting capacity is created & as it supports other projects intending to increase cross border transmission capacity, and in particular for Belgium considering the nuclear phaseout. | ELIA | BE | NDP1, Belgium, 2020-2030, §4.1.3 | 2035 | 2 | False | True | The reinforcement of the high voltage backbone with HTLS conductors will enable integration of future XB interconnections as well as respect of the Clean Energy Package requirement for a RAM of minimally 70%. The project also increases the grid hosting capacity which is a.o. important in the framework of security of supply. The calculated benefits are considered a lower bound of the full value to be captured, since the redispatch simulations do not yet take into account the realization of additional interconnection capacity, nor potential future additional on/offshore RES. | Upgrade | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The upgrade of the backbone ring will unlock the full potential of future cross border capacity investments allowing higher market exchanges between bidding zones and leading to a higher price convergence in more hours of the year. This project contributes to adequacy, as both new grid hosting capacity is created and as it supports other projects intending to increase cross border transmission capacity, and in particular for Belgium considering the nuclear phase out. This project contributes to resolving internal congestions, considering expected increased market exchanges which induce higher flows. RES integration implies higher flows in the meshed AC-grid and thus increases the need for internal transmission capacity. This project satisfies this need in a cost-efficient manner. | Internal (Belgium) | 1500 | 1500
253 | Upstream reinforcement in France to increase FR-CH capacity | The project consists in attracting the flows to the interconnection south of Lake Geneva in order to alleviate the congestion on the link west to Lake Geneva. This project is coupled with Project 333 "PST Foretaille" and will be implemented right after the implementation of PST in Foretaille. | RTE | CH ;FR | SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), France, 2019, project n°446, page 442, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 | 2031 | 1 | True | False |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure | Figures 2.12 and 2.13 of IoSN report: average marginal price difference higher than 10€/MWh between France and Switzerland in future scenarios. Project has positive impact on SoS indicator. Project upgrades the thermal capacity requested for meeting the export increases that have an impact on French internal lines, such as Creys - St Vulbas. Phase-shifting transformer allows optimization of flows on the border. | Switzerland - France | 500 | 500
254 | HVDC Ultranet Osterath to Philippsburg | The Ultranet project consists of a 2 GW HVDC-connection from the Region of Osterath (Rhineland) to the Region of Philippsburg (Baden-Württemberg). It's a pilot project with DC circuits on the same pylons as AC lines and will therefore deliver profund knowledge.It represents a separate subsection for the large-scale transmission link from the North Sea coast to Baden-Württemberg (with P132). | AMPRION TRANSNET-BW | DE | NDP, Germany, Netzentwicklungsplan 2030 Version 2019, Project DC2, p. 363 | 2024 | 3 | False | True | Comment on CO2 Reduction (B2a): According to the results of the redispatch calculations the project leads to an increase in CO2 emissions. This effect occurs due to the assumptions concerning the reference grid. As mentioned in the project description this project has a close connection to project 132 which is basically the extension to Northern Germany. By assessing the project without the northern part, which is not part of the reference grid, it will mainly transport conventional energy from the Rhineland leading to an increase of CO2 emissions. In case the Northern extension (P132) is factored into the assessment a huge amount of the transported energy will consist of renewable energy (e.g. from offshore and onshore wind) and the CO2 emissions will decrease. Comment on Impact on grid losses (B5): According to the results of the redispatch calculations the project leads to an increase in grid losses. The project facilitates new power flows in the German grid, in order to shift more energy to the HVDC link and transport it further to the south. As far as the project P132 is not included to the reference grid, these new flows lead to a higher utilization of the AC grid especially in Western Germany which results in the higher amount of grid losses. | New | True | 2.9 |  | True | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL, BE-LU, FR-DE Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | In connection with P132, the planned HVDC connection transports the energy of regenerative Energy sources in northern Germany directly to the demand regions of southern Germany. It strengthens the common German market area through targeted energy transport. The project reduces loop flows to Germany's neighboring countries by reducing bottlenecks in northern Germany and providing a transport task from western Germany to southern Germany The project enables the integration of offshore wind and onshore wind energy in combination with P132 and prevents potential bottlenecks in northern Germany and southern Germany. The project contributes significantly to security of supply and grid stability through the widespread integration of renewable energies in northern (wind offshore and onshore) and southern Germany (wind onshore). In particular, the system flexibility is increased by the use of HVDC converter. | Internal (Germany) | 2000 | 2000
258 | Westcoast line | New 380-kV-line Heide/West – Klixbüll inside Schleswig – Holstein. Main focus of the project is the integration of onshore RES – mainly wind – in Western Schleswig-Holstein. The project is labeled as PCI 1.3.2. It is the southbound connection of PCI 1.3.1. and is necessary to increase the GTC between Denmark/West and Germany by 500 MW. | TenneT DE | DE | NEP2030 v2019 | 2022 | 4 | False | True |  | New | False |  |  | False |  |  | Internal (Germany) | 500 | 500
259 | HU-RO | 400 kV interconnection line between Hungary and Romania. In Romania, the following internal investments are necessary associated to this project: -new 400/220 kV transformer in substation Rosiori -reconductoring 220 kV OH line Urechesti-Tg. Jiu-Paroseni- Baru Mare-Hasdat -new 400/220 kV transformer in substation Resita | MAVIR TRANSELECTRICA | HU ;RO | A Magyar Villamosenergia-rendszer Hálózatfejlesztési Terve 2017., Hungary, 2017, Page 6; The project is not included in the last approved Romanian NDP but it is included in the draft version of Romanian NDP (Planul de dezvoltare a RET perioada 2020-2029 - draft version) submitted in October 2020 for approval to the Romanian NRA -page 253, https://web.transelectrica.ro/noutati/noutati/55_2020.08.17_14-30-42.pdf | 2030 | 1 | True | False |  | MostlyNew | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | The project contributes to the increase of the transfer capacity across the border between Hungary and Romania. Increased cross-border capacities allow countries to exchange more energy and this will have an impact on reducing the marginal costs. The project creates an additional energy corridor between Hungary and Romania, and it can be claimed that it will provide balancing flexibility area for both sides. | Romania - Hungary | 1117 | 685
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | This project considers a multi-purpose HVDC interconnection between Great Britain and The Netherlands, that combines the benefits of connecting electricity markets and offshore wind generation in Great Britain and The Netherlands. The base capacity of the cross border interconnection is around 2GW, but more can be considered. | National Grid TENNET-NL | GB ;NL |  | 2030 | 1 | True | False |  | New | True | 1.16 |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | e.g. can ramp quickly to meet system needs | United Kingdom - Netherlands | 2000 | 2000
262 | Belgium-Netherlands: Zandvliet-Rilland | Bilateral study has assessed multiple reinforcement options. The study concluded that an upgrade of the existing corridor Zandvliet-Rilland via the installation of two additional PSTs in Zandvliet and the upgrade of Zandvliet-Rilland line to high capacity conductors is the most appropriate solution. The constuction of the substation Rilland is part of TenneT's project ""Zuid-West 380"", id 346. Project motivation: A need has been identified during TYNDP16 and TYNDP18 to develop additional interconnection capacity between Belgium and The Netherlands. This project effectively increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This project has an important adequacy contribution due to decreasing figures of installed conventionals (bad market conditions) and especially in light of the nuclear phaseout. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. PSTs will also help to balance the flows over the different cross border lines of the Belgian Dutch interconnection.Based on the above, the project directly contributes to the interconnection criteria 2030. | ELIA TENNET-NL | BE ;NL | NDP1, Belgium, 2020-2030, §4.2.2.1 | 2022 | 4 | True | False |  | New | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This project has an important adequacy contribution due to decreasing figures of installed conventionals and considering the nuclear phaseout in Belgium. The installation of phase shifting transformers will help to balance the flows over the different cross border lines on the Belgian-Dutch border. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | The Netherlands - Belgium | 1000 | 1000
263 | Lake Constance East | This project increases the capacity between CH and its neighbours DE and AT. This enables to connect large renewable generation in Northern Europe to consumers and pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. | SWISSGRID VUEN | AT ;CH ;DE | https://www.swissgrid.ch/dam/swissgrid/projects/strategic-grid/sg2025-technical-report-de.pdf , Switzerland, 2015 - NDP VUEN, Austria, NDP Nr. 4/2019, 16, http://www.vuen.at/ | 2035 | 1 | True | False |  | MostlyNew | False |  | The clustering of investments Rüthi - Bonaduz/Mettlen and Vorarlberg enables to show the full benefit of both investments (one investment cannot perform its intended function without the realization of the other investment). | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to lowering the price differentials between Switzerland on the one hand and Germany and Austria on the other hand. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | Austria - Switzerland Switzerland - Germany Austria - Germany | 100 600 1000 | 200 250 1000
264 | Swiss Roof I | This project increases the capacity between CH and its neighbours DE, AT and IT. This enables to connect large renewable generation in Northern Europe to pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. | SWISSGRID | CH | https://www.swissgrid.ch/dam/swissgrid/projects/strategic-grid/sg2025-technical-report-de.pdf , Switzerland, 2015, page 155 | 2035 | 3 | False | True |  | MostlyNew | False |  | The investments of the Swiss Stategic Grid 2025 that chiefly contribute to increasing the cross-border capacity with Germany and Austria are clustered in the project Swiss Roof I. | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to lowering the price differentials between Switzerland on the one hand and Germany and Austria on the other hand. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | Austria - Switzerland Switzerland - Germany Switzerland - Italy | 400 1500 200 | 400 1500 0
265 | Tessin | Reinforcement of the infrastructure in canton Tessin. | SWISSGRID | CH | https://www.swissgrid.ch/dam/swissgrid/projects/strategic-grid/sg2025-technical-report-de.pdf , Switzerland, 2015, page 122 | 2035 | 2 | False | True |  | MostlyNew | False |  | Infrastructure located in canton Tessin. | False | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | Switzerland (Internal) | 200 | 200
266 | Swiss Ellipse I | The project helps accommodate new pump storage units which mainly support the increasing RES generation in the European areas with solar and wind generation and increase the DE-CH NTC. | SWISSGRID | CH | https://www.swissgrid.ch/dam/swissgrid/projects/strategic-grid/sg2025-technical-report-de.pdf , Switzerland, 2015, page 148 | 2029 | 3 | False | True |  | MostlyNew | False |  | The investments of the Swiss Stategic Grid 2025 that chiefly contribute to accommodating the new pump storage units in the Swiss Alps are clustered in the project Swiss Ellipse I. | True | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to reduce price differentials between EU and/or non-EU countries | This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. This project contributes to lowering the price differentials between Switzerland on the one hand and Germany on the other hand. | Switzerland - Germany | 800 | 800
267 | Hansa PowerBridge II | Possible second HVDC cable interconnector between southern Sweden (Bidding area SE4) and Germany (50Hertz). This project candidate is driven by market based target capacities found in the Common Planning Studies by Regional Group Baltic Sea. | Svenska Kraftnät 50HERTZ | DE ;SE | NEP2030, Germany, version 2019, page 527 https://www.netzentwicklungsplan.de/sites/default/files/paragraphs-files/NEP_2030_V2019_2_Entwurf_Teil2.pdf | 2035 | 1 | True | False |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The main driver is market integration of the Nordic hydro/nuclear/RES dominated system with the German thermal/RES based system. The infrastructure will reduce price differentials between EU countries. The system adequacy is enhanced in Germany which will increase the import potential in period of low wind and solar generation. Also the system adequacy in southern Sweden is enhanced since it given more import capacity in a future with less available nuclear generation capacity. Increase of RES in both countries leads to higher need for trade with high surplus during high wind power production. Flows are to be balanced with southbound flow during peak hours and when hydro inflow in Sweden are high and northbound in periods of high German RES generation by night | Germany - Sweden | 700 | 700
270 | FR-ES project -Aragón-Atlantic Pyrenees | This project consist of a new HVDC interconnection between France and Spain located in the Central part of the Pyrenees between Aragón region (Spain) and Marsillon (France). Internal AC reinforcements in Spain complement the cross border section, in order to connect the new converter station to the existing network. This project was included in the 2015 and 2017 PCI list (PCI 2.27.1) | Red Eléctrica de España RTE | ES ;FR | French NDP, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), France, 2019, project n°1039, page 442, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035, Spanish NDP, Spain, 2015-2020, in tables in Annex II, page 6 as Ejea de los Caballeros-French Border. Definition of the project has evolved since the publication of the last NDP towards the current definition in this TYNDP. | 2030 | 2 | True | False | Explanation of the project benefits The project helps to integrate RES generation of the Iberian Peninsula: it mainly allows to replace nuclear in France by RES generation that would have been curtailed without the project. It sometimes also helps to decrease thermal generation in Spain and Portugal and farther in Europe substituting it by available RES. This leads to a considerable reduction of the total generation costs (SEW) in all scenarios. Furthermore SEW benefits are higher in 2040 horizon after nuclear phase out in France (see IoSN report). When analyzing the results of the different scenarios studied, it can be concluded that the higher the penetration of RES in the Iberian Peninsula, especially solar generation, the higher the SEW of the project is. Thus, the SEW is the lowest in scenarios NT 2025 and CT 2030, and the highest in scenario DE 2030. These scenarios frame the results of scenarios NT2030 and GA2030 in terms of SEW results. The TYNDP 2018 showed greater benefits. Indeed, the scenarios used at that time corresponded to a more ambitious objective of nuclear phase-out in France and the French nuclear installed capacity was therefore much lower. Thus, the avoided curtailed energy in the Iberian Peninsula, instead of replacing cheap French nuclear generation, replaced a much larger share of thermal generation. Additionally the Spanish thermal capacity in TYNDP 2018 scenarios was greater than the one considered in these new scenarios in which the forecasted gradual closure of coal-fired power plants is considered. The project shows a significant contribution to avoid ENS: the SOS indicator shows that this interconnection project gives large benefits to use existing thermal generation in the Iberian Peninsula to avoid potential ENS in Western Europe. In addition, an increase of transfer capacity between Iberia and the rest of Europe would improve the system security and its robustness from the dynamic point of view. Amount of losses are quite high as the project allows higher long transit power flows on long distances in order to supply the demand with the cheapest generation available through Western Europe. These results are aligned in volume (MWh) with TYNDP 2018. Nevertheless, the cost of losses are significantly lower due to particularly low marginal costs in France and Spain in NT2030 scenario. Navarra-Landes project reduces the congestion rate in a range from 11 to 12% in NT 2030 scenario, depending on the climate year. Nevertheless after the commissioning of the project the congestions are limited to 48-56%. Aragón-Atlantic Pyrenees project reduces the congestion rate in a range from 11 to 12% in NT 2030 scenario, depending on the climate year. Nevertheless after the commissioning of the project the congestions are limited to 48-56%. Disclaimer: Preliminary studies show that a number of internal reinforcements could be necessary on both sides of the border to reach the net transfer capacity targets of 6500 and 8000 MW which are the main NTC objectives of projects 276 and 270 respectively. REE and RTE should further develop a thorough joint study in order to design more precisely these reinforcements, to assess the appropriateness and relevance of clustering some of these reinforcements with projects 270 or 276, and thus make their economic analysis more robust, and also to define how to optimize the distribution of flows between east and west of the border by better adjusting the HVDCs set points, which could have a high impact on the overall NTC. All the needed internal reinforcements will have to be coordinated with internal energy transition objectives, which will require further analyses and review of the benefits, costs, and social and environmental impacts. How the project fits to the regional trends: This project helps to integrate the Iberian Peninsula in a full-integrated European internal energy market, as it reduces its historical electric isolation (Spain won't yet fulfill the 10% objective for 2020 in spite of the strong technical and political efforts, as Spain would still be a range of 6-7%. This project also helps to integrate the high RES potential in the Iberian Peninsula. In addition, it also contributes to the security of supply, not only regarding adequacy (especially in tight situations), but also regarding flexibility and stability of the system. | New | True | 2.27.1 |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The IoSN report show high price differentials in FR-ES that would be reduced with a project in this border. IoSN report shows that for the 2040 time horizon there is need for developing projects in the French-Spanish border. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchanges between France and the Iberian Peninsula. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity in ES-FR. | Spain - France | 1500 | 1500
276 | FR-ES project -Navarra-Landes | This Project consist of a new HVDC interconnection between France and Spain in the Western part of the Pyrenees between Pamplona area (Spain) and Cantegrit (France). The project is considered as an HVDC project of 2x1000 MW. Internal reinforcements complement the cross border section. This project was included in the 2015 and 2017 PCI list (PCI 2.27.2) | Red Eléctrica de España RTE | ES ;FR | French NDP, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), France, 2019, project n°1039, page 442, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 Spanish NDP, Spain, 2015-2020, in tables in Annex II, page 18 as Muruarte-French Border. Definition of the project has evolved since the publication of the last NDP towards the current definition in this TYNDP. | 2029 | 2 | True | False | Explanation of the project benefits: The project helps to integrate RES generation of the Iberian Peninsula: it mainly allows to replace nuclear in France by RES generation that would have been curtailed without the project. It sometimes also helps to decrease thermal generation in Spain and Portugal and farther in Europe substituting it by available RES. This leads to a considerable reduction of the total generation costs (SEW) in all scenarios. Furthermore SEW benefits are higher in 2040 horizon after nuclear phase out in France (see IoSN report). When analyzing the results of the different scenarios studied, it can be concluded that the higher the penetration of RES in the Iberian Peninsula, especially solar generation, the higher the SEW of the project is. Thus, the SEW is the lowest in scenarios NT 2025 and CT 2030, and the highest in scenario DE 2030. These scenarios frame the results of scenarios NT2030 and GA2030 in terms of SEW results. The TYNDP 2018 showed greater benefits. Indeed, the scenarios used at that time corresponded to a more ambitious objective of nuclear phase-out in France and the French nuclear installed capacity was therefore much lower. Thus, the avoided curtailed energy in the Iberian Peninsula, instead of replacing cheap French nuclear generation, replaced a much larger share of thermal generation. Additionally the Spanish thermal capacity in TYNDP 2018 scenarios was greater than the one considered in these new scenarios in which the forecasted gradual closure of coal-fired power plants is considered. The project shows a significant contribution to avoid ENS: the SOS indicator shows that this interconnection project gives large benefits to use existing thermal generation in the Iberian Peninsula to avoid potential ENS in Western Europe. In addition, an increase of transfer capacity between Iberia and the rest of Europe would improve the system security and its robustness from the dynamic point of view. Amount of losses are quite high as the project allows higher long transit power flows on long distances in order to supply the demand with the cheapest generation available through Western Europe. These results are aligned in volume (MWh) with TYNDP 2018. Nevertheless, the cost of losses are significantly lower due to particularly low marginal costs in France and Spain in NT2030 scenario. Navarra-Landes project reduces the congestion rate in a range from 11 to 12% in NT 2030 scenario, depending on the climate year. Nevertheless after the commissioning of the project the congestions are limited to 48-56%. Aragón-Atlantic Pyrenees project reduces the congestion rate in a range from 11 to 12% in NT 2030 scenario, depending on the climate year. Nevertheless after the commissioning of the project the congestions are limited to 48-56%. Disclaimer: Preliminary studies show that a number of internal reinforcements could be necessary on both sides of the border to reach the net transfer capacity targets of 6500 and 8000 MW which are the main NTC objectives of projects 276 and 270 respectively. REE and RTE should further develop a thorough joint study in order to design more precisely these reinforcements, to assess the appropriateness and relevance of clustering some of these reinforcements with projects 270 or 276, and thus make their economic analysis more robust, and also to define how to optimize the distribution of flows between east and west of the border by better adjusting the HVDCs set points, which could have a high impact on the overall NTC. All the needed internal reinforcements will have to be coordinated with internal energy transition objectives, which will require further analyses and review of the benefits, costs, and social and environmental impacts. How the project fits to the regional trends: This project helps to integrate the Iberian Peninsula in a full-integrated European internal energy market, as it reduces its historical electric isolation (Spain won't yet fulfill the 10% objective for 2020 in spite of the strong technical and political efforts, as Spain would still be a range of 6-7%. This project also helps to integrate the high RES potential in the Iberian Peninsula. In addition, it also contributes to the security of supply, not only regarding adequacy (especially in tight situations), but also regarding flexibility and stability of the system. | New | True | 2.27.2 |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The IoSN report show high price differentials in FR-ES that would be reduced with a project in this border. IoSN report shows that for the 2040 time horizon there is need for developing projects in the French-Spanish border. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchanges between France and the Iberian Peninsula. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity in ES-FR. | Spain - France | 1500 | 1500
280 | FR-BE: study Lonny-Achene-Gramme | The project aims at sustaining further market integration within the long-term perspective of the energy transition and subsequent need to develop interconnection capacity on the French-Belgium border whilst alleviating Lonny-Achene-Gramme as bottleneck.The reinforcement strategy consists of maximizing the potential of the 400kV interconnector Lonny-Achene-Gramme through the use of cost-efficient technologies such as PSTs and HTLS as well as the possibility to rebuild Lonny-Achene-Gramme as a 2-circuit solution. The bilateral study will determine the appropriate implementation option and phasing of this implementation (for example: first install a PST, then upgrade the line capacity), taking into account 1) the optimization of flows between the 400kV interconnectors Avelin-Avelgem-Horta & Lonny-Achene-Gramme 2) that by 2025 Lonny-Achene-Gramme is a structural bottleneck due to the planned nuclear phase out in Belgium, and as such a first implementation step (for example PST) is needed 3) gain in efficiency in developing a structure with 2 circuits versus current structure with 1 circuit on Lonny-Achene-Gramme Project motivation: With this project RTE and Elia investigate the possibilities to further develop interconnection capacity on the FR-BE border, in line with the signals provided by the 2030 interconnection target criteria as well as the identification of needs upon 2040 scenario's, illustrating that higher power flows will emerge from future production mixes with more RES. This project fits within the strategy to develop cost efficient upgrades of the existing AC interconnectors in the CWE area. | ELIA RTE | BE ;FR | NDP1, Belgium, 2020-2030, §4.2.2.2 - NDP2, France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), 2019, project n°1050, page 442, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 | 2030 | 1 | True | False |  | MostlyUpgrade | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between Belgium and France. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours yearly and reduces therefore the price differentials. This is also included as key trigger of the 2030 interconnection criteria. Based on IOsN report, 15% IC-target requires higher cross border transmission capacity. This project contributes to satisfy this need, provided that the project benefits outweigh its costs. With the potential use of PSTs to better balance flows between the different crossborders lines, it will reduce bottlenecks and consequently increase the exchanges on the boundary itself and also in CWE area. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | Belgium - France | 1000 | 1000
283 | TuNur | TuNur aims at connecting to the European electricity network a Concentrated Solar Power (CSP) plant with storage and an overall capacity in excess of 2000 MW to be located in Rejim Maatoug, Kebili, Tunisia. The connection point to ENTSO-E’s network is located in Montalto di Castro, North of Rome, Italy. The transmission project will consist in a +/- 500 kV DC overhead line in Tunisia spanning from the power plant to the shoring point, submarine cables from the Tunisian Northern coast to Montalto di Castro, VSC HVDC converter stations at both terminal points, and short 400 kV AC cables from the HVDC converter in Montalto to Terna’s 400 kV station. No sea electrode is foreseen. | TuNur Ltd | IT ;TN | The project is mentioned in the Italian “Piano di Sviluppo”, Terna S.P.A. E Gruppo Terna of 2019 at page 167. There is no project number allocated to the project. The development plan can be found at: https://download.terna.it/terna/0000/1188/36.PDF | 2026 | 1 | True | False | Regarding B6 – Security of Supply Italian power system has been identified as no-adequacy issue system during the 2030 NT Scenario SoS check. This means that the system already reached the adequacy standards in the base case (without a project), therefore the project cannot have contribution in this sense. | New | False |  | To connect to Terna’s grid, the main investment (DC cable) requires a short AC cable. The AC cable has no standalone purpose without the main investment. | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | The TuNur project will contribute to improving market integration and reducing price differentials between EU and non-EU countries by providing an additional 2000 MW of low cost and low carbon available capacity, through a new connection between a non-EU (Tunisia) and EU (Italy). TuNur will provide dispatchable low-carbon power, thereby mitigating the risk of power failure, and will contribute to system adequacy deficiencies by increasing transmission capacity. This power source will improve security of supply by reducing Loss of Load durations across EU networks, making a significant contribution to system stability The TuNur project will significantly contribute to system flexibility through direct access to a new source of renewable energy. TuNur will also contribute to system stability by improving transient stability and helping to meet RoCoF system needs. TuNur will provide flexible power with black-start capacity. TuNur consists in infrastructure that will contribute to balancing flexibility by providing the European network with a new source of low-carbon dispatchable power. Additionally, the TuNur project will deliver a 2000 MW power reserve through a new HVDC interconnection between Tunisia and Italy. | Italy - Tunisia | 2000 | 2000
284 | LEG1 | LEG1 is a submarine HVDC interconnection project, enabling bidirectional electricity exchange between South-East Europe and North Africa. The interconnector will link the area of Tobruk, in Libya, to Linoperamata in Crete. Landing spots have been discussed with the respective TSOs. GreenPower2020 has identified an ideal submarine corridor (305 km) reaching a maximum depth of 2700m, providing one of the shortest possible links between continental Europe and North Africa, as Crete will be connected to continental Greece with a 1,000 MW DC interconnector in 2023. LEG1 interconnector will have a power rating of 2,000 MW and a DC voltage of 525 kV. VSC was chosen for converter technology because it is more favorable for power trading and has other advantages such as blackstart capacity and voltage stability support. LEG1 will also connect Libya to Egypt (Salloum) through AC overhead line with related substations, benefiting from Libya and Egypt solar projects (initial 150 MW plant included), further contributing to the achievement of the EC’s Green Deal 2030 objectives. It will play an essential role in optimizing competitive production and consumption, taking advantage of the strong weekly and seasonal imbalances - Fridays vs Sundays / winters vs summers | GreenPower 2020 | EG ;GR ;LY |  | 2025 | 1 | True | False |  | New | False |  |  | False | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure designed to offer more supply options to isolated areas Capability for Black Start & Islanding Operation | Sustainability: The project offers a connection to additional renewable energy on the southern side of the Mediterranean Sea, supporting the EU goal of Climate Neutrality by 2050. Provides also a mean for evacuation of excess of electricity in periods of high generation and low demand Voltage stability of the system: VSC converters can be used to support the grid by mixing active and reactive power during stressed conditions Security of supply: The link will provide enhanced security of supply for the island of Crete, which is in the process of decarbonizing its electrical generation. | Greece - Lybia | 2000 | 2000
285 | GridLink | 1.4 GW HVDC electricity interconnector between UK and France Voltage Source Converter (VSC) Grid connection point (substations name): Kingsnorth (UK) and Warande (France) Total cable length (substation to substation) 160km (112km in UK and 48km in France) Two cables (MI) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load Annual Availability: 98% availability, 2% planned outages, 0% forced outages. Maximum single failure according to the design: 1.4GW UK Transmission network reinforcement required: Uses spare bay with minimum works at Kingsnorth substation France transmission network reinforcement: Extension to Warande substation Main environmental impact: reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. No material environmental impacts during construction and operation. | Elan Energy Ltd National Grid RTE Nationalgrid ESO | FR ;GB | 2016 2018 TYNDP, RTE’s 2018 Schéma décennal de dévelopement du réseau and National Grid ESO Electricity Ten Year Statement 2018 (Appendix H) | 2024 | 3 | True | False |  | New | True | 1.7.5 |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment |  | France - United Kingdom | 1400 | 1400
286 | Greenlink | An electricity interconnector between Ireland and Wales, Greenlink brings significant benefits on both sides of the Irish Sea for energy security and the integration of renewable low carbon energy sources. For Ireland, it provides a natural link to the EU and Nordic electricity markets via Wales, England and Scotland. Greenlink will employ proven HVDC technology and is similar to the successful East West Interconnector between North Wales and Ireland. The cable route will run from existing substations in Great Island, Co. Wexford and Pembrokeshire in Wales connecting EirGrid and National Grid power systems. It is unobtrusive, being underground subsea cables with a converter station located at each connection point. Both Ireland and the UK have stated their support for increased interconnection and its strategic benefits. | Element Power Statkraft | GB ;IE | National Grid’s Electricity Ten Year Statement 2018 in Appendix C Figure C4: https://www.nationalgrideso.com/document/133191/download | 2023 | 3 | True | False |  | New | True | 1.9.1 |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment |  | United Kingdom - Ireland | 500 | 500
293 | Southern Aegean Interconnector | The project refers to the construction of a submarine DC transmission link to connect the licensed RES plants, located on 23 small uninhabited islands at the South Aegean sea, with mainland Greece and the islands of Crete, Kos and the Dodecanese. The main link will be an HVDC link connecting the island of Levitha to both the metropolitan area of Athens and the island of Crete; the 400kV substation at Lavrion area will be the connection point in the Athens area and the substation of Atherinolakkos will be the connection point in Crete (located in the South-East coast). The capacity of each link will be 600 to 800MW both directions using HVDC (High Voltage Direct Current) XLPE insulated technology and both links will consist of two parallel cables in order to increase the reliability of each link. 3 conversion stations using HVDC VSC technology are foreseen in Lavrio, Levitha & Crete (Atherinolakkos). All the installations on the islands (converter stations, substations etc) will be of closed type using GIS technology. The project will provide 19TWh/year of wind energy, increasing the transfer capacity between mainland Greece and Crete-Kos islands. | Kykladika Meltemia SA | EG ;GR | Not in a NDP yet. | 2025 | 1 | False | True |  | New | False |  | The clustering explanation is that the whole project refers to the construction of one common submarine DC transmission link to connect the licensed RES plants at the South Aegean Sea to mainland Greece and the islands of Crete, Kos and the Dodecanese. The main link will be an HVDC link connecting the island of Levitha to both the metropolitan area of Athens and the island of Crete. | False | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure designed to offer more supply options to isolated areas Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | Currently non-interconnected islands face significant RES curtailments, as the conventional units available in each island do not meet the flexibility requirements in view of adapting to the RES generation profile. Such curtailments will be significantly reduced when the project is implemented. More the project will facilitate the cost efficient grid connection of the under development Wind Turbine Plants (approx. 600 MW installed power) with mainland Greece. The supply of currently non interconnected autonomous islands will be enhanced with via the development of Southern Aegean Interconnector. The increased RES (Wind Turbine) capacity penetration provided with the development of Southern Aegean Interconnector shall lead to significant enhancement of System Adequacy (LOLE & LOEE decrease). | Internal (Greece) | 582 | 582
296 | Britib | EU Priority Corridor: NSI West Electricity. Category: Electricity Highway. Acronym: Bretagne-Britain-Iberia (BritIb). Interconnection project between South-West England (United Kingdom), Cordemais (France) and Basque Country (Spain) in a multiterminal HVDC configuration of 525-600 kV with 3 inputs/outputs of 1800 MW each, and a mostly subsea route from Spain to Great Britain along the French coast of about 1330 km in total. The project’s development started in 2009 and is aligned with the EU Parliament priorities established in EU Regulation 347/2013 (Annex I): NSI West Electricity corridor (2) and e-Highways area (11). The Britib project was included in TYNDP 2014, 2016 and 2018. | ACS Cobra | ES ;FR ;GB | The project is not included in a National Development Plan. | 2026 | 1 | True | False |  | New | False |  |  | False | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) | Design with VSC technology allows use of physical capacity for balancing services to be shared and mutual help in case of major incidents for grids’ operation. UK, ES and FR seriously affected by worst 9h power ramps (9-5 GW/h) (Contribues with system flexibility and stability) Linking areas with high share of intermittent renewables between them and EU Central grid (FR). High complementarity enables solar power mostly from ES-PT towards Northern Europe (UK) in summer and significant exchange of wind power between N. . Sea region/ France and SP-PT | France - United Kingdom Spain - France Spain - United Kingdom | 1800 1800 1800 | 1800 1800 1800
297 | BRABO II + III | Realization of a new 380 kV corridor between Zandvliet and Mercator consisting of a double-circuit AC overhead line, including a new substation 380kV in Lillo. Project motivation: BRABO II and III sustain the development of interconnection capacity on the Belgian North Border towards a broader scenario framework, hereby securing the supply of electricity around the Antwerp harbour area in light of the increasing industrial demand (mainly applicable to BRABO II), as well as developing capacity for the potential integration of new production in the Antwerp area (mainly aplicable to BRABO III). This project contributes to resolving internal congestions, considering expected high international transit & loop flows. This project increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials.This project allows to deal with the growth in industrial consumption from the Antwerp harbour and to increase the grid hosting capacity for connection of new production capacity, thereby contributing to the overall adequacy of the system, especially relevant considering the nuclear phase out in Belgium.RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | ELIA | BE | NDP1, Belgium, 2020-2030, p.193, ID 29-and 32 | 2025 | 3 | False | True |  | New | True | 2.23 |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This project allows to deal with the growth in industrial consumption from the Antwerp harbour and to increase the grid hosting capacity for connection of new production capacity, thereby contributing to the overall adequacy of the system, especially relevant considering the nuclear phase out in Belgium. This project contributes to resolving internal congestions, considering expected increased market exchanges inducing higher flows. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | Belgium - Netherlands | 1000 | 1000
299 | SACOI3 | New HVDC line between Italy mainland, Corsica and Sardinia replacing existing link SACOI2. Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. The project will allow the increase of the energy flows among Sardegna - Corsica and Italy mainland via 400 MW of additional capacity. In addition, the project contributes with +100MW between Corsica and Italy, but this contribution was not considered in the project sheets, neither in the assessment of this project. | TERNA EDF | FR ;IT | Avanzamento Piani di Sviluppo precedenti 2015/Pag.436, Italy | 2024 | 3 | True | False | About B6 - Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served monetised): In Italy a different parameter is used for the monetization of the Expected Energy Not Served (EENS) variation due to this project, because the current parameter used by ENTSOE in this project sheet (10 k€/MWh) is not compliant with National regulations in force in Italy n°627/2016 (“Minimum Requirements for the preparation of the Ten Year Development Plan of the National Transmission Network” according to which benefits related to reduction of EENS is monetized through a Value of Lost Load (VOLL) in a range between 20 k€/MWh and 40 k€/MWh. | Upgrade | True | 2.4 |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | This project contributes to lowering the price differentials between Italian market zones and Corsica This project will improve the integration of italian RES generation This project will contribute to overcome flexibility/stability problems due to scarsely meshed grid This project helps Italy to reach the 15% interconnection target by 2030 | Internal (Italy) | 400 | 400
309 | NeuConnect | NeuConnect will be the first subsea HVDC electricity Interconnector to connect the UK and German electricity markets. It will be approximately 700km long with a capacity of 1.4GW. This large capacity Interconnector has the advantage of accelerating the European wide ambition to create a single, competitive and efficiently driven electricity market for the benefit of consumers. | NeuConnect Britain Limited NeuConnect Deutschland GmbH | DE ;GB | Germany - Bedarrfsermittlung 2019-30 Measure M534 Fedderwarden – Großbritannien (NeuConnect) Leitung United Kingdom - National Grid “Network Options Assessment 2019/20 - Section 5 and NeuConnect appears in the Interconnectors Connection Register www.nationalgrideso.com/connections/registers-reports-and-guidance | 2022 | 3 | True | False |  | New | True | 1.20 | NeuConnect is an Independent Interconnector and not connected to any other transmission project. | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | ENTSO-E’s Socio Economic Welfare benefit study indicates an average of between 29 and 75 MEur/Yr. Our own modelling suggests that Germany produces around 400GWh of additional renewable electricity in 2030 and an additional 1,200 GWh in 2035 compared to the scenario without NeuConnect. This additional renewable generation displaces GB thermal generation ENTSO-E’s assessment indicates an average avoided curtailment of between 362 and 1183 GWh/annum. Our own studies indicate curtailment of German renewable sources is reduced between 0.4 and 2.22TWh between 2030 and 2045. | Germany - Untied Kingdom | 1400 | 1400
312 | St. Peter (AT) - Tauern (AT) | This project is part of the Austrian 380-kV security ring. It therefore provides based on the concept a redundant and robust connection and increases security of supply significantly. In addition higher transport capacities are able to connect RES production in the corners of the region with the Alpine storages and therefore integrate both efficiently and properly. | Austrian Power Grid | AT | APG Netzentwicklungsplan 2019, AT, 2019, 11-10, 48, https://www.apg.at/de/Stromnetz/Netzentwicklung | 2035 | 4 | False | True |  | New | True | 3.1.2 |  | True | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | Interconnection between huge amounts of RES and storage capacity in the Alps helps to reduce the amount of RES curtailment significantly facilitates interconnection capacity Interconnection between huge amounts of RES and storage capacity in the Alps provides flexibility and stability. | Internal (Austria) | 2000 | 2000
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | New 380kV Line between TenneT-DE and APG (Isar/Altheim/Ottenhofen - St. Peter). This project reinforces the interconnection capacity between Austria and Germany. It supports the interaction of RES in Northern Europe (mainly in Germany) and in the eastern part of Austria with the pump storages in the Austrian Alps and therewith facilitates their utilisation. | Austrian Power Grid TenneT DE | AT ;DE | DE: NEP2030 v2019; APG Netzentwicklungsplan 2019, AT, 2019, 11-7, 48, https://www.apg.at/en/Stromnetz/Netzentwicklung | 2035 | 3 | True | False |  | New | True | PCI 3.1.1 |  | True | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | helps to reach 15% target in Germany high RES generation connected to pump storage high RES generation connected to pump storage | Austria - Germany | 2000 | 2000
320 | Slovenia-Hungary/Croatia interconnection | The project consists of a new 80km double circuit 400kV OHL in Slovenia (section Cirkovce-Pince) and a new 400 kV substation of Cirkovce(SI). The new double 400 kV overhead line will be connected to one circuit of the existing double circuit 400kV OHL Heviz(HU)-Zerjavinec(HR). By this two new cross-border lines will be established - Heviz(HU)-Cirkovce(SI) and Cirkovce (SI)-Zerjavinec (HR). | ELES HOPS MAVIR | HR ;HU ;SI | A Magyar Villamosenergia-rendszer Hálózatfejlesztési Terve 2017., Hungary, 2017, Page 5 ; https://www.eles.si/Portals/EN/Document/ELES NDP 2019-2028.pdf?ver=2019-06-05-095251-500, Page 32, 6.2 | 2021 | 4 | True | False |  | MostlyNew | True | 3.9.1 |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | Project 320 will establish the first cross-border connection between Slovenia and Hungary, by which a new border and new transmission capacity with up to 1200 MW in both directions will be established. Project will increase market integration in the region, facilitate access to Eastern electricity markets and decrease price differentials in the region. Project 320 will increase system flexibility and stability, improve operational reliability and by this improve security of supply. This is expected also in cases of extraordinary grid events (blackouts, extreme weather events, outages of major generation units or other unforeseen events) where the Project will assure important new and reliable transmission capacity to overcome such problems. Furthermore, project is also essential for successful completion of smart grid project SINCRO.GRID, which will, jointly with project 320 regionally assure regional voltage regulation and regional voltage stability and thus system stability. In future scenarios production from RES sources will increase greatly, having also an influence on the power flows. Project will significantly increase transmission capacities and assure a higher level of security of supply, by which a positive effect on accomodation of power flows from new RES generation will be possible and in essence an increase of the amount of new RES integration. By realization of Project 320, also smart grid project SINCRO.GRID (PCI 10.3) will be completed, by which the level of regional system stability will be raised, having a direct effect on increased integration of additional RES generation in this region. With the project the first connection between Slovenia and Hungary will be established. By this reserve sharing will be possible, this demontrasted also in scope of project FutureFlow. | Hungary - Slovenia Slovenia - Croatia | 1200 0 | 1200 150
322 | Wullenstetten - Border Area (DE-AT) | Between point Wullenstetten and point border area (DE-AT) as well as between Herbertingen and Point Neuravensburg, an upgrade of an existing 380-kV-line is necessary (grid enhancement). Furthermore, between switching point Neuravensburg and Austrian National border (AT) a new line with a significantly higher transmission capacity will be constructed in an existing corridor (grid enhancement). Thereby, a significantly higher transmission capacity is realized. | AMPRION VUEN | DE | NDP1, Germany, Netzentwicklungsplan 2030 Version 2019, Project 52, p. 445 | 2025 | 2 | False | True | According to the CBA indicators for the scenarios NT2025 and NT2030 the project has only a small impact which is not positive for all indicators. The reason for this is the fact that the project is only one fragment preparing the German side of the grid for project 263 (Lake Constance East) which foresees a complete restructuring of the grid in the area around Lake Constance. The joint projects will increase the transmission capacity between Germany and Austria even more and therefore the whole effect of the project will only show significantly in combination with project 263. | Upgrade | False |  |  | False | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project increases the German interconnection level to Austria. The project helps connecting German RES power with pump storages in Austria and therefore improves the accomodation of flows. | Internal (Germany) | 0 | 0
323 | Dekani (SI) - Zaule (IT) interconnection | The Zaule (IT) - Dekani (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E3, ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o.. and Holding Slovenske Elektrarne d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Zaule (IT) substation to Dekani (SI) substation, including a 110/135 kV Phase Shifter Transformer. | HSE d.o.o. (Holding Slovenske Elektrarne, d.o.o.) E3 d.o.o. (ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o) Adria Link Srl | IT ;SI | The Italian TSO "Terna" stated in its NDP 2019 to include only merchant line projects exempted under the European Regulation and with a signed connection agreement. The Dekani (SI) - Zaule (IT) interconnection project obtained exemption pursuant to Reg. (EC) 714/2009 but has not yet signed a connection agreement. For this reason, this projects is not included in its NDP. Terna mentions the project in table n. 165 on page 162 of the NDP 2019 (https://download.terna.it/terna/0000/1188/36.PDF). | 2021 | 3 | True | False | Regarding NTC increases: 1. The values indicated by the TSOs Terna and Eles in the “Transfer Capacity Increase” fields do not respect the methodology and calculations of the TYNDP 2020 CBA - ENTSO-E Guidelines. The TSO calculation considers its own studies (different methodology), with different network, load, generation and network scenarios (different database than ENTSO-E); 2. The values indicated by the TSOs Terna and Eles in the “Transfer Capacity Increase” fields are not consistent with the purpose of the project sheet. The paragraph expressly refers to the National Trend scenario in 2025, while the evaluation of the TSOs is based not only on different scenarios, but also on different time horizons (network scenario, generation and load in 2019 specifically). Furthermore, the 2025 evaluation carried out by the TSOs is based on a partial update of the 2019 network model. In particular the NTC value at 2025 is evaluated as the minimum value calculated by Eles with reference scenario at 2025 and Terna with reference scenario at 2019. Adria Link Srl, taking into account the assumption indicated above, expresses concerns about the correctness of the note reported by the TSOs and about its coherence with the overall project sheets. | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to offer more supply options to isolated areas | The Project will enhance the interconnection capacity between the interconnected Countries and will allow a progressive alignment of the Italian border price differentials also in line with the interconnection target recommendations (Nov 2017) by EC Expert Group. The project will enhance the adequacy of the interconnected systems in the mid/long-term scenarios. In particular, it improves the share of the renewable energy sources and new flexible thermal generation in the electricity systems. The Project contributes to increase the Italian cross-border capacity in the medium-long term objectives (2030) as also reported in the Italian Implementation Plan for the requirements set in article 20 of Regulation 2019/943 of 5th June 2019 on the Internal Electricity Market (IEM). Considering that the Italian Peninsula is one of the most European isolated area, the Project will increase the Italian cross-transfer capacity contributing to reduce the gap with the other European Countries. | Italy - Slovenia | 125 | 125
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | "The Redipuglia (IT) - Vrtojba (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E 3, ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o. and Holding slovenske elektrarne d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Redipuglia (IT) substation to Vrtojba (SI) substation, including a 110/135 kV Phase Shifter Trasformer." | HSE d.o.o. (Holding Slovenske Elektrarne, d.o.o.) E3 d.o.o. (ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o) Adria Link Srl | IT ;SI | The Italian TSO "Terna" declared in its NDP 2019 that it includes only merchant line projects exempted and with a connection agreement signed. The Redipuglia (IT) – Vrtojba (SI) interconnection project has a connection agreement signed but it has not yet obtained the exemption under the Reg. (CE) 714/2009. For this reason these projects are not included in its NDP. Terna mentions the project in the table n. 165 at page 162 of the NDP 2019 (https://download.terna.it/terna/0000/1188/36.PDF) | 2021 | 3 | True | False | Regarding NTC increases: 1. The values indicated by the TSOs Terna and Eles in the “Transfer Capacity Increase” fields do not respect the methodology and calculations of the TYNDP 2020 CBA - ENTSO-E Guidelines. The TSO calculation considers its own studies (different methodology), with different network, load, generation and network scenarios (different database than ENTSO-E); 2. The values indicated by the TSOs Terna and Eles in the “Transfer Capacity Increase” fields are not consistent with the purpose of the project sheet. The paragraph expressly refers to the National Trend scenario in 2025, while the evaluation of the TSOs is based not only on different scenarios, but also on different time horizons (network scenario, generation and load in 2019 specifically). Furthermore, the 2025 evaluation carried out by the TSOs is based on a partial update of the 2019 network model. In particular the NTC value at 2025 is evaluated as the minimum value calculated by Eles with reference scenario at 2025 and Terna with reference scenario at 2019. Adria Link Srl, taking into account the assumption indicated above, expresses concerns about the correctness of the note reported by the TSOs and about its coherence with the overall project sheets. | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to offer more supply options to isolated areas | The Project will enhance the interconnection capacity between the interconnected Countries and will allow a progressive alignment of the Italian border price differentials also in line with the interconnection target recommendations (Nov 2017) by EC Expert Group. The project will enhance the adequacy of the interconnected systems in the mid/long-term scenarios. In particular, it improves the share of the renewable energy sources and new flexible thermal generation in the electricity systems. The Project contributes to increase the Italian cross-border capacity in the medium-long term objectives (2030) as also reported in the Italian Implementation Plan for the requirements set in article 20 of Regulation 2019/943 of 5th June 2019 on the Internal Electricity Market (IEM). Considering that the Italian Peninsula is one of the most European isolated area, the Project will increase the Italian cross-transfer capacity contributing to reduce the gap with the other European Countries. | Italy - Slovenia | 20 | 120
325 | Obersielach (AT) - Podlog (SI) | Obersielach (AT) - Podlog (SI); 380-kV Upgrade; +500 MW NTC in both directions | Austrian Power Grid ELES | AT ;SI |  | 2034 | 1 | True | False |  | Upgrade | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project increases capacity of SI-AT border and decreases price difference between both markets in all future scenarios. This project will contribute to redution of system adequacy deficiencies by increasing transmission capacity on SI-AT border. This project improves the integration of RES generation into the Continental European transmission grid. | Austria - Slovenia | 500 | 500
328 | Interconnector DE-LUX | The project comprises the construction of two new 380/220-kV-substations in Germany (Aach) and Luxemburg (Bofferdange). The new substations will be connected via a new AC-link to allow a higher cross border capacity between Germany and Luxembourg. | AMPRION CREOS | DE ;LU | NDP1; Germany, Netzentwicklungsplan 2030 Version 2019, Project 406, p. 662; | 2026 | 2 | True | False |  | MostlyNew | False |  | The new AC double circuit overhead 400 kV line between Germany and Luxembourg is clustered with substation Aach (DE) and Bofferdange (LU) to secure the needed capacity and distribute the energy into lower voltage levels. The existing 220 kV OH-lines Trier-Blooren and Quint-Heisdorf will be decommissioned after the 400 kV OH lines and substations will be put in operation. | False | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. |  | Germany - Luxembourg | 1000 | 1000
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | The development of ~6 GW transport capacity through the elaboration of a new corridor in the western part of Belgium, between the Stevin axis and the Izegem/Avelgem substation. Should the corridor end in Izegem, it is to be complemented with an HTLS upgrade of the existing Izegem-Avelgem connection. Along this corridor a substation functioning as 'gateway' for the evacuation of offshore potential is envisioned. This corridor is envisioned to be implemented in AC technology following the example of the Stevin project. Timing, routing, scope, etc. subject to feasibility studies and subsequent spatial planning procedures. Project motivation: The capacity of the Stevin axis will be fully used by 2020 for the integration of the first wave of 2.3 GW offshore wind in the Belgian North Sea and Nemo Link. A further development of the 380 kV grid via a new corridor towards the coast creates the necessary perspective to unlock the energetic potential of the North Sea beyond 2020, including but not limited to the development of additional offshore wind in the Belgian part of the North sea. This new corridor will be linked to the Stevin corridor, creating a meshed 380 kV grid structure and considerably increasing the reliability. | ELIA | BE | NDP1, Belgium, 2020-2030, §4.1.5 page 10 | 2028 | 2 | False | True | The project enables the integration of the second wave of offshore wind in Belgium, as well as future cross border interconnection , RES integration and alleviation of internal congestions. The calculated benefits illustrate the facilitation of the SEW of project ID 120, but do not include another important SEW factor which is the facilitation of the cost-efficient option to connect project ID 121. | New | False |  |  | False | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to resolving internal congestions, considering expected high international flows as well as internal grid flows due to increased market exchanges. This projects foresees the installation of phase shifting transformers enabling power flow control and optimizing the use of existing infrastructure. This project creates the necessary onshore grid capacity to facilitate offshore wind development. This project will facilitate further offshore development and create grid hosting capacity for onshore and offshore RES development. | Internal (Belgium) | 6000 | 6000
330 | 4th 400kV CZ-SK interconnector | This new 400 kV cross-border overhead line between the substations Otrokovice (CZ) - Ladce (SK) will strenghten the transmission capacity between Slovak and Czech transmission systems, aiming to maintain secure operation of both transmission systems. | CEPS SEPS | CZ ;SK | Both CEPS and SEPS - This project is not included in the last approved NDP as the Energy Act requires to have in NDP only projects which are commisioned in the ten year time frame of the NDP. | 2035 | 1 | True | False |  | New | False |  | The new 400kV CZ-SK cross-border single OHL Otrokovice (CZ) - Ladce (SK) aims to increase NTC at the CZ-SK cross-border profile. The new 400kV substation Ladce (SK) is clustered with the CZ-SK cross-border line into one projects as it is directly connected into the new 400kV substation Ladce (SK). | False | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the NTC on CZ - SK profile and therefore facilitates the future need for cross-border flows and improves operational security. The project replaces the decommissioning of the two 220 kV interconnectors on the CZ - SK profile. In this way the secure operation of both transmission systems and the power exchange will be ensured. The project is aiming at facilitation of the power flows from the RES generation in the northern part of Europe and eastern part of CZ therefore promotes RES integration. | Czechia - Slovakia | 500 | 500
333 | PST Foretaille | Installation of two PSTs in Foretaille that control the flow on the Foretaille - Verbois 220 kV double line | SWISSGRID | CH | Schema decennal de development du reseau, France, 2019, page 139 https://www.rte-france.com/sites/default/files/sddr2019_rapport_complet_1.zip | 2031 | 1 | False | True |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to lowering the Price differentials between France on the one hand and Switzerland on the other hand. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | Switzerland - France | 100 | 1000
335 | Project 335 - North Sea Wind Power Hub | TenneT Netherlands, TenneT Germany, Energinet, Gasunie and Port of Rotterdam joined forces to develop a large scale European electricity system for offshore wind in the North Sea. The North Sea Wind Power Hub (NSWPH) consortium partners consider the project to be an im-portant possible alternative path of an internationally coordinated roll-out towards accom-plishing the green energy transition and achieving the Paris Agreement. Central to the vision is the construction of one or more hubs at a suitable location in the North Sea with interconnectors to bordering North Sea countries. The whole system may function as a hub for transport of wind energy, an interconnection hub to the connected countries, a working hub for offshore wind developers and a location for possible power-to-gas solutions. This project is a first building block in the hub-and-spoke concept (NSWPH) connecting up to 12 GW future offshore wind parks to the systems of Denmark, the Netherlands and Germany after 2035. Analysis by Roland Berger (commissioned by the EC) on this innovative project has shown that the hub-and-spoke concept provides significant cost savings (EUR 3.6bn over a 25year span) compared with the current, traditional, point-to-point interconnections and individual connec-tions for offshore windfarms (see Additional Information for source). An integral part of the NSWPH is to assess the perspectives of coupling large-scale wind power production with the gas system through power-to-gas (PtG) technology. The combination of cost-efficient infrastructure and the flexibility offered by the gas system may very well outweigh conversion losses, increasing the value of wind production and contribute to synergy effects through sector coupling in the transition of the energy system (see additional information). Several studies examining the benefits of PtG solutions can be found under “Additional Infor-mation”. As such the NSWPH infrastructure offers benefits by optimising integration costs of offshore wind, increasing socio-economic welfare by further coupling energy markets, supporting secu-rity of supply at wider regional level and providing potential to innovative power-to-gas con-cepts to optimise total energy system costs. | Energinet.dk TENNET-NL TenneT DE | DE ;DK ;NL | The NSWPH is not yet included in the last National Development Plans of Denmark, Germany or the Netherlands and therefore the additional internal required grid reinforcements are not yet analysed. Note that generally these plans have a shorter time horizon than 2035 (expected commissioning year of the project). In the Danish case, a future 'Strategic Investment Plan' will be developed and cover a 20-year period in which the NSWPH will be included. The NSWPH is presently analyzed in various feasibility studies at wider regional level. It builds on long-term system needs also identified in ENTSO-E’s Regional Investment Plan North Sea. Due to the strong internationally coordinated drive of this project, the concept is first addressed in ENTSO-E’s TYNDP process. In next steps it can be considered for NDP inclusion in a consistent manner. | 2035 | 1 | True | False |  | New | True | 1.19 | The North Sea Wind Power Hub investment items need to be clustered and thereby realized together to meet its full benefit. The investment items are mutually dependent on each other. Realizing one investment contributes to the realization of the full potential of another investment item. Without the Power Link Island, the concept cannot reach the same level of scale and would depend on multiple smaller configurations with higher costs. Without the wind farm connections, the configuration would merely provide interconnection while the RES integration would still require additional (radial) connections to shore. And without the interconnection links, the concept would be a single hub to shore, while missing the opportunities of market integration and sharing of reserves. Presently all investments in the NSWPH project are ‘under consideration’, with a provisional commissioning for 2035. | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The NSWPH entails deployment of new offshore wind capacity, which will be connected to European countries (NL, DK, DE). In addition, the new interconnection capacity via the hub will support the reduction of price differentials between EU countries. The infrastructure in relation to the NSWPH can accomodate future scenarios and cross-border flows, reducing the congestions in the onshore transmission system. The infrastructure in relation to the NSWPH, including combined grid connection and interconnection (and possibly large scale sector coupling) optimise large scale cost efficient integration of offshore wind. | Germany - Denmark/Netherlands | - | -
336 | Prati (IT) – Steinach (AT) | New Italy-Austria tie-line between the existing 110kV Steinach substation in Austria and 132 kV Brennero substation, including PST; and connection to 132 kV Prati di Vizze substation. Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. | TERNA Tinetz | AT ;IT | Avanzamento Piani di Sviluppo precedenti 2019, Italy, Page 139 https://download.terna.it/terna/0000/1188/42.PDF | 2023 | 4 | True | False |  | New | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian market zones and Austria. This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity. This project helps Italy reach the 10% target by 2020 and 15% target by 2030. This project will improve the integration of Italian RES generation | Austria - Italy | 90 | 90
338 | Adriatic HVDC link | New HVDC line between Villanova (or Villavalle) and Fano (or Portotolle) existing 400 kV substations (the nominal power of the link will be at least 1000 MW) | TERNA | IT | Avanzamento Piani di Sviluppo Precedenti - Volume 2, Italy, 2019, page 11 https://download.terna.it/terna/0000/1188/44.PDF | 2030 | 2 | False | True | About B6 - Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served monetised): In Italy a different parameter is used for the monetization of the Expected Energy Not Served (EENS) variation due to this project, because the current parameter used by ENTSOE in this project sheet (10 k€/MWh) is not compliant with National regulations in force in Italy n°627/2016 (“Minimum Requirements for the preparation of the Ten Year Development Plan of the National Transmission Network” according to which benefits related to reduction of EENS is monetized through a Value of Lost Load (VOLL) in a range between 20 k€/MWh and 40 k€/MWh. | New | False |  |  | False | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure | The new line will allow congestion reduction on the Southern-Northern border, and the integration of the local renewable production. Increasing of the Social Economic Welfare and reduction of the ancillary market services. | Internal (Italy) Internal (Italy) | 600 1000 | 1000 1000
339 | Italian HVDC tri-terminal link | Italian HVDC link between Campania, Sicily and Sardinia | TERNA | IT | Title of the document: “Avanzamento Piani di Sviluppo Precedenti - Volume 2”, Italy, 2019; Project number of NDP: 723-P, pages n.342-343-344-345 URL: https://download.terna.it/terna/0000/1188/44.PDF | 2025 | 2 | False | True | About B6 - Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served monetised): In Italy a different parameter is used for the monetization of the Expected Energy Not Served (EENS) variation due to this project, because the current parameter used by ENTSOE in this project sheet (10 k€/MWh) is not compliant with National regulations in force in Italy n°627/2016 (“Minimum Requirements for the preparation of the Ten Year Development Plan of the National Transmission Network” according to which benefits related to reduction of EENS is monetized through a Value of Lost Load (VOLL) in a range between 20 k€/MWh and 40 k€/MWh. | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase market exchanges between market zones Increase of security of supply increase RES integration | Internal (Italy) Internal (Italy) | 1000 1000 | 1000 1000
340 | Avelgem-Center: new corridor (Boucle du Hainaut) | The development of ~6 GW transport capacity through the elaboration of a new corridor between the Avelgem substation and the center of the Belgium (substation to be determined along the axis Bruegel-Courcelles). This corridor is envisioned to be implemented in AC technology as per the example of the Stevin project. Timing, routing, scope, etc. subject to feasibility studies and subsequent spatial planning procedures. Project motivation: Today, the west and the center of the country are connected on 380 kV via only one corridor between Mercator and Horta, which is currently being upgraded to HTLS. Additional capacity between the west and the center is, however, required to sustain price convergence within a European merit order increasingly characterized by RES. A new corridor between Avelgem and the center of the country would deliver around 6 GW of capacity and at the same time increases the maintainability and reliability of the grid, fulfilling the regulatory expectation that internal grids should be sufficiently strong so that society can fully reap the benefits from European market integration. Furthermore, the Avelgem – Center corridor is a pre-requisite for the integration of new offshore production capacity, for the connection of new large power plants west of Mercator, and for the integration of a second interconnector with Great-Britain (Nautilus). | ELIA | BE | NDP1, Belgium, 2020-2030, §4.1.4, page 10 https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/fr/20190516_plan-de-developpement-federal_fr.pdf | 2028 | 2 | False | True | The project enables the integration of the second wave of offshore wind in Belgium, as well as future cross border interconnection, RES integration and alleviation of internal congestions. The calculated benefits illustrate the facilitation of part of the SEW of project ID 120, but do not include another important anticipated SEW factor, which is the realization of additional PINT interconnection capacity from project 121. | New | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project deals with future more frequently expected situations with coinciding imports from France and UK together with evacuation of offshore wind. This project contributes to sustain price convergence between regions. Increased redundancy of onshore path ways will put less restrictions on cross border transmissions capacity for the market. This project contributes to resolving internal congestions, considering expected high international flows as well as internal grid flows due to increased market exchanges. This projects foresees the installation of phase shifting transformers enabling power flow control and optimizing the use of existing infrastructure. This project creates the necessary onshore grid capacity to facilitate offshore wind development. This project will facilitate further offshore development and create grid hosting capacity for onshore and offshore RES development. | Internal (Belgium) | 6000 | 6000
341 | North CSE Corridor | This project will consist of three investments. The investments of this project are SS 400/110 Belgrade West, OHL 400 kV SS Belgrade West - WPP Cibuk and doubling existing OHL 400 kV Portile de Fier (RO) - Djerdap 1 (RS). Every investment included in this project represents a segment of the new significant corridor in the East-to-West direction, boasting the massive cross-border impact on the boundary between Serbia and Romania. This, in detail, means that the project will enhance the market integration in the region, allowing the lower difference in marginal energy costs, allow the connection of huge capacities of renewable sources that have applied for connection in the observed area (only in Serbia, there is about 3 GW of new wind and solar power plants foreseen in the Banat region) and affect the security of supply in the aforementioned region by increasing the available balancing capacity across the mentioned border. It is clear that the new renewable capacities, enabled for connection by this project's commissioning, will enormously change the generation mix in Serbia and provide a boost for the Serbian transition towards the sustainable and environmentally acceptable green energy production. | EMS TRANSELECTRICA | RO ;RS | Plan razvoja prenosnog sistema Republike Srbije za period 2019 - 2028, page 158 (Serbian national TYNDP 2019-2028). The project is not included in the last approved Romanian NDP but is included in the draft version of Romanian NDP (Planul de dezvoltare a RET perioada 2020-2029 - draft version) submitted in October 2020 for approval to the Romanian NRA -page 253, https://web.transelectrica.ro/noutati/noutati/55_2020.08.17_14-30-42.pdf | 2030 | 2 | True | False |  | MostlyNew | False |  | These investments will help the evacuation of RES in North-East part of Serbia and enhance energy exchange in the East-West corridor | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | As the project contributes to the increase of the transfer capacity across the border between Serbia and Romania, it is safe to claim that it will enhance the market integration in the region and reduce the price differentials, as requested by this need. The internal investments in Serbia, included in the scope of North CSE Corridor, are foreseen to mitigate the risks of potential blackouts in the Belgrade region. Investment SS Belgrade West will provide major help in reducing the loading of the existing 400/x and 220/x kV substations in Srem area. Due to the fact that the commissioning of this project creates an additional energy corridor between Serbia and Romania, as confirmed by the NTC calculations, it can be claimed that it will, among other benefits, prove to be a major asset in the balancing flexibility area for both sides. As the Banat region in the close proximity of the border between Serbia and Romania offers a great possibility for the connection of renewable sources, the investments enveloped by this project will most certainly help the safe and reliable placement of the produced energy in the systems of interest. | Serbia - Romania | 347 | 622
342 | Central Balkan Corridor | This corridor will enable transmission of energy from east to west on the border between Bulgaria to Serbia and further to Montenegro and Bosnia and Herzegovina. It consists of several investments from SS Sofia West on the east to SS Pljevlja 2 and SS Visegrad on the west. In that way this corridor will be directly connected with project Transbalkan corridor (therefore, enabling the connection between Bulgarian energy market and Italian energy market), which represent a direct prerequisite for the proper development of the Central Balkan corridor. Among the numerous other benefits expected once this project is commissioned, the increase of NTCs on the borders between the involved countries (implying both the market integration and additional resources in securing the reliability of transmission systems' operation) can be seen as one of the most prominent. | EMS ESO | BA ;BG ;ME ;RS | Plan razvoja prenosnog sistema Republike Srbije za period 2019 - 2028, page 157, (Serbian national TYNDP 2019-2028) | 2034 | 2 | True | False |  | MostlyUpgrade | False |  | These investments will form a new 400 kV corridor from Bulgaria, through Serbia to the border with the Bosnia and Herzegovina and Montenegro. New corridor will enable evacuation of energy from new RES in Bulgaria to the western part of Balkan region. | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | The Central Balkan corridor, among other investments, also includes strengthening of the interconnections in the CSE region (that involves both EU and non-EU countries), enhancing the market integration in the area of interest and, hence, succeeding in reducing the price differentials. As the project envelops the replacement of severely ageing 220 kV infrastructure in Central Serbia with the new 400 kV lines and substations, it is expected to significantly improve the system reliability in this area, thus reducing the possibility of putting the security of supply at risk in some operational regimes. Since the project of Central Balkan corridor offers the new interconnections between Serbia and several neighboring countries, it is most certainly envisaged as valuable improvement regarding the system flexibility, the full impact of which becoming apparent in the light of rapidly developing renewable energy sources in the CSE region. As the relevant scenarios, taken into account in the scope of the analyses carried out in the scope of TYNDP 2020, consider the significant flows across the borders in the CSE region, the NTC increases, caused by this project, might prove to be crucial for the involved systems. | Montenegro - Serbia Bosnia Herzegovina - Serbia Bulgaria - Serbia | 500 500 730 | 500 500 186
343 | CSE1 New | The project will contribute in strengthen Croatian transmission grid along its main north-south axis (in parallel with eastern Adriatic coast) allowing for additional long-distance power transfers (including cross border) from existing and new planned power plants (RES/wind/ and conventional/hydro and thermal/) in Croatia (coastal parts) and BiH to major consumption areas in Italy (through Slovenia) and north Croatia. The increased transfer capacity will support market integration (particularly between Croatia and Bosnia-Herzegovina) by improving security of supply (also for emergency situations), achieving higher diversity of supply & generation sources and routes, increasing resilience and flexibility of the transmission network. | HOPS NOS-BIH | BA ;HR | Desetogodišnji plan razvoja hrvatske prijenosne mreže 2019.-2028. s detaljnom razradom za početno trogodišnje i jednogodišnje razdoblje, Croatia, 2019, Page 72 | 2030 | 2 | True | False |  | New | False |  | The Project implies increasing of transfer capacity between HR and BA by construction of new SS 400/110 kV Lika and its connection to an existing SS 400/220/110 kV Melina and SS 400/220/110 kV Konjsko in HR, and to an existing SS 400/110 kV Banja Luka in BA. | False | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. |  | Croatia - Bosnia and Herzegovina | 644 | 298
344 | Reinforcements Ring NL phase II | Upgrade of existing 380kV circuits from 2,5 kA to 4 kA | TENNET-NL | NL |  | 2040 | 1 | False | True |  | Upgrade | False |  |  | False | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Upgrade of the internal grid helps solve important congestions that arise due to future scenarios. Upgrade of the internal grid to help accommodate transport of high volumes of RES and thus decrease curtailment of RES | Internal (The Netherlands) | 0 | 0
346 | ZuidWest380 NL Oost | New 380 kV connection between Rilland and Tilburg including new substation. | TENNET-NL | BE ;NL | Samenvatting KCD 2017, The Netherlands, page 22 | 2029 | 3 | False | True |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Upgrade of the internal grid helps increase the cross-border exchange capabilities Netherlands and Belgium reducing thus price differentials between these different bidding zones Due to the change of the generation mix in both countries as well as the need to increase the interconnection capacity between the two countries, a new pattern of power flows will be created. This project, in combination with projects 262 and 297, helps facilitate these new needs and flow patterns By upgrading existing parts of the transmission grid, but also creating new corridors in it, a cost-efficient integration of large amounts of offshore wind production is implemented and thus reduces possible RES curtailment. | Belgium - Netherlands | 1000 | 10000
348 | NoordWest380 NL | Upgrade of existing 220kV circuits between Eemshaven and Vierverlaten to 2* 380kV – 2645MVA circuits | TENNET-NL | NL | Samenvatting KCD 2017, The Netherlands, page 23 https://www.tennet.eu/fileadmin/user_upload/Company/Publications/Technical_Publications/Dutch/TenneT_KCD2017_samenvatting.pdf | 2023 | 4 | False | True |  | Upgrade | False |  |  | False | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Due to the connection of new offshore wind power production in the north, as well as, the COBRA interconnector, a new pattern of power flows will be created. This project helps facilitate these new flow patterns. This projects facilitates the integration of large amounts of offshore wind generation connected to the north of the Netherlands by upgrading and expanding the Dutch transmission grid. | Internal (The Netherlands) | 150 | 150
349 | MaresConnect | MaresConnect is a 750MW HVDC VSC Interconnector between Great Britain and Ireland with three node connections; (i) Bodelwyddan (Wales), (ii) Maynooth (Dublin area, Ireland) and (iii) Bellacorick new node (Mayo area, Ireland). HVDC transmission will be made directly between Bellacorick and Bodelwyddan with a tapped connection at Maynooth. MaresConnect is an integral part of the MARES project, which aims to integrate 1,750MW of new RES and 6GWh of PHES in Mayo in the west of Ireland to the GB and SEM networks as well as provide increased interconnector capacity and voltage stability. | Mares Interconnector Holdings Limited | GB ;IE | Project Ireland 2040 National Development Plan 2018-2027.: Pages 22,28,75, refer to increrased commercial interconnection projects between UK and Ireland. P79 refers to closure of Moneypoint oal Plant, which the MAREX project intends to replace through the interconnector, PHES sorage, and new Wind generation. Classified as a Strategic Development by An Bord Pleanála, The Irish Planning Authority in 2013 as part of the grid connection of the MAREX project, ABP reference 16.PC0093 | 2025 | 2 | True | False | MARES brings the traditional benefits of interconnection as well as a number of project specific benefits to Ireland’s energy network and broader regional economy. 1. Lower projected wholesale prices for electricity in the Irish market through the reduction of RES curtailment during periods of high Irish wind and the ability to import lower priced GB power during periods of low Irish wind. 2. Displacement of CCGT capacity in GB, highly polluting coal and peat in Ireland through RES integration 3. Additional security of supply to both the Irish and GB markets 4. An investment in excess of €750m in Irish and GB transmission infrastructure as well as a large stimulus for €500 million investment in Pumped Heat Electrical Storage (PHES) and a further 2,000 MW wind generation in the west of Ireland 5. Significant employment during construction phase of all projects 6. Long-term export revenues to Ireland Employment benefits during construction phase of IC and related PHES project, and new critical transmission infrastructure to the Mayo region of Ireland, expected to bring much needed development to the communities there. NAME OF STUDY OPIC: GB-Ireland Interconnector Assessment STUDY CONDUCTED BY Poyry, UK STUDY YEAR 2017 STUDY HORIZON 2023-2040 STUDY APPROVED No https://www.dropbox.com/s/tzd0ix5qei745cz/Extract%20-%20Poyry%20OPIC%20GB-Ireland%20Interconnector%20Assessment%20%28Sept%202017%29.pdf?dl=0 | New | False |  | MaresConnect is composed of an HVDC transmission system between Bodelwyddan and Bellacorick replacement. This line has been listed in two sections; (i) the cross Irish Sea section from Bodelwyddan to Maynooth in Ireland, and (ii) from Maynooth to Bellacorick replacement. The system consists of three convertor stations; Bodelwyddan in Wales, Maynooth in the Greater Dublin area, and Bellacorick replacement in Mayo. At each of these locations there is an interface with the TSO’s 245kV or 400kV AC network with associated infrastructure including connection bays and transformers. Near Glinsk, a new 12 bay 220kV substation “Bellacorick replacement” is required to accommodate 220kV cables from four new wind farms, connection to the Bellacorick convertor station and two 245kV lines to connect a PHES (part of project 1030). | False | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The European Commission Expert Group on Electricity Interconnection Targets recommends an increased threshold of interconnection capacity of at least 30% of installed renewable generation capacity by 2030 to ensure adequate export capacity for the continued development of renewable generation in Member States and is of particular relevance to IE wind potential IoSN report 2020 pages 42-44 ; RegIP NS 2020 ; MAF 2019; IoSN report 2020: Appendix Fig 15, 16; Regional Investment Plan: Fig 3.13; Regional Investment Plan CCE 2017: section 5.1; IoSN report 2020: Appendix Fig 15 & 16; IoSN Report 2020 (Appendix); Regional Investment Plan CSE 2020 (Ch. 3); Regional Investment Plan CSE 2017 (Ch. 5);IoSN main report (chapter 5) IoSN report 2020 pages 42-44 ; RegIP NS 2020 ; MAF 2019; IoSN report 2020: Appendix Fig 15, 16; Regional Investment Plan: Fig 3.13; Regional Investment Plan CCE 2017: section 5.1; IoSN report 2020: Appendix Fig 15 & 16; IoSN Report 2020 (Appendix); Regional Investment Plan CSE 2020 (Ch. 3); Regional Investment Plan CSE 2017 (Ch. 5);IoSN main report (chapter 5) The Ireland Climate Action Plan 2019 ‘to tackle climate breakdown’ sets The plan sets out a roadmap to 2030, which in electricity terms, primarily involves an primarily involves an Increased reliance on renewables from 30% to 70% adding 12GW of renewable energy capacity | Ireland- United Kingdom | 750 | 750
350 | South Balkan Corridor | This project consists of three investments: one 400 kV OHL Bitola(MK)- Elbasan(AL), and two 400 kV SS Ohrid and Kumanovo, in Macedonia. The interconnection contributes to increasing the transmission capacity in the East-West direction. The mentioned two SS-s will increase the security of supply in the SouthWest part of the FYR of Macedonia. Construction of 400 kV OHTL interconnection from SS Bitola 2 to Macedonian/Albanian border and SS 400/110 kV Ohrid 400 kV interconnection transmission line Bitola (Macedonia) - Elbasan (Albania) is the last part of the implementation of the Corridor 8 in the context of creating a corridor East-West power transmission corridor between Bulgaria, Macedonia, Albania and Italy. | MEPSO | AL ;MK | 2017 | 2020 | 4 | True | True |  | New | False |  | to be filled in | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. |  | Albania - North Macedonia | 500 | 500
375 | Lienz (AT) - Veneto region (IT) 220 kV | Reconstruction of the existing 220kV-interconnection line between Lienz and Veneto Region (IT). The project includes the adjustment of power regulation devices. Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. | Austrian Power Grid TERNA | AT ;IT | Avanzamento Piani di Sviluppo precedenti 2015/Pag.168, Italy | 2027 | 2 | True | False | About B2 - CO2 emissions: Results relative to CO2 emissions are strictly dependent on scenario assumptions (especially lifetime of lignite and coal power plants, that should be assessed from a perspective consistent with considered time horizons 2030 and 2040). About B6 - Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served monetised): In Italy a different parameter is used for the monetization of the Expected Energy Not Served (EENS) variation due to this project, because the current parameter used by ENTSOE in this project sheet (10 k€/MWh) is not compliant with National regulations in force in Italy n°627/2016 (“Minimum Requirements for the preparation of the Ten Year Development Plan of the National Transmission Network” according to which benefits related to reduction of EENS is monetized through a Value of Lost Load (VOLL) in a range between 20 k€/MWh and 40 k€/MWh. | Upgrade | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | This project contributes to lowering the price differentials between Italian market zones and Austria This project will improve the integration of italian RES generation This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity. This project helps Italy to reach the 15% interconnection target by 2030. | Austria - Italy | 500 | 500
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | The project aims at the reconductoring of the already existing 400kV interconnection line between Meliti (GR) and Bitola (MK), in order to increase transfer capacity between the power systems of Greece and North Macedonia. | Admie MEPSO | GR ;MK |  | 2036 | 1 | True | False |  | Upgrade | False |  |  | False | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | Project implementation will contribute to a further improvement of the following ITEG indicators: 2. pushing ratio between nominal transmission capacity and installed RES capacity past 30% The TYNDP-2020 IoSN studies indicate a need of NTC increase (NT2030 +1000MW, NT2040 +500MW) for the GR-MK interconnection. Replacing existing OH line conductors (2xACSR 490/65 1920 A/1330 MVA) with new ones of higher ampacity (2xCTC_Cardinal/ACCC/TW/ 680mm2) is thus justified | Greece-North Macedonia | 500 | 500
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | This study envisions an upgrade of the existing interconnector VanEyck-Maasbracht between Belgium and the Netherlands making use of PSTs and/or HTLS technology.The study will determine the appropriate implementation option and timing, taking into account - The already planned upgrade of the Zandvliet-Rilland interconnector on the BE-NL border (see project 262) - The synchronisation with project study to upgrade interconnection DE-NL, also currently under consideration (see project 256) Project motivation: A need has been identified to further develop interconnection capacity on the BE-NL border, hereby alleviating VanEyck-Maasbracht as bottleneck. This project effectively increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. This project is likely to increase the potential for imbalance netting & reserve sharing due to increased remaining available margins of the cross border transmission capacity. PSTs will also help to balance the flows over the different cross border lines of the Belgian Dutch interconnection. Based on the above, the project directly contributes to the 2030 interconnection criteria. | ELIA TENNET-NL | BE ;NL | NDP1, Belgium, 2020-2030, §4.2.3.1, https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/fr/20190516_plan-de-developpement-federal_fr.pdf | 2030 | 1 | True | False |  | Upgrade | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and Dutch bidding zones. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This project has an important adequacy contribution due to decreasing figures of installed conventionals (bad market conditions) and considering the nuclear phaseout in Belgium. Phase shifting transformers will help to balance the flows over the different cross border lines of the Belgian Dutch border. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | Belgium - Netherlands | 1000 | 1000
378 | Transformer Gatica | New tranformer 400/220 kV in existing Gatica subestation, with potential impact in cross border values | Red Eléctrica de España | ES | Spanish NDP, Spain, 2015-2020, included in tables of Annex II page 22 | 2025 | 2 | False | True | This internal project contributes to improve the ES-FR capacity associated to the P16 cross border Project. Thus the CBA assessment of this project is the same as P16 assessment and the explanations provided in P16 project sheet are applicable to this project as well. As this internal project contributes to improve the ES-FR capacity associated to the P16 cross border project, it helps to integrate the Iberian Peninsula in a full-integrated European internal energy market, as it reduces its historical electric isolation (Spain wont yet fulfill the 10% objective for 2020 in spite of the strong technical and political efforts). This project also helps to integrate the high RES potential in the Iberian Peninsula and accommodate the new power flow patterns expected in the future. In addition, it also contributes to the security of supply, not only regarding adequacy (especially in tight situations), but also regarding flexibility and stability of the system. | New | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | The increase of interconnection capacity will be essential to cope with the residual load ramps challenge. The increase of interconnection capcity between countries will allow to exchange the power flows from flexibility sources. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchange between France and the Iberian Peninsula. | Internal (Spain) | - | -
379 | Uprate Gatica lines | Uprate of the following 400kV lines that reach Gatica subestation : Gatica-Gueñes, Gatica-Amorebieta-Ichaso and Gatica-Azpeitia. This internal project has influence in the exchange capacity values between France and Spain, and it is directly related to the P16 Biscay Gulf. | Red Eléctrica de España | ES | Spanish NDP, Spain, 2015-2020, Annex III page 145 mentions the need, and that it will be addressed/defined in future NDPs | 2025 | 1 | False | True | This internal project contributes to improve the ES-FR capacity associated to the P16 cross border Project. Thus the CBA assessment of this project is the same as P16 assessment and the explanations provided in P16 project sheet are applicable to this project as well. As this internal project contributes to improve the ES-FR capacity associated to the P16 cross border project, it helps to integrate the Iberian Peninsula in a full-integrated European internal energy market, as it reduces its historical electric isolation (Spain wont yet fulfill the 10% objective for 2020 in spite of the strong technical and political efforts). This project also helps to integrate the high RES potential in the Iberian Peninsula and accommodate the new power flow patterns expected in the future. In addition, it also contributes to the security of supply, not only regarding adequacy (especially in tight situations), but also regarding flexibility and stability of the system. | Upgrade | False |  |  | True | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | The increase of interconnection capacity will be essential to cope with the residual load ramps challenge. The increase of interconnection capcity between countries will allow to exchange the power flows from flexibility sources. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchange between France and the Iberian Peninsula. | Internal (Spain) | - | -
1034 | HVDC corridor from Northern Germany to Western Germany | Project 1034 consists of two new HVDC cable from Heide/West to Polsum and from Wilhelmshaven to Uentrop. The HVDC have a transfer capacity of 2 GW each. The project is a grid expansion project for low-loss transmission of high power over long distances from Northern Germany to the Ruhr-Area. Northern Germany is characterized by a large number of regenerative onshore and offshore energy sources which exceed the demand of Northern German loads. The Ruhr-Area, however, is a high-production region with large conventional generation capacity that has to be substituted by renewable generation capacity due to the German coal phase-out. | AMPRION TenneT DE | DE | Netzentwicklungsplan Strom 2030, Version 2019, 2. Entwurf (Aktualisierung Januar), Germany, 2019, pp. 380-391; https://www.netzentwicklungsplan.de/de/netzentwicklungsplaene/netzentwicklungsplan-2030-2019 | 2030 | 2 | False | True |  | New | False |  |  | False | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Reducing the redispatch leading to more flexibility and increasing the stability of the system. In critical grid situations, costly congestion management measures are taken to avoid overload of grid elements. The project will reduce the demand for re-dispatching, countertrading and curtailment of renewable energy producers by adding significant transmission capacity between the congested routes in the North-Western part of Germany integration of huge amounts of offshore and onshore wind. | Internal (Germany) | 4000 | 4000
1039 | SE North-south long-term reinforcements | Replacement of ageing overhead lines and reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. | Svenska Kraftnät | SE | System Development Plan 2018-2027, Sweden, 2017, p. 62. Nordic Grid Development Plan 2019, p. 14. | 2040 | 1 | False | True |  | MostlyUpgrade | False |  |  | False | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increased transfer capacity between northern and southern Sweden is needed to support the growth of RES production in north. | Internal (Sweden) | 1000 | 1000
1040 | LirIC | LirIC is a new HVDC sub-sea interconnector between Scotland and Northern Ireland. LirIC is being developed to increase the level of interconnection between Scotland and Northern Ireland addressing a market need and resulting in welfare generation opportunities in GB and consumer benefit in Ireland. A second beneficial driver for the project is the alleviation of Ireland's synchronous generation constraint, where there is an imposed limit on the level of demand that can be met by wind. These two effects result in significant benefit for British exports to Ireland to exploit wholesale power price arbitrage and Irish exports to Britain to avoid wind curtailment. | Transmission Investment | GB ;IE | No | 2027 | 1 | False | True |  | New | False |  | N/A - No clustering | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | LirIC will provide increased capacity between the iSEM and GB markets thereby converging the prices of these two regions With significant increases in wind generation expected in Scotland the increased capacity between Scotland and Northern Ireland will increase options for the System Operators to efficiently balance the systems enhancing security of supply and reducing the risk of power failures in both regions. The LirIC project will give access to wider markets for the increasing level of RES in Scotland. The project will therefore reduce congestion on the Scotland-England border thereby reducing the level of RES curtailment. LirIC will contribute towards the GB and iSEM interconnection targets of 15% and support reducing price differentials between the two markets. | Internal (United Kingdom) | 700 | 700
1041 | GREGY Interconnector | The GREGY interconnection project concerns the possibility to create a new energy highway within the Mediterranean Basin, between South East region of ENTSOE and South Eastern Mediterranean power systems by interconnecting Egypt and Greece. Rational behind the project is to establish a new interconnection between two large synchronous areas enabling series of benefits such as market coupling, enhanced security of supply (Adequacy, Flexibility, Stability) and socio-economic welfare. GREGY is also part of a bigger project including the construction of large wind farms (app. 3300MW) in order to exploit the high wind potential of Egypt, mainly on the Suez Gulf and bank sides of the Nile. Therefore, the project is expected to allow RES energy exports from Egypt to Greece at times of high RES generation and also vice versa contributing to a significant increase of participation of renewables in the energy mix and reduction of greenhouse emissions of the power sector. GREGY project consists of an HVDC interconnection from Wadi-El-Natroon (Egypt) to Attica area (Greece) of total length approximately 1373km and HVAC network connecting Egypt converter station to wind farms location (app. 640km). | ELICA S.A. | EG ;GR | No | 2028 | 1 | True | False |  | New | False |  | The total project includes the connection of Wind Farms installed at Suez Area with Greek power system which will enable energy market trading between Greek and Egypt. The project is rather complex since, besides its extensive length, it implicates various transmission system technologies, such as AC and DC lines, overhead, underground and submarine transmission lines. There is high technical and economical correlation among this diversification leading inevitably to the proposed clustering, which will help towards a more effective technical and economical assessment of the overall project. The transfer to Greece of low cost energy from the envisaged wind power plants in Egypt is an integral part of the GREGY project, therefore the clustering of the HVDC link and the prescribed EHV AC grid is necessary. | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | GREGY establishes a high capacity connection route between southeast Europe and Egypt along with nearby power systems, enabling electricity trading. Therefore, it will constitute a critical asset towards coupling of power markets of EU with North Africa and the Middle East. GREGY interconnector will allow sharing of the need for back-up adequacy resources among the interconnected countries. The risk of power failures, even in severe incidents, can be significantly reduced, provided that the interconnector will be able to cover power deficit up to 3GW. GREGY interconnector will also enable access to new balancing sources for both power systems. High capacity of interconnection will permit trading of significant volumes of balancing and reserve services, increase flexibility and allow optimal operation of variable RES. GREGY is part of a bigger project including the construction of large wind power plants (approximately 3300 MW), so that the high wind potential of Egypt can be optimally exploited. | Greece - Egypt | 3000 | 3000
1042 | Offshore wind integration | Integration of 700 MW off-shore wind farms in Baltic Sea near Lithuania coast. To connect offshore wind farms it will be necessary to strenghten western part of 330 kV network in Lithuania, build offshore platform in Baltic Sea and connect platform via 60-80 km AC or DC cable to planned Darbenai substation. | LITGRID AB | LT | '"Development of the Lithuanian electric power system and transmission grids. 2017-2026" (https://www.litgrid.eu/uploads/files/dir417/dir20/dir1/12_0.php), page 23. | 2030 | 1 | False | True |  | New | False |  |  | False | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | Connection of 700 MW offshore wind farms is supporting national strategy targets in Lithuania to significally increase generation from renewables. Connecting 700 MW offshore wind farms will accommodate future scenarios, by helping to reach decarbonisation targets and increase generation from renewable energy sources. | Internal (Lithuania) | 700 | 700
1043 | Wahle-Mecklar | North-South transmission in Germany. AC links from Northern Germany towards the load centers of Bavaria and Baden-Württemberg | TenneT DE | DE | NEP2030 v2019 (Germany), page 317 | 2024 | 4 | False | True |  | New | False |  |  | False |  |  | Internal (Germany) | 0 | 0
1046 | N-S Finland P1 stage 3 | This project consists of the sixth 400 kV overhead line (Nuojuankangas-Huutokoski) connecting North Finland to South Finland, new 400 kV lines Tuomela B - Nuojuankangas and Petäjävesi-Hikiä as well as reactive compensation measures to improve the voltage stability of the grid. The project is built to increase the North-South transmission capacity thus enabling the integration of new renewable and conventional generation in northern Finland. | FINGRID | FI | Kantaverkon kehittämissuunnitelma 2019-2030 (currently in Finnish, will be available in english later), Finland, 2019, codes FG-NS-5P0, FG-NS-6P1-002, FG-NS-7P2 | 2030 | 3 | False | True |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. |  | Internal (Finland) | 1000 | 1000
1047 | Emden-Eemshaven | Increase of the interconnection capacity between the Netherlands (Eemshaven) and Germany (Emden) by adding a new 380kV tranmission line. The project is planned as a combination of overheadline, onshore cable and sub sea cable. | TenneT DE | DE ;NL |  | 2035 | 1 | True | False |  | New | False |  |  | False |  |  | Germany - Netherlands | 1000 | 1000
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | The project refers to the construction of a submarine DC transmission link of total capacity 2000MW (2x1000MW) interconnecting Egypt's North Mediterranean coast and Greece at the island of Crete. A new HVDC conversion station close to the existing thermal power plant of Atherinolakkos in South-East Crete will be the connection point to Greece. Crete interconnection with mainland Greece is already under way by the Greek TSO (IPTO) with the implementation works expected to be completed before 2030 (both AC and DC links). Moreover, the "Southern Aegean Interconnector" transmission project will provide another transmission route of the transfer capacity through the Aegean sea. The connection point in Egypt will be at its Northern coast located South of Crete, where the bulk of Egypt's electrical load and HV transmission grid infrastructure is located. All the aforementioned installations (converter stations, substations etc) will be of closed type using GIS technology. The proposed Greece - Africa interconnection project will provide energy stability to the Eastern Mediterranean Sea area as intercontinental energy transfers will be facilitated and generation adequacy of the region will be increased. | Kykladika Meltemia SA | EG ;GR |  | 2028 | 1 | True | False |  | New | False |  |  | False | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | The proposed Greece - Africa interconnection project will provide energy stability to the Eastern Mediterranean Region as intercontinental energy transfers will be facilitated and generation adequacy of the region will be increased. Various future scenarios will be made eligible for testing and analysis between EU and non EU cross border flows. Energy transactions between Greece and Egypt through GAP Interconnector (HVDC cable) will lead to reduced price differentials between EU (Greece) and non-EU countries (Egypt). Certainly the increased interconnection capacity between Greece and Egypt provided via the development of GAP Interconnector shall lead to significant decrease of RES curtailments. The increased Interconnection capacity provided via the infrastructure of GAP Interconnector will enhance System Adequacy for both Power Systems (Greek - EU and Egyptian - Africa). Power failures will be mitigated in a more bulk interconnected grid. | Greece - Egypt | 2000 | 2000
1049 | Cronos Energy Ltd | Cronos Energy Ltd (“Cronos”) is permitting a 1400MW DC Bipole VSC interconnector between England and Belgium. The project started in 2017 and has obtained a legally binding grid connection agreement with National Grid at Kemsley, Kent in the UK for rights to construct, connect and operate an interconnector. The management team of Cronos has a successful track record in developing and operating interconnectors and transmission projects as well as large-scale grid connected power stations in the UK and Europe and has been involved in over 40GW of transmission power station and interconnector projects in Europe. Our mandated technical advisor for electrical engineering, infrastructure and power systems is WSP Ltd, our mandated financial advisor is EY (Ernst & Young). The interconnector is expected to reach commercial operations in late 2026 and the permitting and construction timetables are attached in Microsoft Excel format. Cronos has commenced the planning and environmental work as well as having undertaken detailed work on the undersea cable route and onshore works. Cronos is committed to the project and has detailed knowledge of interconnector permitting, regulatory regimes, energy contracting, project financing and construction and operations including O&M. | Cronos Energy Ltd | BE ;GB |  | 2025 | 1 | True | False |  | New | False |  |  | False | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure designed to offer more supply options to isolated areas | A significant Change in the generation portfolio and residual load ramps (which are of indicative of helping security of supply)- the project has approximately 3200MWh per year of reduction in Energy Not Served The project has positive impacts by reducing the curtailments of Renewable Energy wind/solar farms and other energy sources, and this has been quantified as being approximately 8GWh per annum. Transmission Capacity Increase- the project offers a 1400MW transmission capacity increase for Belgium and the UK | Belgium - United Kingdom | 1400 | 1400
1050 | Tarchon Energy Ltd | Tarchon Energy Ltd (“Tarchon”) is permitting a 1400MW DC Bipole VSC interconnector between England and Germany. The project started in 2017 and has obtained a legally binding grid connection agreement with National Grid at Corringham in the UK for rights to construct, connect and operate an interconnector. The management team of Tarchon has a successful track record in developing and operating interconnectors and transmission projects as well as large-scale grid connected power stations in the UK and Europe and has been involved in over 40GW of transmission power station and interconnector projects in Europe. Our mandated technical advisor for electrical engineering, infrastructure and power systems is WSP Ltd, our mandated financial advisor is EY (Ernst & Young). The interconnector is expected to reach commercial operations in late 2026 and the permitting and construction timetables are attached in Microsoft Excel format. Tarchon has commenced the planning and environmental work as well as having undertaken detailed work on the undersea cable route and onshore works. Tarchon is committed to the project and has detailed knowledge of interconnector permitting, regulatory regimes, energy contracting, project financing and construction and operations including O&M. | Tarchon Energy Ltd | DE ;GB |  | 2028 | 1 | True | False |  | New | False |  |  | False | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure designed to offer more supply options to isolated areas | A significant Change in the generation portfolio and residual load ramps (which are of indicative of helping security of supply)- the project has approximately 1575MWh per year of reduction in Energy Not Served. The project also has positive impacts by reducing the curtailments of Renewable Energy wind/solar farms and other energy sources, and this has been quantified as being approximately 855GWh per annum (GA 2030 scenario). Transmission Capacity Increase- the project offers a 1400MW transmission capacity increase for Germany and the UK. | Germany - United Kingdom | 1400 | 1400
1051 | Aminth Energy Ltd | Aminth Energy Ltd (“Aminth”) is permitting a 1400MW DC Bipole VSC interconnector between England and Denmark. The project started in 2017 and has obtained a legally binding grid connection agreement with National Grid at Norwich Main in the UK for rights to construct, connect and operate an interconnector. The management team of Aminth has a successful track record in developing and operating interconnectors and transmission projects as well as large-scale grid connected power stations in the UK and Europe and has been involved in over 40GW of transmission power station and interconnector projects in Europe. Our mandated technical advisor for electrical engineering, infrastructure and power systems is WSP Ltd, our mandated financial advisor is EY (Ernst & Young). The interconnector is expected to reach commercial operations in late 2026 and the permitting and construction timetables are attached in Microsoft Excel format. Aminth has commenced the planning and environmental work as well as having undertaken detailed work on the undersea cable route and onshore works. Aminth is committed to the project and has detailed knowledge of interconnector permitting, regulatory regimes, energy contracting, project financing and construction and operations including O&M. | Aminth Energy Ltd | DK ;GB |  | 2028 | 1 | True | False |  | New | False |  |  | False | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure designed to offer more supply options to isolated areas | A significant Change in the generation portfolio and residual load ramps (which are of indicative of helping security of supply)- the project has approximately 1570MWh per year of reduction in Energy Not Served. The project also has positive impacts by reducing the curtailments of Renewable Energy wind/solar farms and other energy sources, and this has been quantified as being approximately 843GWh per annum (GA 2030). Transmission Capacity Increase- the project offers a 1400MW transmission capacity increase for Denmark and the UK. | Denmark - United Kingdom | 1400 | 1400
1052 | Lienz (AT) - Obersielach (AT) | The 380-kV-ring can be completed in Austria with the reinforcement of the Carinthia transmission grid. The advantages of a ring structure are only made possible by the project. Security of supply in Carinthia and Austria can be guaranteed in the long term. With the 380-kV-ring closure in the south, a redundant connection of the renewable energy feed-in centers in the east Austria (mainly wind and PV) and the load centers with the pumped storage power plants in the central Alpine region. The 380-kV-ring closure is essential for the grid integration of renewable energies and the Austrian Federal Government's climate and energy strategy, and its necessity will also be addressed in the Carinthian Government's 2018-2023 program. The project will also enable the development of additional transmission capacity to the neighboring countries | Austrian Power Grid | AT | APG Netzentwicklungsplan 2019, AT, 2019, 11-14, 48, https://www.apg.at/en/Stromnetz/Netzentwicklung | 2030 | 2 | False | True |  | New | False |  |  | False | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Facilitation of capacities between RES and pump storages in Austria as well as optimisation of cross border flows. Enabling future developments (load/generation). Faclilitation and optimisation of pump storage connections in the western part of Austria and therefore increasing flexibility. Connecting RES with pump storages. | Austria - Slovenia | 500 | 500
1054 | Westtirol (AT) - Zell/Ziller (AT) | An Upgrade of the existing 220kV-line Westtirol (AT) - Zell-Ziller (AT) and the erection of an additional 220/380kV-transformer. | Austrian Power Grid | AT | APG Netzentwicklungsplan 2019, AT, 2019, 14-3, 48, https://www.apg.at/en/Stromnetz/Netzentwicklung | 2027 | 2 | False | True |  | MostlyUpgrade | True | 3.1.4 |  | False | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Facilitation of capacities between RES and pump storages in Austria as well as optimisation of cross border flows. Enabling future developments (load/generation). Faclilitation and optimisation of pump storage connections in the western part of Austria and therefore increasing flexibility. Connecting RES with pump storages. | Austria - Germany | 600 | 600
1055 | Interconnection of Crete to the Mainland System of Greece | Crete is the largest electrically non-interconnected island system in Greece, representing a particular case, due to large size, rapid growth, remote location and large RES potential. The project aims to increase security of supply and improve stability issues of the island by its interconnection to the mainland system. It is expected to contribute to the reduction of the operation of oil-fired units that currently supply the island and in the long run to allow their progressive decommissioning, thus contributing to the reduction of production variable costs and greenhouse gas emissions. It will allow the full exploitation of local RES potential. The project shall ensure a more reliable and cost-effective supply of electricity to the island. This interconnection will be implemented in two phases. In Phase I Crete will be connected to Peloponnese with a 150 kV AC double circuit submarine cable interconnector of 2x200 MVA nominal transfer capacity. In Phase II Crete will be connected to Attica with a bipolar submarine HVDC-VSC link of 2x500 MW capacity transfer. The project in total contributes in achieving the EU-wide targets and policy objectives set in the 2030 climate and energy framework. | Admie | GR | NDP 2018-2027, Greece, 2018, 14.26 & 17.7, 17132 (or 86), http://www.admie.gr/fileadmin/user_upload/Files/masm/2018_2027/DPA_2018_2027.pdf | 2022 | 4 | False | True |  | New | False |  | The final design and implementation of the whole project with its clustering into two Phases imposed by several reasons, technical, financial and environmental. The aim to ensure security of supply for the island is the main reason for undertaking the investment. The rapid increase of electricity demand in the island, along with the need for decommissioning of the local oil-fired generation units, in short term horizon, to comply to the environmental Directives IED 2010/75/ΕΕ (IED) and 2015/2193/ΕΕ (MCPD directive), gave a character of urgency. The advanced level of maturity of the subproject of Phase I in terms of studies (detailed engineering, routing, seabed studies, environmental studies), in terms of financing (acquisition of grants in the framework of NSRF 2014-2020 and loans by EIB), in terms of low risk implementation due to capacity of promoter and its experience by similar AC interconnection projects (Cyclades interconnection to HETS) led to proceed immediately. Thus, the implementation of the Phase I has been started. Regarding Phase II project, it took more time to reach maturity. Phase II is technically more complicated. The need for in depth studies and better organization of the project implementation led IPTO to proceed with Phase II after implementation of major parts of Phase I in order to successfully achieve the best results and obtain the objectives as security of supply, increase of RES penetration, reduction of CO2 emissions, reduction of PSOs, etc. | True | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure designed to offer more supply options to isolated areas Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | The project will allow the full exploitation of local abundant RES potential, currently subject to limitations imposed by the autonomous operation. Crete is currently the largest electrically non-interconnected island system in Greece that operates in autonomous mode. The project will increase security of supply and improve stability issues for the electric system of the island, by its interconnection to the mainland system. Crete is the largest electrically non-interconnected island system in Greece, characterized by high annual consumption and load peak. Adequacy issues have been recognized, as several generation units have to be decommissioned or replaced according to EU Directives. The project ensures system adequacy by interconnecting the island to mainland | Internal (Greece) | 800 | 800
1056 | Croatian south connection | Currently, the South of Croatia is connected with the rest of Croatia via the territory of the Republic only by one electric power line SS Komolac - SS Rudine - SS Ston - SS Ponikve - SS Blato with transmission capacities limited to 110 MVA by the transmission line between SS Komolac and SS Ston. The second 110 kV connection is between SS Opuzen and TS Ston and it goes through the territory of BA and is introduced into SS Neum (BA). The safe operation of that part of the power system is largely dependent on interconnections with BiH. The power systems of Croatia and Bosnia and Herzegovina are extremely well connected with a total of 21 interconnectors at 400, 220 and 110 kV voltage levels contributing to the safety of both countries. However, the shape of territory and transmission network of Croatia, the southernmost part of the Croatian power system is practically dependent on interconnections with BA. To ensure the security of supply and enable additional integration of RES in that area following investments are necessary: 1. SS 400 kV ZONE 5, 2. SS 400/220 kV ZONE 6, 3. OHL 2x400 kV ZONE 5 - ZONE 6, 4. OHL 2x220 kV ZONE 6 – Plat, 5. SS 220/110 kV Plat | HOPS | HR |  | 2035 | 1 | False | True |  | New | False |  |  | False |  |  | Internal (Croatian) | 0 | 0
1057 | HVDC CentraLink | 2GW HVDC Connection from northern Germany (North Sea area) to Baden-Württemberg (Großgartach area). A rapid increase of the installed RES capacities in the northern areas o Germany has already by far exceeded the local load expectations and created an additional demand for transmission capacities. The RES based Generation mostly located in the northern regions of Germany has to be connected with the load centers situated in the southern parts of the country. The relevance, as well as, the sustainability of this concept project is directly correlated with the further increase of the installed RES capacities in the northern Germany. As such the idea complies to the vision of North-South-Interconnectors created and pursued by EC. | TRANSNET-BW | DE | This project is not included in the German National development plan (NEP) 2019. | 2035 | 1 | False | True |  | New | False |  |  | False | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The new HVDC transmission link enable a power transmission over long distances with lower losses and contribute to the improving of voltage stability and security of supply in the German power system. The further expansion of RES capacities in Germany, especially offshore wind, leads in critical grid situations to the overloads of internal grid elements. The project will create an efficient targeted connection between RES in northern Germany and load centres in southern Germany, which prevents potential bottlenecks in transmission routes. The HVDC transmission link will directly connect regions with high amount of RES and load centres in southern Germany, which enables a further integration of RES. This project will also contribute to energy transport from south to north in case when there is high solar radiation and little wind. | Internal (Germany) | 2000 | 2000
1058 | HVDC Interconnector DE-CH | This concept project concerns an extension of German HVDC lines towards Switzerland via an additional HVDC link. It pursues an ultimate goal to realise a new HVDC N-S corridor connecting the load / generation capacities in the North Sea area with the ones installed in the Mediterranean sea region. | SWISSGRID TRANSNET-BW | CH ;DE | This project is not included in the German National development plan (NEP) 2019. | 2040 | 1 | True | False | This project is currently under consideration. Due to the early planning phase and expected commissioning date after 2035, this project has not been assessed in the 2030 scenarios of the TYNDP 2020. | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Germany and Switzerland and possibility of higher market exchanges, which lead to higher price convergence. The full controllability of the HVDC link between Germany and Switzerland will contribute to the voltage stability and security of supply, which can significantly increase the flexibility of power systems in both countries. The further expansion of RES capacities in Germany, especially offshore wind leads to increasing RES-curtailment in the coming decades. By increasing the transmission capacity between Germany and Switzerland, the alternative HVDC measure allows a higher export in hours of high RES infeed. | Switzerland - Germany | 1000 | 1000
1059 | Southern Italy | New 400 kV lines in Campania and in Calabria, affecting existing 400 kV substation. The link will remove grid constraints and congestions due to the new renewable installed capacity. | TERNA | IT | Avanzamento Piani di Sviluppo Precedenti - Volume 2, Italy, 2019, https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete | 2030 | 3 | False | True | About B6 - Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served monetised): In Italy a different parameter is used for the monetization of the Expected Energy Not Served (EENS) variation due to this project, because the current parameter used by ENTSOE in this project sheet (10 k€/MWh) is not compliant with National regulations in force in Italy n°627/2016 (“Minimum Requirements for the preparation of the Ten Year Development Plan of the National Transmission Network” according to which benefits related to reduction of EENS is monetized through a Value of Lost Load (VOLL) in a range between 20 k€/MWh and 40 k€/MWh. | New | False |  |  | False | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure | Increase of security of supply The new line will allow congestion reduction on the Central-Southern/Southern border, and the integration of the local renewable production. Increasing of the Social Economic Welfare and reduction of the ancillary market services, especially in case of failure of the existing line 380 kV Laino-Altromonte | Internal (Italy) | 200 | 200
1061 | Reactive compensation for project 197 | Reactive compensation in substations to increase the transfer capacity from North to South Finland: installation of STATCOM(s), SVC(s) and/or shunt compensation. This investment was previously included within project 197 but has been set aside to abide with the CBA Guideline clustering rules. | FINGRID | FI | Kantaverkon kehittämissuunnitelma 2019-2030 (currently in Finnish, will be available in English later), Finland, 2019, codes: FG-NS-5P1 and FG-NS-PECOMP | 2022 | 1 | False | True |  | New | False |  | n/a | False | Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment
1062 | Reactive compensation for project 1046 | Reactive compensation measures in substations to increase the transfer capacity from North to South Finland: installation of STATCOM(s), SVC(s) and/or shunt compensation. This project supports project 1046 by improving the voltage stability of the grid. Compensation probably needed in two or more locations/substations. | FINGRID | FI | Kantaverkon kehittämissuunnitelma 2019-2030 (currently in Finnish, will be available in english later), Finland, 2019, codes FG-NS-5P0, FG-NS-6P1-002, FG-NS-7P2 | 2029 | 1 | False | True |  | New | False |  | n/a | False | Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment
1063 | ZuidWest380 West | New 380 kV connection between Borssele and Rilland. This investment was previously clustered within project 346. | TENNET-NL | NL | Samenvatting KCD 2017, The Netherlands, page 22 | 2022 | 4 | False | True |  | New | False |  |  | False | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This projects facilitates the integration of large amounts of offshore wind generation connected to the west coast of the Netherlands by upgrading and expanding the Dutch transmission grid. This project helps accommodate the new flow patterns as a result of increased cross-border flows and the new generation mix due to future connection of high volumes of RES
1066 | Bulgaria - Turkey | The project concerns the construction of a new AC 400kV interconnection Bulgaria - Turkey. The proposed interconnection line with a total length 150 km will connect Maritsa East 2 SS in Bulgaria and Vize Havza SS in Turkey. This project, together with the project for a new interconnection between Greece and Turkey, compose the project “East Balkan Corridor” that will contribute to increasing the cross -border transfer capacities between ENTSO-E countries and Turkey and address a system need, identified in ENTSO-E's System Needs study. The construction of the two interconnections will also improve the stability of the connection of a large electricity system such as the Turkish one to the unified electricity system of the countries of continental Europe. Furthermore the project will allow integration of more renewables to the grids, support the convergence of market price between the neighboring countries and thus will help the realization of clean energy package targets. | ESO | BG ;TR |  | 2036 | 1 | True | False |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | The project contributes in reducing high price differentials indicated between Turkey and Bulgaria in the future due to the generation shift, enabling lower and more balanced wholesale prices. Project implementation will enhance transmission capacity between Bulgaria and Turkey and thus will contribute to a further improvement of the 2nd ITEG indicator pushing ratio between nominal transmission capacity and installed RES capacity past 30% Constraints (e.g. congestion) occur in future scenarios where high flows are exchanged between Bulgaria and Turkey with the current grid. The project contributes in transfer capacity increase, thus minimizing congestion at the BG – TR border. | Bulgaria-Turkey | 1100 | 700
1067 | New AC 400 kV interconnection line Greece - Turkey | The project concerns the construction of a new AC 400kV interconnection Greece - Turkey. The proposed interconnection line with a total length 130 km will connect Nea Santa SS in Greece and Babaeski SS in Turkey. This project, together with the project for a new interconnection between Bulgaria and Turkey, compose the project “East Balkan Corridor” that will contribute to the increase of the cross-border transfer capacities between ENTSO-E countries and Turkey and address a system need, identified in ENTSO-E's System Needs study. The construction of the two interconnections will also improve the stability of the connection of a large electricity system such as the Turkish one to the unified electricity system of the countries of continental Europe. Furthermore the project will allow integration of more renewables to the grids, support the convergence of market price between the neighboring countries and thus will help the realization of clean energy package targets. | Admie | GR ;TR |  | 2036 | 1 | True | False |  | New | False |  |  | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | The project contributes in reducing high price differentials indicated between Turkey and Greece in the future due to the generation shift, enabling lower and more balanced wholesale prices. Project implementation will enhance transmission capacity between Greece and Turkey and thus will contribute to a further improvement of the 2nd ITEG indicator pushing ratio between nominal transmission capacity and installed RES capacity past 30%. Constrains (e.g. congestions) occur in future scenarios where high flows are exchanged between Greece and Turkey with the current grid. The project contributes in transfer capacity increase, thus minimizing congestions at the GR – TR border. | Greece-Turkey | 600 | 600
1068 | LaSGo Link | LaSGo Link is a new multi terminal HVDC sub-sea interconnector project linking Sweden, the Island of Gotland and Latvia. The project consists of two sections: a 700MW internal grid reinforcement between the Swedish mainland and the island of Gotland and a 500MW cross border connection between the island of Gotland and Latvia. LaSGo Link is being developed to increase grid capacity to Gotland and increase the level of cross border capacity in the Baltic Sea region. This will meet the current challenge of security of supply experienced in this region and therefore support industry and the further growth of wind power in the Gotland region. The cross border element of the project will provide further routes to market for generation thereby reducing internal grid congestion in Sweden and providing socio-economic benefit to both Sweden, Latvia and the interconnected markets in the Baltic Sea region. | Transmission Investment | LV ;SE |  | 2036 | 1 | True | False |  | New | False |  | The LaSGo Link project is a multi-terminal HVDC link with converter stations sited in Sweden, the island of Gotland and Latvia. The Sweden to island of Gotland section is an internal Swedish grid reinforcement project but is required to support the connection of the cross border element between the island of Gotland and Latvia. Equally the sizing of the Sweden to Gotland section is based on the requirement of the cross border section. These two sections are therefore mutually inclusive and must be realised as a single project to maximise the capital efficiency and socio-economic welfare of the project. | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | The new cross border capacity will give lower cost generators in Sweden access to wider markets, reducing the cost of power in Latvia and converging prices in the region. LaSGo Link will mitigate current grid deficiencies and support the connection of offshore wind in the seas around the island of Gotland. Furthermore, the project will reduce current security of supply issues that are limiting industrial expansion on the island with increased access to decarbonised energy. The multi-terminal design of LaSGo Link improves the capital efficiency and operational security of connecting future offshore wind around the island of Gotland directly to the markets of Sweden and Latvia. The project will support reducing price differentials in the Baltic region and support the expansion of wind generation around the island of Gotland contributing to the 30% RES capacity target.
1074 | Pannonian Corridor | The new 400 kV line connecting Serbian and Hungarian transmission systems, initially considered to connect SS Subotica 3 (RS) and SS Sándorfalva (HU). This is, however, not definitely decided, as the bilaterally developed Pre-Feasibility Study is expected to be done in 2021. This Study will provide much clearer insight into the situation in the area of interest and suggest the optimal substations that should be connected by the new line. Also, this project includes strengthening the North-to-South transmission corridor in Serbian system, by building two new 400 kV lines: SS Sombor 3 – SS Srbobran and SS Srbobran – SS Sremska Mitrovica 2. This is also deemed necessary, as numerous calculations have indicated that the new tie-line may not affect the NTC value enough if it is not accompanied by the two mentioned internal lines. The project can, alongside covering the needs seen in IoSN report, also be seen as a response to the ever-higher requests for integration of renewable sources in the Bačka region, while simultaneously strongly enhancing the security of supply and reliability of the transmission systems' operation in the included countries. | EMS | HU ;RS |  | 2036 | 1 | True | False |  | New | False |  | Each of these investments represents a segment of the new corridor for energy transmission, spanning across Serbian-Hungarian border, simultaneously increasing the NTC on it (which is a need stated in IoSN report) and facilitating the renewable sources integration in the Bačka region (area in the close proximity of the mentioned border). | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | As the foreseen scope of the project envisages the new interconnection between Serbia and Hungary, it can be seen as another step towards the fully integrated energy market of the CSE region, leading to the noteworthy reduction of the price differentials between the EU and non-EU countries. The additional NTC, vouched for by the commissioning of this project, is expected to be a major asset in the field of system flexibility and stability, especially if the massive capacities of variable RES, predicted along the routes of its investments, are taken into consideration. As the fully integrated market represents one of the main goals set before the system development plans, the new interconnection enveloped by this project will certainly lead the systems of interest in the desired direction, characterized, among other facets, by the substantial balancing flexibility. Since the Bačka region, in the vicinity of the border between Serbia and Hungary, becomes more and more attractive for the investors in the wind plants each day, this project represents a guarantee that the energy evacuation from the newly built sources will happen reliably and safely. | Hungary-Serbia | 500 | 500
1077 | Crete-North Greece-North Macedonia-Bulgaria Interconnector | The Crete-North Greece-North Macedonia-Bulgaria Interconnector is a multiterminal HVDC interconnection project of 2000 MW connecting Crete, North of Greece (Thessaloniki), North Macedonia and Bulgaria. It will complement the project LEG1 (HVDC interconnection between Libya and Crete), reinforcing bidirectional electricity exchange between South-East Europe and North Africa. The project will have a DC voltage of 525 kV. VSC is preliminary chosen for converter technology because it is more favorable for power trading and has other advantages such as blackstart capacity and voltage stability support. This project will increase power exchange capacity between Greece, North Macedonia and Bulgaria and give to these countries access to solar energy from Libya, contributing to the achievement of the EC’s Green Deal 2030 objectives | GreenPower 2020 | BG ;GR ;MK |  | 2036 | 1 | True | False |  | New | False |  | This is both a national and a cross-border project. One investment feeds the other. | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Capability for Black Start & Islanding Operation Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) | ENTSO-E's System needs study finds a difference in electricity prices of 7.53 €/MWh between Greece and Bulgaria in 2040. Interconnecting these countries shall participate in reducing the price differential. VSC links have controllable AC output voltage and frequency, increasing grid stability VSC converters can be used to support the grid by mixing active and reactive power during stressed conditions VSC converter is available almost instantly after the blackout and includes blackstart capability and special modes of operation for islanded grids. The VSC converters will provide 500 MVar of reactive power and will be able to operate in STATCOM mode. | Greece - North Macedonia North Macedonia - Bulgaria | 2000 2000 | 2000 2000
1081 | LAG Interconnector (LAG) | LAG is a multiterminal HVDC interconnection project of 2000 MW connecting Libya (Tobruk) to the North-West of Greece (Arachthos) and subsequently to Albania (Tirana). It will reinforce bidirectional electricity exchange between South-East Europe and North Africa and help bridge the power deficit of Albania. LAG will have a DC voltage of 525 kV. VSC is preliminary chosen for converter technology because it is more favorable for power trading and has other advantages such as blackstart capacity and voltage stability support. This project will act as a power exchange platform but also give Albania and Greece access to RES electricity from Libya, contributing to the achievement of the EC’s Green Deal 2030 objectives. | GreenPower 2020 | AL ;GR ;LY |  | 2036 | 1 | True | False |  | New | False |  | The first investment (main one) feeds electricity to the second one. The second one complements the first one in the sense that it will help maximize the capacity usage of the first one. | False | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Capability for Black Start & Islanding Operation Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) | ENTSO-E's System Needs study finds a price difference of 8.7 €/MWh between Greece and Albania in 2040. Interconnecting these countries shall participate in reducing the price differential. VSC links have controllable AC output voltage and frequency, increasing grid stability VSC converters can be used to support the grid by mixing active and reactive power during stressed conditions VSC converter is available almost instantly after the blackout and includes blackstart capability and special modes of operation for islanded grids The VSC converters will provide 500 MVar of reactive power and will be able to operate in STATCOM mode. | Albania-Greece Greece-Lybia | 2000 2000 | 2000 2000
1082 | Sea-Socket | Sea-Socket - Connection of up to 700MW of additional offshore wind in Ireland. The Project aims to facilitate and leverage the substantial wind resources available on the West Coast of Ireland, estimated between 25 GWh – 27GWh. The project provides for innovative offshore grid infrastructure to include a high voltage substation platform centrally linking up to four offshore floating wind parks connecting a total of 700MW of new offshore wind. The size of the initial platform is 700-MW and will facilitate multiple connections points. The collected energy will be transmitted via 220kV subsea AC cables to onshore substation(s) located along the Shannon Estuary. Sea-Socket aims to mitigate the main the development constraints for the deployment of offshore wind capacity by efficiently reducing investment costs, the impact on the environment and streamlining the permitting process to connect new offshore generation facilities to the grid for use and export to other markets in the EU. Sea-Socket can make a substantial contribution to facilitating RES integration, and potentially supporting the realisation of emerging industrial opportunities in the production of hydrogen using offshore wind resources. | Siga Hydro Limited | IE |  | 2036 | 1 | False | True |  | New | False |  |  | False | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to reduce price differentials between EU and/or non-EU countries | The Project aim is to deliver high volumes of RES by the deployment of innovative offshore grid infrastructure (i.e. a floating substation/connection platform) to exploit the significant wind resources on the west coast of Ireland. The use of innovative and emerging floating technologies will enable the cost-efficient connection of multiple wind parks and reduce project constraints in fully realising Ireland’s wind resources for use and export to EU Member States. The Project will enable and deliver up to 700MW of floating offshore wind capacity in Ireland for export to other EU countries utilising existing and new interconnection (EWIC and PCIs North-South Line, Greenlink 286, Celtic 107 and storage PCI Silvermines Hydro 2.29). It will support the price differentials and trading capabilities between EU countries. | Internal (Ireland) | 700 | 700

## Trans.Investments
TYNDP 2020 Transmission projects - General information on transmission investments | [8 empty] | Technical characteristics of the investment | [5 empty] | Costs of the investment |  |  | CBA indicators at investment level - Qualitative Stability Indicators |  |  | Residual environmental impact |  |  | Residual social impact |  |  | Other residual impact
Investment number | Investment Name | This investment belongs to project number… | Description of the investment | Commissioning Year | Status ID 1 : Under Consideration, 2 : In Planning but not permitting, 3 : In permitting, 4 : Under Construction | Explanation in case of delay or reclustering | Is Main Investment(s) | Is Main Investment(s) | Type of Element | Substation From | Substation To | Technology | Type of HVDC | Total route length (km) | Estimated CAPEX (MEUR) | Estimated OPEX (MEUR) | Cost Uncertainty Range | Transient stability | Voltage stability | Frequency stability | Distance (km) | Type of sensitivity | Additional information | Distance (km) | Type of sensitivity | Additional information | Other residual impact
2 | Pedralva-Sobrado | 1 | New double circuit Pedralva (PT) - Sobrado (PT) 400kV OHL, (only one circuit installed in a first step). | 2024 | 2 | Due to the expected delay of the connection of new RES generation, the commissioning date of this investment item was rescheduled | Rescheduled | FALSE | ACTransmissionLine | Pedralva (PT) | Sobrado (PT) | AC | None | 67 | 30.4 | 0.066 | ±10% | ++ | ++
4 | V.Minho -R.Pena-Feira | 1 | New double-circuit 400kV OHL Vieira do Minho (PT) - Ribeira de Pena (PT) - Feira (PT). | 2022 | 3 |  | Ahead of time | TRUE | ACTransmissionLine | V.Minho (by Ribeira de Pena) | Feira (by Ribeira de Pena) | AC | None | 131 | 69 | 0.155 | ±10% | ++ | ++ |  | 13 7 | 10 | Other | Globally Important Agricultural Heritage Systems (GIAHS)
474 | Substation Ribeira de Pena | 1 | New 400/60kV substation in Ribeira de Pena. | 2021 | 3 |  | Ahead of time | TRUE | OnshoreSubstation | Ribeira de Pena (PT) | - | AC | None | 0 | 7.4 | 0.054 | ±10% | ++ | ++
18 | Beariz (ES) - Fontefria (ES) | 4 | New northern interconnection. New double circuit 400kV OHL between Beariz (ES) - Fontefria (ES). | 2022 | 3 | Delays due to social and environmental problems (possibility of re-routing and/or siting or re-siting of facility(ies)). The permitting had to be reinitiated. | Delayed | TRUE | ACTransmissionLine | Beariz (ES) | Fontefria (ES) | AC | None | 30 | 18.69 | 0.49 | 10% | ++ | ++
496 | Fontefria (ES) - Vila Nova de Famalicão (PT) | 4 | New northern interconnection. New 400kV OHL Fontefria (ES) - Ponte de Lima (PT) - Vila Nova de Famalicão (PT). | 2022 | 3 | Delays due to social and environmental problems (possibility of re-routing and/or siting or re-siting of facility(ies)). The permitting had to be reinitiated. | Delayed | TRUE | ACTransmissionLine | Fontefria (ES) | Vila Nova de Famalicão (PT) (By Ponte de Lima) | AC | None | 140.21 | 63.92 | 0.208 | 10% | ++ | ++ |  | 0.5 29 3 | 1 | HabitatsDirective
498 | SE Fontefria 400/220kV | 4 | New northern interconnection. New 400kV substation Fontefria (ES), previously O Covelo. | 2022 | 3 | Delays due to social and environmental problems (possibility of re-routing and/or siting or re-siting of facility(ies)). The permitting had to be reinitiated. | Delayed | TRUE | Transformer | Fontefria (ES) | REE | AC | None | 0 | 13.16 | 0.17 | 10% | ++ | ++
499 | Beariz 400kV (ES) | 4 | New northern interconnection. New 400kV substation Beariz (ES), previously Boboras | 2022 | 3 | Delays due to social and environmental problems (possibility of re-routing and/or siting or re-siting of facility(ies)). The permitting had to be reinitiated. | Delayed | TRUE | OnshoreSubstation | Beariz (ES) | Beariz (ES) | AC | None | 0 | 7.17 | 0.17 | 10% | ++ | ++
500 | Ponte de Lima (PT) | 4 | New 400/150kV substation Ponte de Lima (PT), previously V. Castelo. | 2022 | 3 | Delays due to social and environmental problems (possibility of re-routing and/or siting or re-siting of facility(ies)). The permitting had to be reinitiated. | Delayed | TRUE | OnshoreSubstation | Ponte de Lima (PT) | Ponte de Lima (PT) | AC | None | 0 | 10.5 | 0.054 | 10% | ++ | ++
38 | HVDC Gatica-Cubnezais | 16 | New HVDC interconnection in the western part of the border via DC subsea cable in the Biscay Gulf (cable and converters at the end). | 2027 | 3 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | Gatica (ES) | Cubnezais (FR) | DC | None | 370 | 1750 | 10.2 | 11.4 | ++ | ++ |  | 11 | 0.269 | HabitatsDirective
60 | FR-BE I: Avelin/Mastaing-Avelgem-Horta HTLS | 23 | Replacement of the current conductors on the axis Avelin/Mastaing - Avelgem - Horta with high performance conductors (HTLS = High Temperature Low Sag) | 2022 | 4 | Rescheduled due to technical issue on HTLS cable | Rescheduled | TRUE | ACTransmissionLine | Avelin/Mastaing (FR) | Horta (BE) | AC | None | 80 | 165 | 0.4 | 5% | ++ | ++ |  | 3 | 35 | HabitatsDirective
614 | Reschenpass Interconnector | 26 | interconnector IT-AT | 2023 | 4 | Delay in Permitting procedure | Rescheduled | TRUE | ACTransmissionLine | Nauders (AT) | Glorenza (IT) | AC | None | 26 | 175 | 2.5 | 10 | ++ | 0 |  | 0 | 2 | Other | -
1503 | Second HVDC Module IT-ME | 28 | Second HVDC Module (600 MW) of interconnection line between Italy and Montenegro via 445 km 500kV DC subsea cable and converter stations at both ending points. | 2026 | 4 | posteponed | Rescheduled | TRUE | DCTransmissionLine | Villanova (IT) | Lastva (ME) | DC | Bipolar | 445 | 362 | 0.7 | 10 | ++ | ++ |  | 0 | 0 | None
635 | Elmed Project | 29 | New interconnection between Italy and Tunisia - new HVDC submarine cable | 2027 | 3 |  | Investment on time | TRUE | DCTransmissionLine | Sicily Area (IT) | Tunisia node | DC | Monopolar | 200 | 600 | 3 | 0 % | ++ | ++ |  | 9 | 0 | None
90 | 90 | 33 | Voltage upgrade of the existing 80km Calenzano-Colunga 220kV OHL to 400kV, providing in and out connection to the existing 220/150kV substation of S. Benedetto del Querceto (which already complies with 400kV standards). | 2023 | 3 |  | Investment on time | TRUE | ACTransmissionLine | Calenzano (IT) | Colunga (IT) | AC | None | 80 | 188 | 1.36 | 10% | ++ | ++ |  | 27 | 3 | Other
1041 | Rem. lim. in Central Italy | 33 | Removing limitations on existing 220 kV grid between Villanova e S.Barbara | 2026 | 2 |  | Investment on time | FALSE | ACTransmissionLine | Villanova (IT) | S. Barbara (IT) | AC | None | 350 | 71 | 0.92 | 10 % | ++ | ++ |  | 34 | 6 | Other | -
313 | Kocin-Mirovka | 35 | Connection of 2 existing 400 kV substations with new double circuit OHL having 120.5 km length and a transmission capacity of 2X1713 MVA. | 2026 | 3 | Delay due to the permit grant procedure and amendment of the respective legal framework | Delayed | TRUE | ACTransmissionLine | Kocin (CZ) | Mirovka (CZ) | AC | None | 120.5 | 145.03 | 0.006 | -10%, +15% | ++ | ++ | [5 empty] | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 313 and 315) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environmental impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval opinion.
315 | Kocin-Prestice | 35 | Adding second circuit to the existing single circuit OHL with a total transmission capacity of 2x1730 MVA and 117 km length | 2028 | 3 |  | Investment on time | TRUE | ACTransmissionLine | Kocin (CZ) | Prestice (CZ) | AC | None | 117 | 175.81 | 0.01 | -10%, +15% | ++ | ++ | [5 empty] | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 313 and 315) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environmental impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval opinion.
141 | Kriegers Flak CGS | 36 | Four offshore windfarms connected to shore combined with 400 MW interconnection between both countries. New technical solution connecting 220 and 150 kV AC offshore grid and onshore HVDC VSC Back-to-Back Converter. | 2020 | 4 | Difficulties during construction | Delayed | TRUE | OffshoreACTransmissionCable | Ishøj / Bjæverskov (DK) | Bentwisch (DE) | AC | None | 24 | 320 | 16 | 20 | ++ | 0
142 | Norway - Germany HVDC | 37 | A 623 km 500 kV HVDC interconnector between southern Norway and northern Germany. 514 km of the interconnector is subsea | 2020 | 4 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | Tonstad (NO) | Wilster (DE) | DC | None | 623 | 1850 | 15 | 0 | ++ | ++ | +
144 | Audorf - Kassoe | 39 | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity. It consists of a new 400kV route in Denmark and In Germany new 400kV line mainly in the trace of a existing 220kV line. | 2020 | 4 |  | Investment on time | TRUE | ACTransmissionLine | Audorf (DE) | Kassoe (DK) | AC | None | 110 | 536 | 4 | ± 10% | ++ | ++
650 | BE-LUX-DE Long-Term perspective | 40 | The technical solution is subject to further studies | 2035 | 1 | An increase of transfer capacity across the BE-LU-DE corridor is envisioned towards the 2030-2040 time horizon. | Rescheduled | TRUE | OnshoreACTransmissionCable | Aubange (TBC) | LUX-DE (TBC) | AC | None | 16 | 210 | 0.6 | 25% | ++ | 0
689 | 689: Vöhringen (DE) - Westtirol (AT) | 47 | Upgrade of an existing over head line to 380 kV, extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. Transmission route Vöhringen (DE) -Westtirol (AT). This project will increase the current power exchange capacity between the DE, AT. | 2027 | 2 | Scope of the project changed due to technical reasons. | Delayed | TRUE | ACTransmissionLine | Vöhringen (DE) | Westtirol (AT) | AC | None | 157 | 174 | 1.3904 | 10% | ++ | ++
696 | Hunew 1 | 48 | 2x70 Mvar shunt reactors in station Sajóivánka (HU) | 2020 | 4 |  | Investment on time | FALSE | ReactiveCompensationDevice | Sajóivánka (HU) | N/A | AC | None | 0 | 0.5 | 0.0097 | ±10% | ++ | ++
697 | Hunew 2 | 48 | Second 400/120 kV transformer in station Sajóivánka (HU) | 2020 | 4 |  | Investment on time | FALSE | Transformer | Sajóivánka (HU) | N/A | AC | None | 0 | 2.1 | 0.0387 | ±10% | ++ | ++
1500 | 1. SK-HU interconnection | 48 | "New interconnection (new 2x400 kV tie-line) between SK and HU starting from Gabcikovo substation (SK) to the Gonyu substation (HU), with one circuit connected to Velky Dur (SK) substation. Project does not include the erection of new switching station Gabcikovo next to the existing one. It includes extension of the new Gabcikovo substation by the two 400 kV bays where the new double line will be connected." | 2020 | 4 |  | Investment on time | TRUE | ACTransmissionLine | Gabcikovo (SK) | Gonyu (HU) | AC | None | 110 | 27.65 | 0.7308 | ±10% | ++ | ++
1501 | 2. SK-HU interconnection | 48 | Connection of the two existing substations Rimavska Sobota (SK) - Sajoivanka (HU) by the new double 400 kV OHL armed only with one circuit on the both sides. | 2020 | 4 |  | Investment on time | TRUE | ACTransmissionLine | Rimavska Sobota (SK) | Sajoivanka (HU) | AC | None | 48 | 51.38 | 0.6904 | ±10% | ++ | ++
386 | 3rd EE-LV interconnection | 62 | "330 kV AC OHL between Kilingi-Nomme substation in Estonia and Riga CHP2 substation in Latvia. New 330 kV power transmission line is planned to take route along already existing 110 kV power transmission lines, by constructing both 110 kV and 330 kV lines on the same towers. Under the framework of the project it is planned to reconstruct the open-air switchyard of the 330/110 kV substation Riga CHP2 by constructing new open-air connection point for the 330 kV line Kilingi Nomme - Riga CHP2. """ | 2020 | 4 |  | Investment on time | TRUE | ACTransmissionLine | Kilingi-Nomme (EE) | Riga CHP2 (LV) | AC | None | 205 | 120 | 0.6 | 10 | ++ | ++
735 | Harku-Sindi 330kV OHL | 62 | New double circuit OHL with 2 different voltages 330 kV and 110 kV and with capacity 1143 MVA/240 MVA and a length 175 km. Major part of new internal connection will be established on existing right of way on the western part of Estonian mainland.The investment helps together with 3rd EE-LV interconnector to increase interarea capacity up to 600 MW. | 2021 | 4 |  | Investment on time | FALSE | ACTransmissionLine | Harku (EE) | Sindi (EE) | AC | None | 175 | 60 | 0.1145 | 0% (Costs have already been realized) | ++ | ++
1062 | Riga CHP2 - Riga HPP | 62 | The internal reinforcement for 3rd EE-LV interconnector and significant investment for Baltic Synchronization project | 2020 | 4 |  | Investment on time | FALSE | ACTransmissionLine | Riga CHP2 (LV) | Riga HPP (LV) | AC | None | 15 | 20 | 0.1 | 10 | ++ | ++
458 | HINP-SEAB New Double Circuit | 78 | New 400kV substation at Hinkley Point. New 400kV transmission route from Hinkley Point to Seabank. Reconstruction of Bridgewater substation for 400kV operation. Uprate Bridgewater - Melksham to 400kV. | 2024 | 3 |  | Investment on time | TRUE | ACTransmissionLine | Hinkley Point (GB) | Seabank (GB) | AC | None | 60 | 1104 | 16.2 |  | ++ | ++
462 | 462 | 81 | A new 138 km single circuit 400 kV 1500 MVA OHL from Turleenan 400/275 kV in Northern Ireland to Woodland 400/220 kV in Ireland. This is a new interconnector project between Ireland and Northern Ireland. | 2023 | 3 | Investment delayed due to judicial reviews of planning consent in IE and delayed approval of planning consent in NI. | Delayed | TRUE | ACTransmissionLine | Woodland (IE) | Turleenan (NI) | AC | None | 138 | 363 | 0.6 | +20% | ++ | ++ |  |  |  | None
463 | Srananagh - South Donegal | 82 | A new EHV overhead line from Srananagh in Co. Sligo to a new substation in south Co. Donegal | 2030 | 2 | A capacity review of committed generators and upcoming new connection policy rules will impact on renewable generation totals that drive the date of need for this investment. | Rescheduled | FALSE | ACTransmissionLine | Srananagh (IE) | New substation in South Donegal (IE) | AC | None | 83 | 171.7 | 0.34 | +50%, -10% | ++ | ++
896 | Omagh South to South Donegal | 82 | A new 275 kV cross border link between a new substation in South Donegal in Ireland and a new substation established south of Omagh in Northern Ireland | 2030 | 2 | A capacity review of committed generators and upcoming new connection policy rules will impact on renewable generation totals that drive the date of need for this investment. | Rescheduled | TRUE | ACTransmissionLine | South Donegal (IE) | Omagh South (NI) | AC | None | 58 | 88.6 | 0.18 | +50%, -10% | ++ | ++
897 | Omagh South to Turleenan | 82 | A new 275 kV overhead line from a new substation established south of Omagh to a new 400/275 kV substation, established at Turleenan by the North South Interconnection Development | 2030 | 2 | A capacity review of committed generators and upcoming new connection policy rules will impact on renewable generation totals that drive the date of need for this investment. | Rescheduled | FALSE | ACTransmissionLine | Omagh South | Turleenan | AC | None | 61 | 135.9 | 0.27 | +50%, -10% | ++ | ++
779 | F.Alentejo-Ourique-Tavira | 85 | New double-circuit 400+150 kV OHL F. Alentejo-Ourique-Tavira. The realization of this connection can take advantage of some already existing 150kV single lines, which can be reconstructed as double circuit line 400+150kV. | 2023 | 2 |  | Ahead of time | TRUE | ACTransmissionLine | F. Alentejo (by Ourique) | Tavira (by Ourique) | AC | None | 122 | 63 | 0.094 | ±10% | ++ | ++ |  | 11 | RAMSARSite
780 | Extension of Ourique substation | 85 | Extension of existing Ourique substation to include 400 kV facilities. | 2023 | 2 |  | Ahead of time | TRUE | OnshoreSubstation | Ourique (PT) | - | AC | None | 0 | 4.1 | 0.028 | ±10% | ++ | ++
1670 | Alqueva-Divor | 85 | New 75 km single-circuit 400 kV OHL Alqueva-Divor. | 2023 | 2 |  | New Investment | FALSE | ACTransmissionLine | Alqueva | Divor | AC | None | 75 | 23 | 0.07 | ±10% | ++ | ++
146 | ALEGrO | 92 | "Connection between the Oberzier substation in Germany and the Lixhe substation in Belgium via a +-100 km HVDC underground cable, including 2 DC/AC convertor stations to integrate the DC cable with the AC substations at Lixhe & Oberzier." | 2020 | 4 |  | Investment on time | TRUE | DCTransmissionLine | Oberzier (DE) | Lixhe (BE) | DC | Monopolar | 90 | 560 | 4.2 | 6% | ++ | ++ |  | 2 | 48 | HabitatsDirective
1493 | PST Vierraden | 94 | Installation of new PSTs in Vierraden | 2022 | 4 | Permitting is delayed | Delayed | TRUE | PhaseShiftingTransformer | Vierraden | Vierraden | AC | None | 0 | 110.8 | 2 |  | ++ | ++
1488 | Diemen-Lelystad-Ens | 103 | Upgrade of existing 380kV circuits between Diemen, Lelystad and Ens from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 2022 | 4 |  | Rescheduled | TRUE | ACTransmissionLine | Diemen | Ens | AC | None | 75 | 105 | 1 | +/- 10% | ++ | ++
1490 | Ens-Zwolle | 103 | Upgrade of existing 380kV circuits between Ens and Zwolle from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 2024 | 3 |  | Rescheduled | FALSE | ACTransmissionLine | Ens | Zwolle | AC | None | 32 | 41 | 0.4 | +/- 10% | ++ | ++
1539 | Krimpen-Geertruidenberg | 103 | Upgrade of existing 380kV circuits between Krimpen and Geertruidenberg from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 2023 | 3 |  | Rescheduled | FALSE | ACTransmissionLine | Krimpen | Geertruidenberg | AC | None | 35 | 41 | 0.4 | +/- 10% | ++ | ++
1540 | Eindhoven-Maasbracht | 103 | Upgrade of existing 380kV circuits between Eindhoven and Maasbracht from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 2025 | 3 |  | Rescheduled | FALSE | ACTransmissionLine | Eindhoven | Maasbracht | AC | None | 50 | 50 | 0.5 | +/- 10% | ++ | ++
810 | France Ireland Interconnector | 107 | A new HVDC subsea connection between Ireland and France | 2026 | 3 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | Knockraha (IE) | La Martyre (FR) | DC | None | 500 | 930 | 8.4 | +/- 10% | ++ | ++ | + | 33.277 | 10.072 | Other | offshore and onshore sensitivity
424 | Norway - Great Britain | 110 | A 720 km long 515 kV 1400 MW HVDC subsea interconnector between western Norway and eastern England. | 2021 | 4 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | Kvilldal (NO) | Blyth (GB) | DC | Bipolar | 720 | 1658.6 | 23.2 | 0 | ++ | ++ | + |  | None
396 | 3rd AC Finland-Sweden north | 111 | Third AC 400 kV overhead line interconnector between Finland north and Sweden SE1. | 2025 | 3 |  | Investment on time | TRUE | ACTransmissionLine | Keminmaa (Finland) | Messaure (Sweden, bidding area SE1) | AC | None | 200 | 238 | 0.11 | +-10% | ++ | ++
1710 | Keminmaa-Pyhänselkä | 111 | The investment is a 400 kV overhead line in North Finland. It is part of the 3rd AC cross border project between Finland and Sweden and will enable its full capacity to be utilized. The project will also allow integration of new RES generation at Bothnian bay. | 2024 | 3 |  | Investment on time | FALSE | ACTransmissionLine | Keminmaa | Pyhänselkä | AC | None | 156 | 59 | 0.19 | +-10% | ++ | ++
1625 | MOG II: connection of up to 2 GW additional offshore wind Belgium | 120 | "MOG II envisions the integration of additional wind farms in the Belgian part of the North Sea. One or more offshore platforms centralize the production from these offshore wind farms, and then transport it via 220 kV subsea AC cables to the onshore substation(s)" | 2028 | 2 |  | Investment on time | TRUE | OffshoreSubstation | Offshore (TBD) | Onshore (TBD) | AC | None | 50 | 1100 | 17 | 25% | ++ | 0
934 | Nautilus: 2nd interco UK - BE | 121 | This investment item envisions the possibility of a second HVDC connection between UK and a Belgian 380kV substation near the coast. Subject to further studies | 2028 | 1 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | Leiston (UK) | TBD (BE) | DC | None | 180 | 900 | 8 | 30% | ++ | ++ | +
373 | Ostroleka-Stanislawow | 123 | Construction of new 400 kV AC double-circuit OHL line with a length of 108 km and capacity of 2x2450 MVA between Ostroleka and Stanislawow. | 2023 | 4 |  | Investment on time | TRUE | ACTransmissionLine | Ostroleka (PL) | Stanislawow (PL) | AC | None | 108 | 79.7 | 1 | +- 5% | ++ | ++
733 | Ekhyddan-Nybro-Hemsjo | 124 | Second phase includes the internal network reinforcements in Sweden to be able to fully utilize the interconnector between Lithuania and Sweden. The internal reinforcement consists of the new 400 kV single circuit overhead transmission line between Ekhyddan-Nybro-Hemsjo. | 2026 | 3 | Permit denied. Appeal process ongoing | Delayed | TRUE | ACTransmissionLine | Ekhyddan (SE) | Nybro/Hemsjo (SE) | AC | None | 160 | 190 | 0.1 | +-10% | ++ | ++ |  | 1.6 0.4 | 43 | OtherNatureProtectionAreasUnderNationalLaw
403 | Reinforcements SE2-SE3 in Sweden | 126 | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. The need for capacity is driven by RES integration in northern Sweden and nuclear decommission in southern Sweden. | 2030 | 2 |  | Investment on time | TRUE | ReactiveCompensationDevice | Ramsele (SE2) | Hamra (SE3) | AC | None | 1200 | 2800 | 1 | +-10%
86 | 86 | 127 | New 178km double circuit 400kV OHL between existing Foggia and Villanova 400kV substations, also connected in and out to the Larino and Gissi substations. | 2024 | 3 |  | Investment on time | TRUE | ACTransmissionLine | Foggia (IT) | Villanova (IT) | AC | None | 178 | 397 | 3.17 | 10% | ++ | ++ |  | 8 | 0 | None
96 | 96 | 127 | New 30km single circuit 400kV OHL between the future substations of Deliceto and Bisaccia, in the Candela area | 2021 | 4 |  | Investment on time | FALSE | ACTransmissionLine | Deliceto (IT) | Bisaccia (IT) | AC | None | 30 | 190 | 1.74 | 10% | ++ | ++ |  | 22 | 0 | None
665 | Wolmirstedt-Isar | 130 | New DC-line to integrate new wind generation from control area 50Hertz especially Mecklenburg-Vorpommern, Brandenburg and Sachsen-Anhalt towards Central/south Europe for consumption and storage. | 2025 | 3 |  | Investment on time | TRUE | DCTransmissionLine | Wolmirstedt (DE) | Isar (DE) | DC | None | 540 | 4220 | 33.8 | +-15% | ++ | ++ |  | 78 | 45 | OtherNatureProtectionAreasUnderNationalLaw
661 | HVDC Line A-North | 132 | New HVDC line from Emden to Osterath to integrate new wind generation especially from North Sea towards Central Germany for consumption. | 2025 | 3 |  | Investment on time | TRUE | DCTransmissionLine | Emden East (DE) | Osterath (DE) | DC | Bipolar | 300 | 2300 | 18.4 | 10% | ++ | ++ |  | 3.5 16.1 11.0 3.9 2.6 | 28.6 8 | HabitatsDirective MarinStrategyFrameworkDirective
273 | 400kV OHL Cernavoda-Stalpu | 138 | Reinforcement of the cross-section between the Western coast of the Black Sea (Eastern Romania) and the rest of the system. A new 400 kV AC OHL double circuit of 159 km shall be built between the 400 kV substation Cernavoda and the existing 220/110 kV Stalpu substation, which shall be replaced with a 400/110 kV substation (onshore). One of the two circuits shall be connected in-out to the 400 kV substation Gura Ialomitei, situated in the vicinity of the new line. | 2023 | 4 | Delays related to land acquisition, obtaining approvals and modificatons to the public procurement legislation. | Delayed | FALSE | ACTransmissionLine | Cernavoda (RO) | Stalpu (RO) | AC | None | 159 | 65 | 0.36 | -5%, +5% | ++ | ++ |  | 1 | 0 | None
275 | 400 kV OHL Smardan-Gutinas | 138 | Reinforcement of the cross-section between the Western coast of the Black Sea (Dobrogea area) and the rest of the system. New 400kV double circuit OHL (one circuit wired) between existing substations. Line length 140km. | 2024 | 3 | Delay in issuing the government decision for expropriation. | Delayed | TRUE | ACTransmissionLine | Smardan (RO) | Gutinas (RO) | AC | None | 140 | 53 | 0.26 | -5%, +5% | ++ | ++ |  | 3 | 0 | None
715 | 220kV Stalpu substation upgrade to 400 kV | 138 | To reinforce the cross-section between the Black Sea coast wind generation in Romania and Bulgaria and the consumption and storage centers to the West, the 220 kV OHL Stalpu-Teleajen-Brazi is upgraded to 400 kV, as a continuation of the 400 kV d.c. OHL Cernavoda-Stalpu. The 220/110 kV substation Stalpu is upgraded to 400/110kV (1x250MVA). | 2023 | 4 | Delays due to the amendment of the public procurement legislation and resumption of auction due to non-compliant offers. | Delayed | FALSE | OnshoreSubstation | Stalpu (RO) | Stalpu (RO) | AC | None | 0 | 15 | 0.15 | -5%, +5% | ++ | ++ |  | 0 | 0 | None
800 | 400 kV OHL Varna-Burgas | 138 | New 86 km single circuit 400kV OHL in parallel to the existing one. | 2021 | 4 |  | Investment on time | FALSE | ACTransmissionLine | Varna(BG) | Burgas(BG) | AC | None | 86 | 63 | 0.8 | +10%, -10% | ++ | ++ |  | 7 | HabitatsDirective
256 | 256 | 142 | New interconnection line BG-GR by a 151km single circuit 400kV OHL. | 2023 | 3 |  | Investment on time | TRUE | ACTransmissionLine | Maritsa East 1 (BG) | N.Santa (GR) | AC | None | 151 | 80 | 1.1 | +10%, -10% | ++ | ++ |  | 0.1 4.4 | HabitatsDirective BirdsDirective
257 | 257 | 142 | New 94km single circuit 400kV OHL in parallel to the existing one. | 2022 | 3 | Having dificulities with acquiring the land | Rescheduled | FALSE | ACTransmissionLine | Maritsa East 1 (BG) | Plovdiv (BG) | AC | None | 94 | 57 | 0.7 | +10%, -10% | ++ | ++
258 | 258 | 142 | New 13km single circuit 400kV OHL in parallel to the existing one. | 2021 | 4 | Having dificulities with acquiring the land | Rescheduled | FALSE | ACTransmissionLine | Maritsa East 1 (BG) | Maritsa East 3 (BG) | AC | None | 13 | 7.4 | 0.1 | +10%, -10% | ++ | ++
262 | 262 | 142 | New 400kV OHL. Line lengt 150km. | 2021 | 4 |  | Investment on time | FALSE | ACTransmissionLine | Maritsa East 1 (BG) | Burgas (BG) | AC | None | 150 | 80 | 1.1 | +10%, -10% | ++ | ++
238 | New_400 kV OHL RO-RS | 144 | New 131 km double circuit 400kV OHL between Romania and Serbia (63 km on Romanian (thermal limit 2513 A) side and 68 km on Serbian (thermal limit 1920 A) side). | 2024 | 4 | Due to some delays related to investments 701 and 269 the line is not operated | Delayed | TRUE | ACTransmissionLine | Resita (RO) | Pancevo (RS) | AC | None | 131 | 47 | 0.23 | -5%, +5% | ++ | ++ |  | 1 | 0 | None
269 | 400 kV OHL Portile de Fier-Resita | 144 | New 116 km 400kV OHL single circuit between existing substation 400 kV Portile de Fier and new 400 kV substation Resita. | 2024 | 4 | Delays in issuing the normative acts necessary for the realization of the OHL which led to very long delays in the execution of works. The execution contract was suspended for a period of 6 months. | Delayed | FALSE | ACTransmissionLine | Portile de Fier (RO) | Resita (RO) | AC | None | 116 | 25 | 0.13 | -5%, +5% | ++ | ++ |  | 30 | 0 | None
270 | Upgrade of the existing 220kV double circuit OHL Resita -Timisoara - Sacalaz - Arad to 400kV double circuit line | 144 | Upgrade of an existing 220 kV AC double circuit line (OHL) between Resita - Timisoara (RO) to 400 kV double circuit line Resita-Timisoara/Sacalaz of which: 74 km from Resita to Timisoara and 92 km from Resita to Sacalaz , both overhead lines will be built on common towers up to Icloda on 58 km. Upgrade of the existing 220 kV AC double circuit line (OHL) Timisoara/Sacalaz-Arad to 400 kV on 67 km of which: 14 km of line will be build single circuit between Sacalaz-C.Aradului-""connection point"", 11 km single circuit from Timisoara to ""connection point"" and the rest 42 km of the line will be double circuit from ""connection point"" to Arad. | 2025 | 3 |  | Investment on time | FALSE | ACTransmissionLine | Resita (RO) | Timisoara-Sacalaz-Arad (RO) | AC | None | 274 | 75 | 0.5 | -5%, +5% | ++ | ++ |  | 34.5 | 0 | None
701 | 400 kV Substation Resita | 144 | New 400 kV substation Resita (T400/220 kV 400 MVA + T 400/110 kV 250 MVA), as development of the existing 220/110 kV substation. | 2025 | 4 | The contractor responsible for the execution of the investment has gone into insolvency and thus the auction must be resumed | Delayed | FALSE | OnshoreSubstation | Resita (RO) | Resita (RO) | AC | None | 0 | 24 | 0.24 | -5%, +5% | ++ | ++ |  | 0 | 0 | None
705 | 400 kV Substation Timisoara | 144 | Replacement of 220 kV substation Timisoara with 400 kV substation (2x250 MVA 400/110 kV) | 2025 | 3 | Long duration of the procurement procedure, delays due to executor and the pandemic impact of COVID 19. | Delayed | FALSE | OnshoreSubstation | Timisoara (RO) | Timisoara (RO) | AC | None | 0 | 18 | 0.18 | -5%, +5% | ++ | ++ |  | 0 | 0 | None
616 | Salgareda - Bericevo | 150 | New HVDC link between Salgareda (IT) and Bericevo/Divaca (SI) | 2028 | 3 | Project under consideration on SI side (permitting not started yet in Slovenia) | Delayed | TRUE | DCTransmissionLine | Salgareda (IT) | Bericevo (SI) | DC | None | 0 | 755 | 4 | 15 | ++ | ++ |  | 169 2 | 174 2 | OtherNatureProtectionAreasUnderNationalLaw Other | -
987 | France-Alderney-Britain | 153 | France-Alderney-Britain (FAB) is a new 220km-long HVDC subsea interconnection between Exeter (UK) and Menuel (France) with VSC converter station at both ends. Expected rated capacity is 2*700 MW. | 2025 | 3 | Delayed due to uncertainty of regulatory decisions | Delayed | TRUE | OffshoreDCTransmissionCable | Menuel (FR) | Exeter (GB) | DC | None | 220 | 870 | 7.6 | +/- 27% | ++ | ++ | + | 10 | 0 | None
998 | Viking Link DKW-GB, TYNDP ID 167.998 | 167 | 2 x700 MW HVDC subsea link across the North Seas. New substations on both sides; Bicker Fen (GB); Revsing (DK) | 2023 | 4 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | Revsing (DKW) | Bicker Fen (GB) | DC | None | 770 | 1655 | 16 | +- 15% | ++ | ++ | +
382 | New 330 kV OHL Vilnius-Neris | 170 | New 330 kV OHL Vilnius-Neris | 2025 | 3 |  | Investment on time | FALSE | ACTransmissionLine | Vilnius | Neris | AC | None | 80 | 23.7 | 0.024 | +5%, - 5% | ++ | ++
1004 | 330kV OHL Paide-Sindi (L346) | 170 | Reinforcement of existing 330 kV OHL between Paide and Sindi 330 kV substations in Estonia. Old line will be replaced with new towers and wires of 3x400 mm2 in phase. The thermal capacity of the line is planned 1143 MVA. The investment is also a backbone for Baltics Synchronization with CE (project nr 170). | 2025 | 1 |  | Cancelled | FALSE | ACTransmissionLine | Sindi | Paide | AC | None | 76 | 15 | 0.04 | +5%, - 5% | ++ | ++
1010 | 330 kV OHL Tartu-Valmiera | 170 | Reinforcement of existing 330 kV OHL. The investment is also a backbone for Baltics Synchronization with CESA. | 2025 | 3 |  | Investment on time | FALSE | ACTransmissionLine | Tartu | Valmiera | AC | None | 133 | 30.66 | 0.094 | +5%, - 5% | ++ | ++
1011 | Valmiera -Tsirguliina 330 kV | 170 | Reinforcement of existing 330 kV OHL. The investment is also a backbone for Baltics Synchronization with CESA | 2025 | 3 |  | Investment on time | FALSE | ACTransmissionLine | Tsirguliina | Valmiera | AC | None | 60 | 22 | 0.13 | +5%, - 5% | ++ | ++
1012 | 330 kV OHL Tartu-Balti (L300) | 170 | Reinforcement of existing 330 kV OHL between Balti and Tartu 330 kV substations in Estonia. Old line will be replaced with new towers and wires of 3x400 mm2 in phase. The thermal capacity of the line is planned 1143 MVA. The investment is also a backbone for Baltics Synchronization with CESA (project nr 170). | 2023 | 3 |  | Investment on time | FALSE | ACTransmissionLine | Balti | Tartu | AC | None | 168 | 51.2 | 0.11 | +5%, - 5% | ++ | ++
1013 | Viru-Tsirguliina 330kV OHL | 170 | Reinforcement of existing 330 kV OHL between Viru and Tsirguliina 330 kV substations in Estonia. Old line will be replaced with new towers and wires of 3x400 mm2 in phase. The thermal capacity of the line is planned 1143 MVA. The investment is also a backbone for Baltics Synchronization with CESA (project nr 170). | 2025 | 3 |  | Investment on time | FALSE | ACTransmissionLine | Viru | Tsirguliina | AC | None | 243 | 73.2 | 0.17 | +5%, - 5% | ++ | ++
1034 | New HVDC interconnector "Harmony Link" | 170 | New HVDC subsea cable connection between Lithuania and Poland. The project includes HVDC submarine and land cable system and converter stations at each end | 2026 | 3 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | Darbenai | Zarnowiec | DC | Bipolar | 400 | 682.6 | 2.45 | +5%, - 5% | ++ | ++
1118 | Further infrastructure aspects related to the implementation of the synchronisation of the Baltic States’ system with the continental European network | 170 | Further infrastructure aspects ‘not-known-today’ related to the implementation of the synchronisation of the Baltic States’ system with the continental European Network arising from ongoing synchronisation studies | 2025 | 1 |  | New Investment | FALSE |  | - | - | AC | None | 0 | 10.5 | 0.105 | +5%, - 5% | ++ | ++
1565 | Reconstruction of 330 kV OHL LE-Vilnius | 170 | Reconstruction of 330 kV OHL LE-Vilnius from single-circuit into double-circuit | 2020 | 6 |  | Investment on time | FALSE | ACTransmissionLine | Lietuvos E | Vilnius | AC | None | 41 | 19.3 | 0.019 | +5%, - 5% | ++ | ++
1566 | Reconstructions in North Eastern Lithuania | 170 | Utenos TP substations and 330/1110/10 kV Ignalinos AE TP substations reconstruction. Relocation of HV equipment (from 330/110/10 kV Ignalinos AE TP substation to 330/110/10 kV Lietuvos E TP substation) and changing topology of 330 kV overhead lines | 2021 | 4 |  | Investment on time | FALSE |  | - | - | AC | None | 0 | 24.26 | 0.024 | +5%, - 5% | ++ | ++
1568 | Upgrades in Alytus substation (LT) | 170 | Construction of three new 400/330 kV autotransformers in Alytus substation, to make LT-PL border operation in AC mode. | 2021 | 4 |  | Investment on time | FALSE |  | Alytus | - | AC | None | 0 | 22.44 | 0.022 | +5%, - 5% | ++ | ++
1571 | New Voltage stabiliser units (SVC), Battery Energy Storage System (BESS) control units in Lithuania, Latvia and Estonia. | 170 | If Studies concerning not known today further infrastructure aspects related to the implementation of the synchronisation of the Baltic States’ system with the continental European network, identify the necessity to install additional SVC. New Battery Energy Storage System (BESS) units - for frequency regulation (FCR and FRR) and to ensure power system secure and stable operation. | 2025 | 1 |  | Investment on time | FALSE |  | - | - | AC | None | 0 | 138 | 1.38 | +5%, - 5% | ++ | ++
1572 | Monitoring and control system upgrades in Lithuania, Latvia and Estonia. Upgrading control systems of exicting HVDC connections (EstLink 1 and EstLink 2 and NordBalt). | 170 | Upgrade of PSS in power stations. AGC impementation and commissioning in SCADA systems and power plants. WAMS and WAMPAC systems. Upgrade of instrument transformers and metering system in transmission network and is necessary to provide stable metering system during synchronous operation with Continental Europe or during island operation in emergency cases. System upgrades (automatics modernisation), SCADA and dispatcher trainer. In order to ensure system stability after high sudden power imbalance during BSPS island operation, activation of fast frequency reserves within view milliseconds via HVDC’s links is crucial. For this project is necessary to perform research, modelling and upgrading control system of HVDC's. | 2025 | 2 |  | Investment on time | FALSE |  | - | - | AC | None | 0 | 43.2 | 0.432 | +5%, - 5% | ++ | ++
1632 | New 330 kV Musa substation | 170 | New 330 kV Musa substation | 2025 | 3 |  | Investment on time | FALSE |  | Musa | - | AC | None | 0 | 6.14 | 0.006 | +5%, - 5% | ++ | ++
1634 | New 330 kV OHL Bitenai - KHAE | 170 | New 330 kV OHL Bitenai-KHAE. One part of the new line will be constructed as second circuit on exicting 330 kV OHL Bitenai-Jurbarkas (44km), one part will be new line (74 km), and as third part of new line will be used part of exicting 330 kV OHL KHAE-Sovetsk. | 2025 | 3 |  | Investment on time | FALSE | ACTransmissionLine | Bitenai | KHAE | AC | None | 234 | 42.1 | 0.042 | +5%, - 5% | ++ | ++
1659 | New 330 kV OHL Darbenai-Bitenai | 170 | New 330 kV OHL Darbenai-Bitenai | 2025 | 3 |  | Investment on time | FALSE | ACTransmissionLine | Darbenai | Bitenai | AC | None | 147 | 62.8 | 0.063 | +5%, -5% | ++ | ++ |  | 10.38 | OtherNatureProtectionAreasUnderNationalLaw
1660 | New 330 kV Darbenai substation | 170 | New 330 kV Darbenai substation, necessary for the connection of the new 330 kV lines as well as new HVDC subsea cable known as Harmony Link. This project includes territory planning, land acquisition and construction phases. | 2025 | 3 |  | Investment on time | FALSE |  | Darbenai | - | AC | None | 0 | 12 | 0.012 | +5%, - 5% | ++ | ++
1661 | Construction of new 400kV line Dunowo-Zydowo Kierzkowo | 170 | Dunowo-Zydowo Kierzkowo 400kV line is necessary to assure that after commissioning of Harmony Link and offshore wind farms, full capabilities would be available on the Polish-Lithuanian subsea interconnector. This project includes reconstruction of Dunowo substation with installation of 400/110 kV transformers and construction of new double-circuit 400 kV. | 2025 | 2 |  | New Investment | FALSE | ACTransmissionLine | Dunowo | Zydowo Kierzkowo | AC | None | 57.11 | 57.79 | 0.11 | +5%, -5% | ++ | ++
1662 | Construction of new 400kV line Pila Krzewina-Zydowo Kierzkowo | 170 | Pila Krzewina-Zydowo Kierzkowo 400kV line is interrelated with project aiming in building Dunowo-Zydowo Kierzkowo line. This project includes reconstruction and modernization of Pila Krzewina electrical station with installation of 400/110 kV transformers and reactive power compensation devices and construction of new double-circuit 400 kV. | 2025 | 2 |  | New Investment | FALSE | ACTransmissionLine | Pila Krzewina | Zydowo Kierzkowo | AC | None | 119 | 110.78 | 0.22 | +5%, -5% | ++ | ++
1663 | Modernization of 400kV OHL Krajnik-Morzyczyn | 170 | To allow effective energy flows in the north-west part of Poland after commissioning of Harmony Link, modernization of “North Line” (line between Krajnik and Gdansk Blonia) is necessary. The first project of North Line is modernization of Krajnik-Morzyczyn 400kV line. | 2023 | 2 |  | New Investment | FALSE | ACTransmissionLine | Krajnik | Morzyczyn | AC | None | 41.5 | 2.1 | 0.04 | +5%, -5% | ++ | ++
1664 | Modernization of 400kV OHL Morzyczyn-Dunowo-Slupsk-Zarnowiec | 170 | Modernisation of Morzyczyn-Dunowo-Slupsk-Zarnowiec 400kV line would be the longest part included in modernization of North Line. Because of its length this project consists of three sections: Modernization of Morzyczyn-Dunowo 400 kV, Modernization of Dunowo-Slupsk 400 kV, Modernization of Slupsk-Zarnowiec 400 kV. | 2025 | 2 |  | New Investment | FALSE | ACTransmissionLine | Morzyczyn | Zarnowiec | AC | None | 288.5 | 16.6 | 0.3 | +5%, -5% | ++ | ++
1665 | Modernization of 400kV OHL Zarnowiec-Gdansk/Gdansk Przyjazn-Gdansk Blonia | 170 | Modernisation of Zarnowiec-Gdansk/Gdansk Przyjazn-Gdansk Blonia 400kV line would be the last part included in modernization of North Line. | 2024 | 2 |  | New Investment | FALSE | ACTransmissionLine | Zarnowiec | Gdansk Blonia | AC | None | 77 | 4.5 | 0.1 | +5%, -5% | ++ | ++
1669 | Synchronous condensers in Lithuania, Latvia and Estonia | 170 | Synchronous condensers providing inertia, voltage stability,frequency stability and short-circuit power in Lithuania, Latvia and Estonia | 2025 | 3 |  | Investment on time | FALSE |  | 330 kV substations in the Baltics | - | AC | None | 0 | 333 | 4.5 | +5%, - 5% | ++ | ++
1702 | Common Baltic Frequency Stability Assessment System (FSAS). Modernisation of System Protection Schemes (SPS) and Under Frequency Load Shedding (UFLS). | 170 | FSAS is a common Baltic IT platform, necessary to ensure frequency monitoring in Baltic system, in order to ensure frequency stability in the region in synchronous mode with the CEN and in izolated mode after incidents. | 2025 | 2 |  | New Investment | FALSE |  | - | - | AC | None | 0 | 11.4 | 0.114 | +5%, - 5% | ++ | ++
1703 | Reconstruction of switchgears with shunt reactors | 170 | Due to the synchronisation project the total length of the power lines will increase. Increase in the total length of power lines higher reactive power generation by these lines. In order to reduce the risk that the voltages will rise too high, sufficient amount of reactive power compensation is needed, which can be achieved with the existing shunt reactors. Nevertheless, the shunt reactors need reliable switchgear to help to minimise the risk induced by commutation errors. | 2025 | 2 |  | New Investment | FALSE |  |  |  | AC | None | 0 | 4.3 | 0.01 | +5%, - 5% | ++ | ++
1487 | ElecLink | 172 | ElecLink is a new FR – UK interconnection cable with 1000 MW capacity through the Channel Tunnel between Sellindge (UK) and Mandarins (FR). Converter stations will be located on Eurotunnel concession at Folkestone and Coquelles. This HVDC interconnection is a PCI project (Project of Common Interest) no. 1.7.3 | 2021 | 4 | In 2016 the project experienced material delays beyond reasonable control as reported to the Commission and the commercial operations date was readjusted. Project is currently on schedule. | Investment on time | TRUE | DCTransmissionLine | Sellindge (UK) | Mandarins (FR) | DC | None | 69 | 580 | 4.5 | 20% | ++ | ++ | +
1281 | Aubange-Moulaine: PSTs | 173 | "Investment consists of the installation of two phase shifting transformers in Aubang, one on each of the 225kV circuits of the Aubange-Moulaine interconnector." | 2021 | 4 |  | Investment on time | TRUE | PhaseShiftingTransformer | Aubange (BE) | Moulaine (FR) | AC | None | 0 | 20 | 0.1 | 5%
1014 | Greenconnector | 174 | Greenconnector is an HVDC interconnector project between Italy and Switzerland for power transport using DC cables rather than overhead lines. The route length is about 165 km. The design power is 1000 MW (1200 MW in overload condition), while the DC voltage is +/- 400 kV DC. Two cables will be installed, working with a bipolar scheme. Great part of the cables route will exploit a section of an existing oil pipeline, no longer in service since January 1997. This pipeline crosses the Italian and Switzerland border at Splgenpass and is running close by the two end stations of the Greenconnector project (Bonaduz in Graubunden Canton and Verderio Inferiore, Lecco). The cables will be pulled inside the pipeline itself, reducing the amount of civil works required before and after cable laying and therefore limiting even temporary environmental impact. For about 47 km the cables will run across the Como lake. | 2024 | 3 | A different location of the Converter Station in Switzerland has been evaluated due to local opposition. A rerouting of the final part of the Interconnector has been evaluated as well. | Delayed | TRUE | DCTransmissionLine | Verderio | Bonaduz | DC | Bipolar | 165 | 660 | 2 | -10 / +15 % | ++ | ++ | [5 empty] | The project avoids the dismatling of about 80 km of an existing oil pipeline no longer in use. The pipeline crosses very sensitive environmental areas (Protected and mountain areas). Should the pipeline be dismissed, the estimated costs add up to about 25 million euros (supporting documents are available upon request). So our project generates a positive residual impact equal to such amount.
995 | Hansa PowerBridge I | 176 | New HVDC interconnector between Sweden (SE4) and Germany (50 Hertz) aiming to enhance the integration of the Nordic and the continental power market. Moreover the interconnector facilitates RES integration and increases the system adequacy in both systems. | 2026 | 3 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | Hurva (SE4) | Guestrow (DE) | DC | None | 300 | 660 | 1 | +-10 % | ++ | ++ | + | 20 8 |  |  |  | Tourist area with protected biotopes, water protection areas: 4 km
1016 | DKE-DE (Kontek 2) | 179 | New 600 MW HVDC subsea cable connecting DK2 and DE. Also called Kontek 2 | 2030 | 1 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | Ørslevvester (DKE) | Bentwisch (DE) | DC | None | 170 | 460 | 9 | 20 % | ++ | ++ | [5 empty] | This information is not available as the project is on a very early phase.
1018 | DKW-DE, Westcoast, TYNDP ID 183.1018 | 183 | New 380 kV line DKW-DE between Klixbuell (DE) and Endrup (DKW) as part of connection Endrup-Brunsbüttel | 2023 | 3 |  | Investment on time | TRUE | ACTransmissionLine | Klixbüll (DE) | Endrup (DKW) | AC | None | 92 | 210 | 2 | +- 20% | ++ | ++ |  | 5 | OtherNatureProtectionAreasUnderNationalLaw
886 | 886 - east of Austria | 186 | To allow the grid integration of the planned renewable energy generation (mainly wind power) in the north-eastern part of Austria ("Weinviertel") and to cover the foreseen load growth in that region the transmission grid infrastructure has to be enforced and new substations for the connection needs to be erected | 2022 | 4 |  | Investment on time | TRUE | ACTransmissionLine | Seyring | Zaya | AC | None | 60 | 215 | 1 | 10 | ++ | ++ |  |  | 31 | None
997 | 997 Pleinting - St. Peter | 187 | new 380-kV-line Pleinting (DE) - St. Peter (AT) on exting OHL corridor | 2028 | 3 |  | Investment on time | TRUE | ACTransmissionLine | Pleinting (DE) | St. Peter (AT) | AC | None | 60 | 197 | 1.576 | 10 | ++ | ++ |  |  | 2 | OtherNatureProtectionAreasUnderNationalLaw
1382 | NorthConnect | 190 | A 665 km long subsea interconnector between Norway and Scotland is planned to be realized in 2024. The main driver for the project is to integrate the hydro-based Norwegian system with the thermal/nuclear/wind-based British system. The interconnector will improve security of supply both in Norway in dry years and in Great Britain in periods with negative power balance (low wind, low solar, high demand etc.). Additionally the interconnector will be positive both for the European market integration, for facilitating renewable energy and also for preparing for a power system with lower CO2-emissions. The interconnector is planned to be a 500 kV 1400 MW HVDC subsea interconnector between western Norway and eastern Scotland. | 2024 | 3 | Permitting process in Norway | Delayed | TRUE | OffshoreDCTransmissionCable | Sima | Peterhead | DC | Monopolar | 665 | 1675 | 10 | Costs are based on feedback from the supply chain; CAPEX same as previous input to ENTSO-E, and OPEX adjusted from 30 to 10. | ++ | ++ | +
742 | Pyhanselka-Petajavesi | 197 | New single circuit 400 kV OHLs will be built from middle Finland to Oulujoki Area to increase the capacity between North and South Finland. Substations to connect wind farms in the region are also in consideration. | 2022 | 4 |  | Investment on time | TRUE | ACTransmissionLine | Pyhanselka (FI) | Petajavesi (FI) | AC | None | 300 | 100 | 0.242 | +-10 % | ++ | ++
308 | Vernerov-Vitkov | 200 | New 400 kV double circuit OHL with a transmission capacity of 2x1713 MVA and 83 km length. | 2023 | 3 |  | Ahead of time | TRUE | ACTransmissionLine | Vernerov (CZ) | Vitkov (CZ) | AC | None | 83 | 92.96 | 0.06 | -10%, +15% | ++ | ++ | [5 empty] | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 308, 309 and 314) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environment impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval.
309 | Vitkov-Prestice | 200 | New 400 kV double circuit OHL with transmission capacity of 2x1713 MVA and 87 km length. | 2021 | 4 |  | Ahead of time | TRUE | ACTransmissionLine | Vitkov (CZ) | Prestice (CZ) | AC | None | 87 | 109.73 | 0.005 | -10%, +15% | ++ | ++ | [5 empty] | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 308, 309 and 314) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environment impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval.
1711 | R Kocin | 200 | Upgrade and extension of the existing 400/110 kV substation, increasing nominal capacity of transformers from 2x250 MVA to 2x350 MVA | 2023 | 4 |  | Investment on time | FALSE | OnshoreSubstation | Kocin (CZ) | N/A | AC | None | 0 | 139.87 | 0.06 | -10%, +15% | ++ | ++ | [5 empty] | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 308, 309 and 314) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environment impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval.
1712 | R Vitkov | 200 | A construction of a new 400/110 kV substation GIS technology equipped with two transformers with nominal capacity of 2x350 MVA | 2021 | 4 |  | Ahead of time | FALSE | OnshoreSubstation | Vitkov (CZ) | N/A | AC | None | 0 | 27.43 | 0.063 | -10%, +15% | ++ | ++ | [5 empty] | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 308, 309 and 314) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environment impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval.
939 | Conneforde - Emden | 207 | New 380-kV-line in existing OHL corridor for integration of RES | 2023 | 4 | Due to complex and long permitting process | Delayed | TRUE | ACTransmissionLine | Conneforde | Emden/Ost | AC | None | 60 | 220 | 1.8 | +-10% | ++ | ++
1684 | Conneforde-Wilhelmshaven | 207 | New 380kV double circuit (OHL, partly underground) Conneforde - Wilhelmshaven (Fedderwarden, former Maade) including new 380kV switchgear Fedderwarden. Length 35 km. | 2020 | 4 |  | Investment on time | FALSE | ACTransmissionLine | Conneforde (DE) | Wilhelmshaven (DE) | AC | None | 30 | 140 | 1.1 | +-10% | ++ | ++
151 | Ganderkesee - Wehrendorf | 208 | New line (length ca. 95km), extension of existing and erection of substations, erection of 380/110kV-transformers. | 2023 | 4 | Due to complex and long permitting process | Delayed | TRUE | ACTransmissionLine | Wehrendorf (DE) | Ganderkesee (DE) | AC | None | 95 | 330 | 2.6 | +-10% | ++ | ++
156 | Niederrhein-Dörpen | 208 | New 380 kV double circuit overhead line Dörpen - Niederrhein including extension of existing substations. | 2023 | 4 | Due to complex and long permitting process | Delayed | FALSE | ACTransmissionLine | Niederrhein (DE) | Dörpen/West (DE) | AC | None | 182 | 540 | 4.3 | +-10% | ++ | ++
1380 | Wurmlach (AT) - Somplago (IT) interconnection | 210 | "Wurmlach (AT) – Somplago (IT) Interconnection is a cross-border electrical line promoted by Alpe Adria Energia Srl. The project concerns a 220kV a.c. merchant line, 300 MW thermal capacity from Somplago substation to new Wurmlach substation, including a Phase Shifter Transformer located in Austria" | 2023 | 3 | PERMITTING - Delays due to environmental problems (including re-routing) and delay of EIA assessment due to change of EIA Commission (2019) | Delayed | TRUE | ACTransmissionLine | SOMPLAGO | WURMLACH | AC | None | 51 | 87.3 | 1.6 | 7% | ++ | 0 |  | 2.2 2.2 | 0.1 | BirdsDirective
1407 | EuroAsia Interconnector | 219 | Investment 1407- PCI 3.10.1 Interconnection between Hadera (IL) and Kofinou (CY) , is part of the PCI 3.10 EuroAsia Interconnector . The Euro Asia Interconnector consists of a 500 kV HVDC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot, Israeli and the Greek transmission networks (offshore). The Interconnector have a total capacity of 2000 MW and a total length of 1208 km and allow for bidirectional transmission of electricity. The system to be used is HVDC (high voltage direct current) technology. Subsea cables and converter stations with a total capacity of 2,000MW The interconnector allows bidirectional power flow. The converter stations are of Voltage Source Converter (VSC) technology and connected to subsea electrodes. | 2023 | 3 | The National Regulatory Authorities of Greece and Cyprus approved the submitted Investment Request for the Project and agreed on the CBCA between them. The decision "Cross-Border Cost Allocation Between the Hellenic Regulatory Authority for Energy (RAE) and the Cyprus Energy Regulatory Authority (CERA)" provided on 10th of October 2017 concerned the implementation of PCIs 3.10.2 & 3.10.3. With the corresponding decision for PCI 3.10.1 not yet received, and to avoid delays in the implementation of the Project and to be in line with the obligations and commitments arising from the CBCA approval, the Project Promoter decided to amend the order of implementation of the three PCIs consisting PCI 3.10 as follows, with PCIs 3.10.2 & 3.10.3 implemented concurrently: PCI 3.10.3 Interconnection between Korakia, Crete and Attica region(EL) PCI 3.10.2 Interconnection between Kofinou (CY) and Korakia, Crete (EL) PCI 3.10.1 Interconnection between Hadera (IL) and Kofinou (CY) | Rescheduled | TRUE | OffshoreDCTransmissionCable | Hadera Site | Kofinou Site | DC | Bipolar | 310 | 1922 | 17.8 | +- 5% | ++ | ++
1409 | EuroAsia Interconnector | 219 | Investment 1409 - PCI 3.10.2 Interconnection between Kofinou (CY) and Korakia, Crete (EL) is part of the PCI 3.10 EuroAsia Interconnector . The Euro Asia Interconnector consists of a 500 kV HVDC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot, Israeli and the Greek transmission networks (offshore). The Interconnector have a total capacity of 2000 MW and a total length of 1208 km and allow for bidirectional transmission of electricity. The system to be used is HVDC (high voltage direct current) technology. Subsea cables and converter stations with a total capacity of 2,000MW The interconnector allows bidirectional power flow. The converter stations are of Voltage Source Converter (VSC) technology and connected to subsea electrodes. | 2023 | 3 | The National Regulatory Authorities of Greece and Cyprus approved the submitted Investment Request for the Project and agreed on the CBCA between them. The decision "Cross-Border Cost Allocation Between the Hellenic Regulatory Authority for Energy (RAE) and the Cyprus Energy Regulatory Authority (CERA)" provided on 10th of October 2017 concerned the implementation of PCIs 3.10.2 & 3.10.3. With the corresponding decision for PCI 3.10.1 not yet received, and to avoid delays in the implementation of the Project and to be in line with the obligations and commitments arising from the CBCA approval, the Project Promoter decided to amend the order of implementation of the three PCIs consisting PCI 3.10 as follows, with PCIs 3.10.2 & 3.10.3 implemented concurrently: PCI 3.10.3 Interconnection between Korakia, Crete and Attica region(EL) PCI 3.10.2 Interconnection between Kofinou (CY) and Korakia, Crete (EL) PCI 3.10.1 Interconnection between Hadera (IL) and Kofinou (CY) | Rescheduled | TRUE | OffshoreDCTransmissionCable | Kofinou Site | Korakia (Crete)Site | DC | Bipolar | 898 | 1922 | 17.8 | +- 5% | ++ | ++
1107 | 2nd interconnecter between Belgium and Germany | 225 | This investment item envisions the possibility of a second 1 GW HVDC interconnection between Belgium and Germany. Subject to further studies. | 2035 | 1 | The recently adopted Clean Energy Package will have a significant impact on the future market design. These developments are likely to have a major impact on the project of a second interconnector between Belgium and Germany. However, as a lot of these regulatory changes are still about to enter into force, the exact impact on this project cannot be established today. | Delayed | TRUE | DCTransmissionLine | Gramme (BE) | Dahlem (DE) | DC | None | 150 | 600 | 4.8 | 20% | ++ | ++
627 | 400kV interconnection RS-BA | 227 | Description of broader context - New double circuit 400kV OHL connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS) and new double circuit 400kV OHL connecting existing substation Visegrad (BA) and substation Bajina Basta (RS). In the first phase one 400 kV circuit would be equiped. In the second phase New SS Bistrica (RS) would be connected to the exisitng double circuit 400 kV OHL between SS Bajina Basta (RS), SS Visegrad (BA) and SS Pljevlja (ME). Part of regional transmission corridor northeast-southwest. | 2026 | 3 | Due to phasing of the project HVDC ME-IT cable and its infuluence on project Transbalkan corridor, there is a need for a new Study with economic and financial CBA analyses. | Delayed | TRUE | ACTransmissionLine | Bajina Basta (RS) | Visegrad (BA) | AC | None | 45.2 | 19.6 | 0.24 | 5% | ++ | ++
628 | 400kV OHL B.Basta-Obrenovac | 227 | Double circuit 400 kV OHL between upgraded substation Bajina Basta and substation Obrenovac. Part of larger regional transmission corridor northeast-southwest. | 2024 | 3 | Due to phasing of the project HVDC ME-IT cable and its infuluence on project Transbalkan corridor, there is a need for a new Study with economic and financial CBA analyses. | Delayed | FALSE | ACTransmissionLine | SS Bajina Basta (RS) | SS Obrenovac (RS) | AC | None | 109 | 55 | 0.66 | 5% | ++ | ++
630 | 400kV interconnection RS-ME | 227 | Description of broader context - New double circuit 400kV OHL (105km RS + 16km ME) connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS) and new double circuit 400kV OHL connecting existing substation Visegrad (BA) and substation Bajina Basta (RS). In the first phase one 400 kV circuit would be equiped. In the second phase New SS Bistrica (RS) would be connected to the exisitng double circuit 400 kV OHL between SS Bajina Basta (RS), SS Visegrad (BA) and SS Pljevlja (ME). Part of regional transmission corridor northeast-southwest. | 2026 | 3 | Due to phasing of the project HVDC ME-IT cable and its infuluence on project Transbalkan corridor, there is a need for a new Study with economic and financial CBA analyses. | Delayed | TRUE | ACTransmissionLine | Bajina Basta (RS) | Pljevlja (ME) | AC | None | 100 | 44.4 | 0.53 | 5% | ++ | ++ |  | 27.8 | OtherNatureProtectionAreasUnderNationalLaw
631 | 400kV SS B.Basta upgrade | 227 | Upgrade of existing 220/110 kV substation in Bajina Basta to 400/220/110 kV substation as part of overall western Serbia system upgrade to 400 kV voltage level. Part of larger regional transmission corridor northeast-southwest. | 2024 | 3 | Due to phasing of the project HVDC ME-IT cable and its infuluence on project Transbalkan corridor, there is a need for a new Study with economic and financial CBA analyses. | Delayed | FALSE | OnshoreSubstation | Bajina Basta (RS) | Bajina Basta (RS) | AC | None | 0 | 11 | 0.13 | 5% | ++ | ++
1526 | 400 kV OHL Lastva - Pljevlja | 227 | 400 kV OHL Lastva - Pljevlja | 2019 | 4 | Due to the delay of B. Basta - Obrenovac and B. Basta - Pljevlja investments | Delayed | FALSE | ACTransmissionLine | SS Lastva | SS Pljevlja | AC | None | 151 | 67.5 | 1.35 | 5% | ++ | ++
1527 | 400 kV OHL Kragujevac-Kraljevo | 227 | 400 kV OHL Kragujevac-Kraljevo | 2020 | 4 |  | Investment on time | FALSE | ACTransmissionLine | SS Kragujevac | SS Kraljevo | AC | None | 60 | 17 | 0.2 | 5% | ++ | ++
1528 | Upgrade of SS Kraljevo | 227 | Upgrade of SS Kraljevo | 2020 | 4 |  | Investment on time | FALSE | OnshoreSubstation | SS Kraljevo | SS Kraljevo | AC | None | 0 | 10.5 | 0.13 | 5% | ++ | ++
1231 | Muhlbach Eichstetten | 228 | Deployment of a second 400kV circuit at existing double circuit OHL Muhlbach - Eichstetten, instead of the currently operated circuit Eichstetten - Vogelgrun (currently operated with 225kV). Some topological adjustments of the existing grid in the area might prove to be necessary. This also include a transformer in Sierentz substation to balance flows between 225kV and 400kV grid in the area. | 2025 | 2 |  | Investment on time | TRUE | ACTransmissionLine | Muhlbach | Eichstetten | AC | None | 32 | 67 | 0.7 | 10% | ++ | ++
1270 | Baczyna-Zielona Góra | 229 | Indentation to the one circuit of 400 kV line Baczyna - Plewiska (construction 40 km new 400 kV line from new substation Zielona Góra to the point of indentation). Creating new route 400 kV Baczyna - Zielona Góra. | 2035 | 1 |  | Investment on time | FALSE | ACTransmissionLine | Baczyna-Plewiska indentation | Zielona Góra | AC | None | 40 | 20 | 0.057 | 9% | ++ | ++
1271 | Zielona Góra - Plewiska | 229 | Indentation to the one circuit of 400 kV line Baczyna - Plewiska (construction 40 km new 400 kV line from new substation Zielona Góra to the point of indentation). Creating new 400 kV route Zielona Góra - Plewiska. | 2035 | 1 |  | Investment on time | FALSE | ACTransmissionLine | Zielona Góra | Baczyna-Plewiska indentation | AC | None | 40 | 20 | 0.057 | 9% | ++ | ++
1272 | Zielona Góra | 229 | Construction of new substation 400/110 kV Zielona Góra to connect 400 kV lines : Baczyna - Zielona Góra, Zielona Góra - Plewiska, Zielona Góra - Eisenhuettenstadt (with installation of Phase Shifting Transformers), Zielona Góra - Polkowice | 2035 | 1 |  | Investment on time | FALSE | OnshoreSubstation | Zielona Góra | n.a. | AC | None | 0 | 90.4 | 2.712 | 5% | ++ | ++
1673 | Zielona Góra - Polkowice | 229 | Construction of new 2x400 kV line from new substation Zielona Góra to existing substation Polkowice | 2035 | 1 |  | New Investment | FALSE | ACTransmissionLine | Zielona Góra | Polkowice | AC | None | 90 | 75 | 0.14 | 9 | ++ | ++
1674 | Zielona Góra - Eisenhuettenstadt | 229 | Construction of new crossborder 2x400 kV line between new substation Zielona Góra (PL) end existing substation Eisenhuettenstadt (DE) | 2035 | 1 |  | New Investment | TRUE | ACTransmissionLine | Zielona Góra | Eisenhuettenstadt | AC | None | 80 | 65 | 0.13 | 9 | ++ | ++
353 | Krajnik-Baczyna | 230 | Construction of new 400 kV double circuit line Krajnik - Baczyna. One circuit will be operating temporarily on 220 kV between stations Krajnik and Gorzów with winter thermal limit 1290 A, summer thermal limit 990 A. | 2021 | 3 |  | Investment on time | FALSE | ACTransmissionLine | Krajnik (PL) | Baczyna (PL) | AC | None | 70 | 45.2 | 0.116 | 5% | ++ | ++ |  | 1
355 | Mikulowa - Swiebodzice | 230 | Construction of new 400 kV double circuit line Mikulowa-Swiebodzice in place of existing 220 kV line. One circuit will be operating temporarily on 220 kV between stations Mikulowa and Swiebodzice with winter thermal limit 1290 A, summer thermal limit 990 A. | 2024 | 3 |  | Rescheduled | FALSE | ACTransmissionLine | Mikulowa (PL) | Swiebodzice (PL) | AC | None | 100 | 89 | 0.307 | 5% | ++ | ++
1035 | Baczyna | 230 | Construction of new 400/110 kV Substation Baczyna to connect the new line Krajnik-Baczyna. | 2021 | 3 |  | Investment on time | FALSE | OnshoreSubstation | Baczyna | n.a. | AC | None | 0 | 24.9 | 0.675 | 5% | ++ | ++
1232 | Baczyna-Plewiska | 230 | Construction of new 400 kV double circuit line Baczyna - Plewiska | 2022 | 3 |  | Rescheduled | TRUE | ACTransmissionLine | Baczyna | Plewiska | AC | None | 147 | 91.9 | 0.7 | 5% | ++ | ++
1282 | 380 kV Grid Reinforcement Beznau - Tiengen | 231 | This projects helps to increase the cross border capacity between Switzerland and Germany by upgrading an existing line from 220 kV to 380 kV including internal reinforcements. | 2030 | 1 |  | Investment on time | TRUE | ACTransmissionLine | Beznau (CH) | Tiengen (DE) | AC | None | 11 | 58 | 0.304 | 10% | ++ | ++
1235 | Conceptual project | 233 | No details about the required network are known yet | 2027 | 1 | National Development Plan does not contain yet a solution for the second phase of projects 1011 and 1019, which compete with each other. | Delayed | TRUE | ACTransmissionLine | - | - | AC | None | 0 | 75 | 1.125 | 10% | ++ | ++
1236 | DKE-PL-1 | 234 | The first HVDC connector between Denmark-East and Poland. The planned transmission capacity of the new connection is 600 MW. | 2033 | 1 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | Avedøre (DKE) | Dunowo (PL) | DC | Bipolar | 330 | 655 | 13 | 20 % | ++ | ++
664 | HVDC Line C | 235 | New DC-lines to integrate new wind generation from Northern Germany towards Southern Germany and Southern Europe for consumption and storage. | 2026 | 3 | Due to complex and long approval process | Delayed | TRUE | DCTransmissionLine | Brunsbüttel, Wilster | Großgartach, Grafenrheinfeld | DC | None | 700 | 9560 | 76.5 | +-20% | ++ | ++ |  | 121 | 157 | OtherNatureProtectionAreasUnderNationalLaw
1241 | Fenno-Skan 1 renewal | 239 | Replacement of the existing 400 kV HVDC cable interconnection between Finland and Sweden. Fennoskan 1 will be decomissioned at the same time with this project being commisioned, which reduces capacity between FI and SE3 by 400 MW while increasing SE2-FI by 800 MW. | 2035 | 1 | The remaining lifetime of Fenno-Skan 1 will be investigated before making final decisions on its renewal. In addition, a joint study showed that the substantial benefits of this project will be realized in case of significant increase of consumption, new RES generation or the decommissioning of the remaining Swedish Nuclear plants which is expected in the 2040s. | Rescheduled | TRUE | OffshoreDCTransmissionCable | Hjalta (SE2) | Tuovila (FI) | DC | None | 200 | 488 | 0.75 | +/-15 % | ++ | ++
1276 | Upgrading of existing 220 kV line between SS Dakovo (HR) and TPP Tuzla (BA) to 400 kV line | 241 | The project necessity stems for the need to increase the target transfer capacity between HR and BA in order to accommodate market integration and exploitation of RES, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4. | 2033 | 1 |  | Investment on time | FALSE | ACTransmissionLine | Dakovo | Tuzla | AC | None | 91 | 26 | 0.033 |  | ++ | ++
1277 | Upgrading of existing 220 kV line between SS Dakovo (HR) and Gradacac (BA) to 400 kV line | 241 | The project necessity stems for the need to increase the target transfer capacity between HR and BA in order to accommodate market integration and exploitation of RES, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4. | 2033 | 1 |  | Investment on time | FALSE | ACTransmissionLine | Dakovo | Gradacac | AC | None | 46.2 | 14.07 | 0.018 |  | ++ | ++
1278 | Upgrading existing 220 kV SS Dakovo to 400 kV | 241 | Upgrading existing 220 kV SS Dakovo to 400 kV enables connection between SS Dakovo (HR) and TPP Tuzla/Gradacac (BA) by 400 kV lines. | 2033 | 1 |  | Investment on time | TRUE | OnshoreSubstation | Dakovo | Dakovo | AC | None | 0 | 11 | 0.0141 |  | ++ | ++
1279 | New double 400 kV line between SS Dakovo and location Razbojiste | 241 | New double 400 kV line between SS Dakovo and location Razbojiste enables connection of planned 400 kV SS Dakovo to existing 400 kV line Zerjavinec - Ernestinovo | 2033 | 1 |  | Investment on time | FALSE | ACTransmissionLine | Dakovo | Razbojiste | AC | None | 25 | 10.375 | 0.0133 |  | ++ | ++
1530 | Upgrading of existing 220 kV line between SS Gradacac (BA) and TPP Tuzla (BA) to 400 kV line | 241 | Upgrading of existing 220 kV line between SS Gradacac (BA) and TPP Tuzla (BA) to 400 kV line | 2032 | 1 |  | Investment on time | FALSE | ACTransmissionLine | SS Gradacac (BA) | TPP Tuzla (BA) | AC | None | 47.8 | 13.7 | 0.0176 |  | ++ | ++
1531 | Upgrading existing 220 kV SS Gradacac (BA) to 400 kV | 241 | Upgrading existing 220 kV SS Gradacac (BA) to 400 kV | 2032 | 1 |  | Investment on time | FALSE | OnshoreSubstation | SS Gradacac (BA) | SS Gradacac (BA) | AC | None | 0 | 7.9 | 0.01 |  | ++ | ++
1269 | New 400 kV overhead line Sombor (RS) - Ernestinovo (HR) | 243 | The project necessity stems for the need to increase the transfer capacity between RS and HR in order to accommodate connection of RES and improve market integration, according to the results based on TYNDP2018 CBA. | 2035 | 1 |  | Investment on time | TRUE | ACTransmissionLine | Ernestinovo | Sombor | AC | None | 70 | 19.04 | 0.0245 | 5% | ++ | ++
1245 | Vigy - Uchtelfangen (or beyond) | 244 | Upgrade of existing transmission OHL between Vigy and Uchtelfangen (or beyond) to increase the thermal cross-border capacity. To reach a higher capacity the options are High Temperature Low Sag (HTLS) conductors or a reconstruction of the tie-line in the existing route . | 2028 | 2 | Scope of the project changed due to technical reasons. | Delayed | TRUE | ACTransmissionLine | Vigy (FR) | Uchtelfangen (DE) | AC | None | 65 | 48 | 0.384 | 10% | ++ | ++
1514 | Power flow control between Vigy and Ensdorf | 244 | Installation of Phase Shift Transformers (PSTs) in Ensdorf substation to allow an optimal use of the capacity increase. | 2027 | 2 |  | Investment on time | FALSE | PhaseShiftingTransformer | Vigy (FR) | Ensdorf (DE) | AC | None | 0 | 46 | 0.368 | 10% | ++ | ++
1246 | Upgrade Meeden - Diele | 245 | Increase of the interconnection capacity between The Netherlands and Germany by adding one new phase shifting transformer and apply dynamic line rating on the existing 380 kV double circuit tie line between Meeden and Diele. | 2021 | 4 |  | Investment on time | TRUE | ACTransmissionLine | Meeden [NL] | Diele [DE] | AC | None | 27 | 38 | 0.4 | +/- 10% | ++ | ++
1381 | AQUIND Interconnector | 247 | AQUIND Interconnector is a proposed High Voltage Direct Current (HVDC) subsea and underground electric power transmission link between Great Britain (Lovedean substation, Hampshire) and France (Barnabos substation, Seine-Maritime) with a net transmission capacity of 2,000 MW. The Interconnector is designed as two parallel monopole 1000 MW circuits employing Voltage Source Converter technology. | 2023 | 3 | In 2018 UK Government, in accordance with the Planning Act 2008, designated AQUIND Interconnector as a Nationally Significant Infrastructure Project. This designation enables AQUIND Interconnector to apply for a Development Consent Order that would include all or nearly all permits and conditions necessary to start construction. Due to the "front-loading" approach and extremely robust evaluation and consultation requirements, which might have impact over more than one constituency, the DCO has been specifically designed to enable significant infrastructure developments. However, this process also takes longer than conventional planning application under the Town and Country Planning Act. Therefore commissioning of AQUIND was postponed by approximately a year from the date declared in the TYNDP 2018. The application for the DCO has been submitted on 14 November 2019. | Delayed | TRUE | OffshoreDCTransmissionCable | Lovedean (GB) | Barnabos (FR) | DC | Monopolar | 240 | 1400 | 14 | +/-10 | ++ | ++ | +
1384 | Merchant line "Castasegna (CH) - Mese (IT)" | 250 | The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Rationalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200 MW.The main Project elements are (merchant line): 220 kV Connection to the Swiss HVG in Castasegna; 220 kV Cable line of around 14 km between Castasegna and Mese; 220/380 kV Substation with PST 250 MVA in Mese. The Grid Rationalisation in the Region of Mese foresees the following actions: Displacement of 2 km of the 380 kV Line """"Soazza - Bulciago""; ""Realisation of a new 380/132 kV Substation in Mese (Transformation 2 x 250 MVA); Displacement of 0.8 km of 132 kV Lines; Realisation of 2.6 km of 132 kV Cable connections; Demolition of 2.45 km of 380 kV line and 2.3 km of 132 kV lines.""" | 2024 | 3 | The permitting phase in Italy is ongoing since April 2014 but we are still facing some challenges regarding Environmental impact of the 380/132kV Substation Terna in Mese. Commissioning expected in 2024. | Delayed | TRUE | ACTransmissionLine | Castasegna | Mese | AC | None | 14 | 90 | 0.1 | +/-15 | ++ | 0 | [5 empty] | Environmental positive impact due to the connected grid rationalisation 380/132kV in the region of Mese. Improvement N-1 security for hydro power plant production transmission in Castasegna (CH).
1050 | Van Eyck - Gramme: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors. Note that recently installed conductors along this axis anticipated the future HTLS upgrade, they don't have to be further upgraded. | 2029 | 2 |  | Investment on time | FALSE | ACTransmissionLine | Van Eyck | Gramme | AC | None | 90 | 140 | 0.4 | 25% | ++ | ++
1456 | Massenhoven - Van Eyck: HTLS upgrade | 252 | Installation of a second circuit (in HTLS) and upgrade of existing circuit to HTLS | 2024 | 3 |  | Investment on time | TRUE | ACTransmissionLine | Massenhoven (BE) | Van Eyck (BE) | AC | None | 90 | 120 | 0.4 | 25% | ++ | ++ |  | 23 23 | 32 | HabitatsDirective
1515 | Gramme - Courcelles: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors | 2033 | 2 |  | Investment on time | FALSE | ACTransmissionLine | Gramme | Courcelles | AC | None | 60 | 150 | 0.3 | 25% | ++ | ++
1516 | Bruegel - Courcelles: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors | 2035 | 2 |  | Investment on time | FALSE | ACTransmissionLine | Bruegel | Courcelles | AC | None | 47 | 110 | 0.2 | 25% | ++ | ++
1517 | Mercator - Bruegel: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors | 2025 | 2 |  | Investment on time | FALSE | ACTransmissionLine | Mercator | Bruegel | AC | None | 16 | 80 | 0.1 | 25% | ++ | ++ |  | 1.5 1.5 | 15 | HabitatsDirective
1676 | Mercator - Massenhoven: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors | 2030 | 2 |  | Investment on time | FALSE | ACTransmissionLine | Mercator | Massenhoven | AC | None | 36 | 70 | 0.2 | 25 | ++ | ++
1224 | Uprate of Creys-St Vulbas | 253 | Uprate of the double circuit 400-kV line Creys - Saint Vulbas with HTLS | 2031 | 1 |  | Rescheduled | FALSE | ACTransmissionLine | Creys (FR) | Saint Vulbas (FR) | AC | None | 21 | 45 | 0.5 | 10% | ++ | ++
1225 | PST in Cornier | 253 | Phase Shifter Transformer in order to attract the flows and alleviate the congestion on the France-switzerland interconnection west of Lake Geneva. | 2031 | 1 |  | Rescheduled | TRUE | PhaseShiftingTransformer | Cornier (FR) | Cornier (FR) | AC | None | 0 | 15 | 0.1 | 10% | ++ | ++
660 | HVDC Line A South - Ultranet | 254 | New HVDC-lines from Osterath to Philippsburg to integrate new wind generation especially from North Sea towards Central-South Germany for consumption and storage. | 2024 | 3 |  | Rescheduled | TRUE | DCTransmissionLine | Osterath (DE) | Philippsburg (DE) | DC | Bipolar | 340 | 1250 | 10 | 10% | ++ | ++ |  | 12.6 16.7 209 | 4.5 15.4 183.3 49.5 | HabitatsDirective RAMSARSite IUCNKeyBiodiversityAreas MarinStrategyFrameworkDirective
667 | Heide/West - Klixbüll | 258 | About 135 km new 380-kV-lines and around 10 new transformers for integration of onshore Wind in Schleswig-Holstein and increase of NTC between DE and DK | 2022 | 4 |  | Investment on time | TRUE | ACTransmissionLine | Brunsbüttel (DE) | Klixbüll (DE) | AC | None | 125 | 360 | 2.9 | +-10% | ++ | ++
1205 | HU-RO | 259 | New 120 km single circuit 400 kV OHL between Hungary and Romania (90 km on Hungarian and 30 km on Romanian side) in order to reach the market based target capacity resulted from the TYNDP 2016 Common Planning Studies based in V4 and TYNDP 2018 IoSN in DG2040 and GCA2040. Internal investments in Romania associated to the project are also included. | 2030 | 1 |  | Investment on time | TRUE | ACTransmissionLine | Józsa | Oradea | AC | None | 120 | 200 | 0.818 | +- 10% | ++ | ++
1255 | Interconnector GB-NL | 260 | Multi-purpose interconnector between GB and NL also connecting GB and NL windfarms. | 2030 | 1 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | TBD | TBD | DC | None | 0 | 850 | 6 | ±10% | ++ | ++ | +
1257 | Belgium-Netherlands: Zandvliet-Rilland | 262 | Upgrade of the capacity of the cross-border lines by replacing the current conductors with high performance (HTLS) conductors combined with the installation of additional phase shifting transformers in Zandvliet. | 2022 | 4 |  | Investment on time | TRUE | PhaseShiftingTransformer | Zandvliet (BE) | Rilland (NL) | AC | None | 10 | 60 | 0.1 | 10% | ++ | ++ |  | 2 2 | 7 | HabitatsDirective
1258 | Rüthi - Bonaduz/Mettlen | 263 | Integration of the new 380 kV tie-line Rüthi (CH) - Meiningen (AT) through optimisations between Rüthi and Mettlen, Rüthi and Bonaduz and the construction of a new 380 kV substation and a new 380/220 kV transformer in Rüthi. | 2035 | 1 |  | Investment on time | FALSE | ACTransmissionLine | Rüthi | Mettlen & Bonaduz | AC | None | 1 | 71 | 0.35 | 10% | ++ | ++ |  | 0 | None None
1583 | Vorarlberg | 263 | Voltage increase of all existing lines to 380 kV (without an increase of the line cross-section) and 2 new 380/22'0 kV transformers in Bürs | 2035 | 1 |  | Investment on time | TRUE | ACTransmissionLine | Rüthi | Border area (DE-AT) | AC | None | 1 | 300 | 1.5 | 10% | ++ | ++ |  | 0 | None
1259 | Beznau - Mettlen | 264 | Optimization of the existing route by voltage conversion to 380 kV, partial reinforcement. | 2029 | 3 | Permitting procedure | Delayed | FALSE | ACTransmissionLine | Beznau | Mettlen | AC | None | 64 | 83 | 0.42 | 10% | ++ | ++ |  |  | 47 | HabitatsDirective
1284 | Pradella - La Punt | 264 | Reinforcement of the existing route | 2022 | 4 | sundry reasons | Delayed | FALSE | ACTransmissionLine | Pradella | La Punt | AC | None | 49 | 102 | 0.51 | 10% | ++ | ++ |  | 3
1287 | Bassecourt - Mühleberg | 264 | Reinforcement of the existing route by voltage conversion to 380 kV including a new 380/220 kV transformer in Mühleberg. | 2027 | 3 | Permitting Procedure | Delayed | FALSE | ACTransmissionLine | Bassecourt | Mühleberg | AC | None | 45.4 | 138 | 0.69 | 10% | ++ | ++
1288 | Mettlen - Ulrichen | 264 | Reinforcement of the existing 220 kV line to 380 kV | 2035 | 3 | preliminary clarifications | Delayed | TRUE | ACTransmissionLine | Mettlen | Ulrichen | AC | None | 87.1 | 276 | 1.38 | 10% | ++ | ++ |  |  | 34 | HabitatsDirective
1290 | Magadino - Ulrichen | 265 | Replacement and extension of the lines in Western part of canton Tessin. The details are given in the link that is included in the project sheet: https://www.swissgrid.ch/content/swissgrid/en/home/projects/project-overview/allacqua-magadino.html | 2035 | 2 |  | Investment on time | TRUE | ACTransmissionLine | Magadino | Ulrichen | AC | None | 1 | 178 | 0.89 | +/- 10% | ++ | ++ |  | 2 1 | Other RAMSARSite None | Emerald Site
1721 | Magadino | 265 | Connection of the Avegno - Gorduno line to the Magadino substation and new 380/220 kV transformer in Magadino | 2035 | 2 | reschedule | Delayed | FALSE | ACTransmissionLine | Magadino | Magadino | AC | None | 0 | 34 | 0.17 | +/- 10% | ++ | ++ |  | 5 3
1286 | Chippis - Lavorgo | 266 | Reinforcement by construction of a new 380 kV route including a new 380/220 kV transformer in Mörel | 2029 | 3 | Permitting Procedure | Delayed | TRUE | ACTransmissionLine | Chippis | Lavorgo | AC | None | 124 | 360 | 1.8 | +/- 10% | ++ | ++
1733 | Bickigen - Chippis | 266 | Bickigen - Chippis: Optimisation of the existing route by voltage conversion to 380 kV | 2027 | 3 | Permitting procedure | Delayed | FALSE | ACTransmissionLine | Bickigen | Chippis | AC | None | 106.6 | 50 | 0.25 | + / - 10% | ++ | ++
1734 | Chamoson - Chippis | 266 | Chamoson - Chippis: Reinforcement by new construction of a 380 kV route New 380/220 kV transformer in Chippis | 2022 | 4 | Permitting procedure | Delayed | FALSE | ACTransmissionLine | Chamoson | Chippis | AC | None | 30 | 166 | 0.83 | +/- 10 % | ++ | ++
1262 | Hansa PowerBridge II | 267 | Possible second HVDC cable interconnector between southern Sweden (Bidding area SE4) and Germany (50Hertz). This project candidate is driven by market based target capacities found in the Common Planning Studies by Regional Group Baltic Sea. | 2030 | 1 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | Hurva (SE4) | Guestrow (DE) | DC | None | 300 | 660 | 1 | +-10% | ++ | ++ | +
1211 | HVDC Aragon region -Marsillon | 270 | New axis Aragon region -Marsillon | 2030 | 2 |  | Rescheduled | TRUE | DCTransmissionLine | Aragon region | Marsillon | DC | None | 230 | 1089.41 | 3.26 | 10% | ++ | ++ |  | 61 | 12 | HabitatsDirective
1212 | New axis Ejea-Aragon region 400 kV | 270 | New AC line (double circuit 400kV) between Ejea and Aragon region where the converter station is located | 2030 | 2 |  | Rescheduled | FALSE | ACTransmissionLine | Ejea de los Caballeros | Aragon region | AC | None | 110 | 62.59 | 2.72 | 10% | ++ | ++
1214 | Ejea de los Caballeros subestation | 270 | New 400kV Ejea de los Caballeros subestation and connection to the lines La Serna-Magallon and Magallon Peñalba | 2030 | 2 |  | Rescheduled | FALSE | OnshoreSubstation | Ejea de los Caballeros | Ejea de los Caballeros | AC | None | 0 | 8 | 0.02 | 10% | ++ | ++
1215 | Aragon region subestation | 270 | New 400 kV Aragon region subestation and connection to existing network and future cross border project | 2030 | 2 |  | Rescheduled | FALSE | OnshoreSubstation | Aragon region | Aragon region | AC | None | 0 | 10 | 0.03 | 10% | ++ | ++
1206 | HVDC Pamplona area - Cantegrit | 276 | HVDC Pamplona area(Spain) -Cantegrit (France) | 2029 | 2 |  | Rescheduled | TRUE | DCTransmissionLine | Pamplona area | Cantegrit | DC | None | 225 | 1192 | 5.33 | 10% | ++ | ++ |  | 20 | 2 | HabitatsDirective
1207 | Upgrade Cantegrit-Saucats | 276 | Upgrade of 2* 400 kV lines Cantegrit-Saucats | 2029 | 2 |  | Rescheduled | FALSE | ACTransmissionLine | Cantegrit | Saucats | AC | None | 70 | 130 | 2 | 10% | ++ | ++
1208 | Upgrade Cantegrit-Marsillon | 276 | Upgrade of existing 2*225kV line Cantegrit-Marsillon to 1* 400kV | 2029 | 2 |  | Rescheduled | FALSE | ACTransmissionLine | Cantegrit | Marsillon | AC | None | 80 | 140 | 2 | 10% | ++ | ++
1210 | New substation Pamplona area | 276 | New substation Pamplona area 400 kV and connection to the 400 kV line Ichaso-Castejón/Muruarte? | 2029 | 2 |  | Rescheduled | FALSE | OnshoreSubstation | Pamplona area | Pamplona area | AC | None | 0 | 8 | 0.17 | 10% | ++ | ++
1008 | Study Lonny-Achene-Gramme | 280 | Installation of PST(s) and/or line capacity upgrade of Lonny-Achene-Gramme. On this axis multiple needs are required : by 2025, installation of a PST at Achêne (planned in the Belgium NDP) to secure the current transfer capacity with the Nuclear shutdown in Belgium that could affect directly axis "Lonny-Achêne-Gramme" with closing of power plant of Tihange. By 2030, to increase the transfer capacity between France and Belgium, Project 280 (HTLS reinforcement + use of PST set in 2025 + additionnal PST) is under consideration in TYNDP 2020. As the two set of reinforcement are on the same axis, for sure they will interact together but the goal is not exactly the same | 2030 | 1 |  | Investment on time | TRUE | ACTransmissionLine | Lonny (FR) | Gramme (BE) | AC | None | 0 | 90 | 0.1 | 25%
1378 | TuNur DC | 283 | TuNur DC consists in a +/- 500 kV DC overhead line in Tunisia from the CSP plant to the shoring point, submarine cables from the Tunisian Northern coast to Montalto di Castro in Italy and VSC HVDC converter stations at both terminal points. | 2026 | 1 | The Tunisian regulatory framework has been settled only recently and this delayed the overall permitting process. | Delayed | TRUE | OffshoreDCTransmissionCable | Rejim Maatoug (TN) VSC HVDC - 400 kV AC +/- 500 kV DC – 2x 1GW | Montalto di Castro (IT) VSC HVDC - 400 kV AC +/- 500 kV DC – 2x 1GW | DC | Bipolar | 1270 | 2680 | 41 | 8% | ++ | ++ |  | 1 |  |  |  | TuNur DC: Job Creation - Creation of numerous qualified jobs in Tunisia for the construction and O&M of the land lines and HVDC converters
1430 | TuNur AC | 283 | 400 kV AC underground cables from the HVDC converter in Montalto to Terna’s 400 kV station in Montalto. CAPEX includes 2 circuit breaker bays within Terna’s station. | 2026 | 1 | The Tunisian regulatory framework has been settled only recently and this delayed the overall permitting process. | Delayed | FALSE | ACTransmissionLine | Montalto di Castro (IT) VSC HVDC - 400 kV AC +/- 500 kV DC – 2x 1GW | Montalto di Castro (IT) Terna station 400 kV AC | AC | None | 2 | 16 | 0.04 | 8% of the overall project cost as exact length is not yet confirmed, it being understood that the impact of the short AC cable on the overall project will be negligible. | ++ | ++ | [5 empty] | TuNur DC: Job Creation - Creation of numerous qualified jobs in Tunisia for the construction and O&M of the land lines and HVDC converters
1619 | LEG1 | 284 | 2000 MW subsea interconnector associated to a 150 MW solar power plant. | 2025 | 2 | LEG1 has been rescheduled to allow for 150 MW solar power plant (comprising energy storage) to be developped. GreenPower2020 feel this is necessary for 2 reasons: 1. to test and to qualify technologies in a given environment (hence not duplicating previous errors from others) and to identify the appropriate combination (PV + battery, CSP + steam, ...) before the utility-scale deployment of 2 x 1 GW. 2. To include energy generation as part of the project to enable LEG1's bi-lateral power exchange capability immediately. | Rescheduled | TRUE | OffshoreDCTransmissionCable | Tobrouk (Libya) | "Linoperamata (Greece, Crete)" | DC | Bipolar | 370 | 1500 | 30 | 15 | ++ | ++ | [5 empty] | By optimizing the flow between the 2 regions (according to seasonality), LEG1 will bring affordable electrical power to a country which is in great need to develop its industry/commerce to reach stability and peace. Furthermore, LEG1 will offer an export channel to all investors wishing to invest in solar or wind farms (for which Egypt and Libya have great proven potential), creating jobs and hard currency for the respective economies. And more prosperity means less migratory pressure which is of great concern for the EU.
1383 | GridLink | 285 | UK-France, 1.5GW HVDC Interconnector | 2022 | 2 |  |  | TRUE | OffshoreDCTransmissionCable | Kingsnorth (UK) | Warande (Gravelines, France) | DC | None | 156 | 906 | 23.9 | +/- 10% | ++ | ++ | +
1385 | Greenlink | 286 | A subsea HVDC interconnector between Wales and Ireland | 2023 | 2 | The PCI was delayed due to regulatory processes in the Republic of Ireland which have now been remedied. The Commission for Regulation of Utilities (CRU), on 21 October 2017, directed EirGrid to progress grid applications from interconnectors with PCI status, including Greenlink; also the CRU issued an information paper on 21 March 2018 acknowledging Greenlink’s application and setting out the timeframe to develop, consult, and make an initial decision on, Greenlink’s application by 30 September 2018. | Delayed | TRUE | OffshoreDCTransmissionCable | Great Island | Pembroke | DC | None | 195 | 396 | 8 | +/-10% | ++ | ++ | + | 0.08 7.8 49.6 0.7 0.4 22.3 36.9 0.7 3.2 |  |  |  | Greenlink is in the permitting stage. Desk-based environmental and technical assessments have been completed and a programme of environmental surveys has been completed, including a full suite of marine surveys, to ensure the design of the project fully considers all environmental constraints. Routing options have been selected following discussions with statutory consultees and other key stakeholders. The PCI will pass through seven European sites: River Barrow and River Nore SAC (Ireland); Hook Head SAC (Ireland); Pembrokeshire Marine SAC (Wales); Castlemartin Coast SPA (Wales); Limestone Coast of South West Wales SAC (Wales); Skomer, Stokholm and the seas off Pembrokeshire SPA (Wales); and West Wales Marine SAC (Wales). As a result of careful routeing and the adoption of low impact installation technologies (including the adoption of Horizontal direction Drills at landfalls) the PCI has minimised or avoided the most sensitive habitats. The PCI has been unable to avoid crossing reef habitats within the Pembroke Marine Special Area of Conservation. Using the results of subsea surveys and input from technical experts and Natural Resources Wales the PCI has minimised any impact on the reef habitats and appropriate environmental compensation is currently being agreed as part of an ongoing IROPI process lead by Natural Resources Wales. An Environmental Impact Assessment has been completed for the PCI. An Environmental Statement has been completed for the Welsh onshore and marine components of the PCI. An Environmental Impact Assessment Report has been completed for the Irish onshore and marine components. All documents have been submitted apart from the documentation relating to onshore Ireland which is due for submission shortly.
1431 | Southern Aegean Interconnector | 293 | New DC link (2 converter SS + 245 km DC subm. cable) to connect 582MW of offshore WF generation to the mainland (Area of Athens and Crete Island) | 2024 | 1 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | Lavrio | Levitha | DC | None | 245 | 600 | 40 | 5% | ++ | ++
1432 | Southern Aegean Interconnector | 293 | Interconnection of the Crete Island to the Greek Mainland via Levitha converter station. | 2026 | 1 |  | Investment on time | FALSE | OffshoreDCTransmissionCable | Levitha | Atherinolakkos Crete | DC | None | 250 | 600 | 40 | 5% | ++ | ++
1433 | Southern Aegean Interconnector | 293 | Connection Wind Farms with AC Substations at Levitha and Syrna | 2025 | 1 |  | Investment on time | FALSE | OffshoreACTransmissionCable | Levitha | Syrna | AC | None | 81 | 150 | 7 | 5% | ++ | ++
1434 | Southern Aegean Interconnector | 293 | AC Submarine cable to connect Kinaros substation to the AC side of Levitha Substation | 2024 | 1 |  | Investment on time | FALSE | OffshoreACTransmissionCable | Kinaros | Levitha | AC | None | 14 | 30 | 1 | 5% | ++ | ++
1435 | Southern Aegean Interconnector | 293 | HVAC Submarine cable to connect Kandeliousa OffsHore Wind Farm HV substation to Syrna HV Subsation | 2025 | 1 |  | Investment on time | FALSE | OffshoreACTransmissionCable | Kandeliousa | Syrna | AC | None | 34 | 80 | 6 | 5% | ++ | ++
1436 | Southern Aegean Interconnector | 293 | HVAC Submarine cable connect Kandeliousa offshore Wind Farm HV substation to Pergousa HV Substation | 2025 | 1 |  | Investment on time | FALSE | OffshoreACTransmissionCable | Kandeliousa | Pergousa | AC | None | 14 | 40 | 2 | 5% | ++ | ++
1704 | Southern Aegean Interconnector | 293 | HVAC Submarine cable connecting Levitha offshore Wind Farm HV substation to Dodecanese (Kos & Rhodes HV Substation) | 2026 | 1 |  | New Investment | FALSE | OffshoreACTransmissionCable | Levitha | Kos - Rhodes | AC | None | 170 | 330 | 10 | 5% | ++ | ++
1437 | Britib | 296 | Interconnection project between South-West England (United Kingdom), Cordemais (France) and Basque Country (Spain) in a multiterminal VSC HVDC bipole configuration of +/- 500-600 kV with 3 inputs/outputs of 1800 MW each, and a mostly subsea route from Spain to Great Britain along the French coast of about 1330 km in total. | 2026 | 1 | Awaiting PCI status | Rescheduled | TRUE | OffshoreDCTransmissionCable | Gatica/Hernani (Spain), Cordemais (France) and Langage/Indian Queens (United Kingdom) | Gatica/Hernani (Spain), Cordemais (France) and Langage/Indian Queens (United Kingdom) | DC | Bipolar | 1330 | 2040 | 20 | +/- 10% | ++ | ++ | +
445 | BRABO II: Zandvliet - Lillo - Liefkenshoek | 297 | The second phase of the BRABO project consists of the construction of a new double circuit 380kV overhead line from Zandvliet via Lillo to Liefkenshoek where the new line will be the temporarily connected to the existing 380kV line Doel-Mercator.This new line will be constructed making use of the corridor of the existing 150kV overhead line Zandvliet-Oorderen-Lillo, which will be undergrounded. | 2020 | 4 |  | Investment on time | TRUE | ACTransmissionLine | Zandvliet | Lillo - Liefkenshoek | AC | None | 18 | 100 | 0.1 | 5% | ++ | ++ |  | 1.5 1
604 | BRABO III: Liefkenshoek - Mercator | 297 | The existing 150kV overhead will be upgraded to a single 380kV overhead line between the site Liefkenshoek and the substation Mercator. To facilitate this upgrade, the adjacent 150kV grid will be adapted. | 2025 | 3 |  | Investment on time | FALSE | ACTransmissionLine | Liefkenshoek (BE) | Mercator (BE) | AC | None | 19 | 70 | 0.1 | 25% | ++ | ++ |  | 4 | 14.7 | HabitatsDirective
605 | BRABO II: Lillo 380 | 297 | "This concerns the construction of the 380kV substation Lillo, including a 380/150 kV transformer, as part of the second phase of the BRABO-project." | 2019 | 4 |  | Investment on time | FALSE | OnshoreSubstation | Lillo (BE) | Lillo (BE) | AC | None | 0 | 15 | 0.1 | 5% | ++ | ++ |  |  | 15.5 | HabitatsDirective
1458 | SACOI3 | 299 | New HVDC triterminal link between Italy mainland, Corsica and Sardinia replacing existing link SACOI2 | 2024 | 3 |  | Investment on time | TRUE | DCTransmissionLine | Codrongianos - Lucciana | Suvereto | DC | Bipolar | 300 | 900 | 7 | 10 | ++ | ++ |  | 1 | 3 | Other | -
1628 | NeuConnect Interconnector | 309 | 1.4GW HVDC Interconnector between UK and Germany | 2023/4 | 3 |  | New Investment | TRUE | OffshoreDCTransmissionCable | Grain West 400kV Substation | Fedderwarden 380kV Substation | DC | None | 700 | 1600 | 32.5 | +/- 15% | ++ | ++ | +
1472 | St. Peter (AT) - Tauern (AT) | 312 | new 380-kV-Line | 2025 | 4 | Duration of permitting process. | Delayed | TRUE | ACTransmissionLine | St. Peter | Tauern | AC | None | 128 | 890 | 4 | 10% | ++ | ++ |  |  | 43 | None
1473 | Isar/Altheim/Ottenhofen - St. Peter | 313 | New 380kV double circuit OHL Isar/Altheim/Ottenhofen - St. Peter including new 380kV switchgears Altheim, Pirach, Simbach and St. Peter. | 2024 | 3 | Delay due to complex and long permitting process | Delayed | TRUE | ACTransmissionLine | Isar/Altheim/Ottenhofen (DE) | St. Peter (AT) | AC | None | 90 | 384 | 3 | 10 | ++ | ++ |  | 4 | OtherNatureProtectionAreasUnderNationalLaw
1558 | Double 400 kV OHL Cirkovce(SI)-Heviz(HU)/Zerjavinec(HR) | 320 | New double circuit 400kV overhead line in Slovenia (section Cirkovce-Pince) and a new 400 kV substation Cirkovce (SI). The new OHL will be connected to one circuit of the existing double circuit 400kV OHL Heviz(HU)-Zerjavinec(HR), creating two new cross-border lines: Heviz(HU)-Cirkovce(SI) and Cirkovce (SI)-Zerjavinec (HR). | 2021 | 4 |  | Investment on time | TRUE | ACTransmissionLine | Cirkovce (SI) | Heviz (HU) \ Zerjavinec (HR) | AC | None | 80 | 132.5 | 0.12 | +/- 5% | ++ | ++ |  | 28 | 37 | OtherNatureProtectionAreasUnderNationalLaw
1476 | Wullenstetten - Border Area (DE-AT) | 322 | Between point Wullenstetten and point border area (DE-AT) an upgrade of an existing 380-kV-line is necessary (grid enhancement). Thereby, a significantly higher transmission capacity is realized. Between switching point Neuravensburg and Austrian National border (AT) a new line with a significantly higher transmission capacity will be constructed in an existing corridor (grid enhancement). | 2025 | 3 | Scope of the project changed due to technical reasons. | Delayed | TRUE | ACTransmissionLine | Wullenstetten (DE) | Austrian National border (AT) | AC | None | 95 | 113.5 | 0.9 | 10% | ++ | ++
1478 | Dekani (SI) - Zaule (IT) interconnection | 323 | The Zaule (IT) - Dekani (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E3 d.o.o. and HSE d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Zaule (IT) substation to Dekani substation, including a 110/135 kV Phase Shifter Transformer. | 2025 | 3 | The promoters asked to the respective NRA for the NTC recalculation not subject to conditions (EG. third party network reinforcements), which will be guaranteed for the exemption period and from the entry into the new commercial operation date (COD) of the interconnector. | Delayed | TRUE | ACTransmissionLine | DEKANI | ZAULE | AC | None | 11 | 15.6 | 0.3 | 7% | ++ | 0
1482 | Redipuglia (IT) - Vrtojba (SI) Interconnection | 324 | "The Redipuglia (IT) - Vrtojba (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E3 d.o.o. and HSE d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Redipuglia (IT) substation to Vrtojba (SI) substation, including a 110/135 kV Phase Shifter Transformer." | 2023 | 3 | The promoter asked the respective NRA for the NTC recalculation not subject to conditions (eg third party network reinforcements), which will be guaranteed for the exemption period and from the entry into the new commercial operation date (COD) of the interconnector. | Delayed | TRUE | ACTransmissionLine | REDIPUGLIA | VRTOJBA | AC | None | 22.5 | 24.3 | 0.4 | 7% | ++ | 0
1483 | Upgrade Obersielach (AT) - Podlog (SI) | 325 | upgrade from 220 kV to 380 kV | 2034 | 1 |  | New Investment | TRUE | ACTransmissionLine | Obersielach (AT) | Podlog (SI) | AC | None | 70 | 210 | 0.5 | 10 | ++ | ++ |  | 4 | 81 | OtherNatureProtectionAreasUnderNationalLaw
1620 | Substation Aach | 328 | New 400/220-kV-substation | 2025 | 2 |  | Investment on time | FALSE | OnshoreSubstation | N/A | N/A | AC | None | 0 | 40 | 0.32 | 10% | ++ | ++ | [5 empty] | The project replaces an existing overhead line.
1629 | Substation Bofferdange | 328 | New 400/220/110 kV substation including transformer 400/220 kV to be commissioned in Bofferdange (LU) | 2025 | 2 |  | Investment on time | FALSE | OnshoreSubstation | N/A | N/A | AC | None | 0 | 42 | 0.34 | 10% | ++ | ++ | [5 empty] | The project replaces an existing overhead line.
1630 | AC Overhead Line Aach-Bofferdange | 328 | New AC Overhead Line between Germany and Luxembourg | 2026 | 2 |  | Investment on time | TRUE | ACTransmissionLine | Aach (DE) | Bofferdange (LU) | AC | None | 40 | 83.5 | 0.67 | 10% | ++ | ++ | [5 empty] | The project replaces an existing overhead line.
1518 | Stevin-Izegem/Avelgem: new corridor | 329 | Realisation of a new AC corridor up to 6 GW capacity | 2028 | 2 |  | Investment on time | TRUE | ACTransmissionLine | Stevin | Courcelles | AC | None | 90 | 400 | 0.3 | 25% | ++ | ++
1498 | New CZ-SK 400 kV interconnector | 330 | This investment consists of single circuit 400 kV OHL Otrokovice (CZ) - Ladce (SK). | 2035 | 1 |  | New Investment | TRUE | ACTransmissionLine | Otrokovice (CZ) | Ladce (SK) | AC | None | 78 | 83.2 | 0.37 | ±10% | ++ | ++
1499 | Extension of the new 400 kV substation Ladce | 330 | This investment consists of extension the new 400 kV substation Ladce, in order to loop 400 kV cross-border OHL from Ladce (SK) to Otrokovice (CZ). The new 400 kV substation Ladce will replace existing 220 kV substation Považská Bystrica and will therefore increase security of supply in this particular region. After commissioning this new 400 kV substation it will be possible to commission new 400 kV cross-border OHL from Ladce (SK) to Otrokovice (CZ). | 2027 | 2 |  | New Investment | FALSE | OnshoreSubstation | Ladce (SK) | Ladce (SK) | AC | None | 0 | 3.1 | 0.25 | ±10% | ++ | ++
1496 | PST Foretaille | 333 | Installation of two PSTs in Foretaille that control the flow on the Foretaille - Verbois 220 kV double line | 2031 | 1 |  | Investment on time | TRUE | PhaseShiftingTransformer | Foretaille | Foretaille | AC | None | 0 | 35 | 0.18 | 10%
1504 | Power Link Island | 335 | Artificial island central in the North Sea (best location for the first hub is under investigation) with a 'copper plate' type electrical installation suitable to connect 12GW of HVDC systems to shore and up to 12GW of nearby offshore wind. The artificial island is large enough to host all equipment HVDC converters and O&M facilities. Reduction of the total system cost is essential to facilitate large scale offshore wind and interconnection capacity deployment and all options in design, installation and operation should be considered to further reduce cost, including the use of a power hub as an island. Realising a power hub as an island located centrally in the North Sea has been assessed to be technically feasible, based on - amongst others - bathymetry, extreme wind speed and hydraulic conditions (wave heights, surge levels, etc.) and geotechnical data. | 2035 | 1 |  | New Investment | TRUE | OffshoreSubstation | 0 | 0 | AC | None | 0 | 2222 | 11 | The Capex uncertainty range for this asset is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this. | ++ | ++
1505 | Interconnection DKw to Power Link Island | 335 | HVDC connector including substations interfacing the Power Link Island and the Western Danish power system. | 2035 | 1 |  | New Investment | FALSE | OffshoreDCTransmissionCable | "Endrup, DKw" | Power Link Island DKw | DC | None | 328 | 1310 | 4.3 | The Capex uncertainty range for this 525kV link covers -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this. | ++ | ++
1506 | Interconnection NL Maasvlakte to Power Link Island | 335 | One of two HVDC connectors including substations interfacing the Power Link Island and the Dutch power system. | 2035 | 1 |  | New Investment | FALSE | OffshoreDCTransmissionCable | Maasvlakte 380 kV | Power Link Island NL1 | DC | None | 360 | 1375 | 4.4 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this. | ++ | ++
1507 | Interconnection NL Eemshaven to Power Link Island | 335 | One of two HVDC connectors including substations interfacing the Power Link Island and the Dutch power system. | 2035 | 1 |  | New Investment | FALSE | OffshoreDCTransmissionCable | Eemshaven 380 kV | Power Link Island NL2 | DC | None | 290 | 1233 | 4.2 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this. | ++ | ++
1508 | Interconnection DE (area of Brunsbüttel) to Power Link Island | 335 | One of three HVDC connectors including substations interfacing the Power Link Island and the German power system. | 2035 | 1 |  | New Investment | FALSE | OffshoreDCTransmissionCable | German substation located in the area of Brunsbüttel (north of the Elbe) | Power Link Island DE1 | DC | None | 390 | 1639 | 5.3 | The Capex for the 640kVHVDC links are extrapolated from 525kV HVDC links and therefore are subject to the same uncertainty range. Furthermore, additional needed internal reinforcements that can have a fundamental impact on the costs have not yet been analysed. | ++ | ++
1509 | Interconnection DE (area of Oldenburg) to Power Link Island | 335 | One of three HVDC connectors including substations interfacing the Power Link Island and the German power system. | 2035 | 1 |  | New Investment | FALSE | OffshoreDCTransmissionCable | German substation located in the area of Oldenburg | Power Link Island DE2 | DC | None | 400 | 1661 | 5.3 | The Capex for the 640kVHVDC links are extrapolated from 525kV HVDC links and therefore are subject to the same uncertainty range. Furthermore, additional needed internal reinforcements that can have a fundamental impact on the costs have not yet been analysed. | ++ | ++
1511 | Interconnection DE (area of Krümmel) to Power Link Island | 335 | One of three HVDC connectors including substations interfacing the Power Link Island and the German power system. | 2035 | 1 |  | New Investment | FALSE | OffshoreDCTransmissionCable | German substation located in the area of Krümmel | Power Link Island DE3 | DC | None | 490 | 1860 | 5.6 | The Capex for the 640kVHVDC links are extrapolated from 525kV HVDC links and therefore are subject to the same uncertainty range. Furthermore, additional needed internal reinforcements that can have a fundamental impact on the costs have not yet been analysed. | ++ | ++
1556 | Prati (IT) – Steinach (AT) | 336 | New Italy-Austria tie-line between the existing 110kV Steinach substation in Austria and 132 kV Brennero substation, including PST; and connection to 132 kV Prati di Vizze substation." | 2023 | 4 | rescheduled | New Investment | TRUE | ACTransmissionLine | Prati di Vizze (IT) | Steinach (AT) | AC | None | 139 | 40 | 0.6 | 0 % | ++ | ++
1521 | New HVDC line between Villanova and Fano existing 400 kV substations | 338 | HVDC lines | 2030 | 2 |  | New Investment | TRUE | OffshoreDCTransmissionCable | Villanova | Fano | DC | None | 400 | 1115 | 17.81 | 10 | ++ | ++
1557 | Italian HVDC tri-terminal link | 339 | Italian HVDC tri-terminal link | 2025 | 2 |  | Investment on time | TRUE | OffshoreDCTransmissionCable | SARDINIA REGION | SICILY REGION - SOUTH OF ITALY | DC | None | 900 | 2600 | 13 | 10 | ++ | ++ |  | 43 | 36 | Other | -
1519 | Avelgem-Center: new corridor | 340 | Realisation of a 6 GW new corridor including PSTs | 2028 | 2 |  | Investment on time | TRUE | ACTransmissionLine | Avelgem | Center (TBD) | AC | None | 100 | 500 | 0.5 | 25% | ++ | ++
1536 | Portile de Fier (RO) - Djerdap (RS) 2nd | 341 | Portile de Fier (RO) - Djerdap (RS) 2nd . Doubling the existing OHL 400 kV (1.5 km on Serbian (thermal limit 1800 A) and 0.5 km on Romanian( thermal limit 2192 A) Side) | 2030 | 1 |  | Investment on time | TRUE | ACTransmissionLine | Portile de Fier | Djerdap | AC | None | 2 | 3.5 | 0.03 | 5% | ++ | ++
1537 | New SS 400/110 kV Belgrade West | 341 | New SS 400/110 kV Belgrade West | 2030 | 1 |  | Investment on time | FALSE | Transformer | Belgrade West | Belgrade West | AC | None | 0 | 22 | 0.33 | 5% | ++ | ++
1538 | New OHL 400 kV WPP Cibuk - SS Belgrade West | 341 | """New OHL 400 kV WPP Cibuk - SS Belgrade West""" | 2030 | 1 |  | Investment on time | FALSE | ACTransmissionLine | WPP Cibuk | Belgrade West | AC | None | 60 | 14 | 0.15 | 5% | ++ | ++
1520 | Sofia West (BG) - Nis 2 (RS) 2nd | 342 | Second interconnection line on the border between Bulgaria and Serbia | 2034 | 2 |  | Investment on time | TRUE | ACTransmissionLine | SS Sofia West | SS Nis 2 | AC | None | 123 | 56 | 0.5 | 5% | ++ | ++
1522 | Upgrade of exsisting OHL 220 kV to 400 kV SS Nis 2 - SS Kruševac 1 | 342 | Upgrade of exsisting OHL 220 kV to 400 kV SS Nis 2 - SS Kruševac 1 | 2034 | 2 |  | Investment on time | FALSE | ACTransmissionLine | SS Nis 2 | SS Krusevac 1 | AC | None | 72 | 17 | 0.2 | 5% | ++ | ++
1523 | Upgrading SS 220/110 kV Krusevac 1 to 400 kV | 342 | Upgrading SS 220/110 kV Krusevac 1 to 400 kV | 2034 | 2 |  | Investment on time | FALSE | OnshoreSubstation | SS Krusevac 1 | SS Krusevac 1 | AC | None | 0 | 6.5 | 0.08 | 5% | ++ | ++
1524 | Upgrading of exsisting OHL 220 kV to 400 kV SS Krusevac 1 - SS Kraljevo 3 | 342 | Upgrading of exsisting OHL 220 kV to 400 kV SS Krusevac 1 - SS Kraljevo 3 | 2034 | 2 |  | Investment on time | FALSE | ACTransmissionLine | SS Krusevac 1 | SS Kraljevo 3 | AC | None | 48 | 11.5 | 0.1 | 5% | ++ | ++
1525 | Uprading exsisting OHL 220 kV to 400 kV SS Kraljevo 3 - SY Pozega | 342 | Uprading exsisting OHL 220 kV to 400 kV SS Kraljevo 3 - SY Pozega | 2034 | 2 |  | New Investment | FALSE | ACTransmissionLine | EMS | EMS | AC | None | 70 | 32 | 0.5 | 5% | ++ | ++
1698 | New 400 kV SY Pozega | 342 | New 400 kV SY Pozega | 2034 | 2 |  | New Investment | FALSE | OnshoreSubstation | SS Pozega | SS Pozega | AC | None | 0 | 2 | 0.1 | +/- 5% | ++ | ++
1699 | New OHL SS Jagodina 4 - SY Drmno | 342 | New OHL SS Jagodina 4 - SY Drmno | 2034 | 2 |  | New Investment | FALSE | ACTransmissionLine | SS Jagodina 4 | SY Drmno | AC | None | 95 | 26 | 0.1 | +/- 5% | ++ | ++
1700 | OHL SS Pozega - SS Pljevlja | 342 | Upgrading 220 kV OHL SS Pozega - node Vardiste to 2x400 kV and conductoring second circuit on 400 kV OHL SS Bajina Basta - SS Pljevlja from node Vardiste to SS Pljevlja. | 2034 | 2 |  | New Investment | FALSE | ACTransmissionLine | SY Pozega | SS Pljevlja | AC | None | 135 | 18 | 0.05 | 5% | ++ | ++
1701 | OHL SS Pozega - SS Visegrad | 342 | Upgrading 220 kV OHL SS Pozega - node Vardiste to 2x400 kV and conductoring second circuit on 400 kV OHL SS Bajina Basta - SS Visegrad from node Vardiste to SS Visegrad.. | 2034 | 2 |  | New Investment | FALSE | ACTransmissionLine | SY Pozega | SS Visegrad | AC | None | 65 | 13 | 0.05 | 5% | ++ | ++ |  | 15.7 | OtherNatureProtectionAreasUnderNationalLaw
1532 | New OHL 400 kV Banja Luka - Lika | 343 | New OHL 400 kV Banja Luka - Lika | 2030 | 2 |  | Rescheduled | FALSE | ACTransmissionLine | Banja Luka (BA) | Lika (HR) | AC | None | 180 | 53 | 0.0648 | ±10% | ++ | ++
1533 | New OHL 400 kV Lika – Melina | 343 | New OHL 400 kV Lika – Melina | 2030 | 2 |  | Investment on time | FALSE | ACTransmissionLine | Lika (HR) | Melina (HR) | AC | None | 68 | 24.24 | 0.02448 | ±10% | ++ | ++
1534 | New OHL 400 kV Lika – Konjsko | 343 | New OHL 400 kV Lika – Konjsko | 2030 | 2 |  | Investment on time | TRUE | ACTransmissionLine | Lika (HR) | Konjsko (HR) | AC | None | 203 | 71 | 0.07308 | ±10% | ++ | ++
1535 | New Substation 400/110 kV Lika | 343 | New Substation 400/110 kV Lika | 2029 | 2 |  | Rescheduled | FALSE | OnshoreSubstation | Lika (HR) | Lika (HR) | AC | None | 0 | 11.9 | 0.1785 | ±10% | ++ | ++
1541 | Zwolle-Hengelo-Doetinchem-Dodewaard | 344 | Upgrade of existing 380kV circuits between Zwolle, Hengelo, Doetinchem and Dodewaard from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 2040 | 1 |  | Rescheduled | TRUE | ACTransmissionLine | Zwolle | Dodewaard | AC | None | 165 | 210 | 2.1 | 10% | ++ | ++
1544 | ZuidWest3808 Oost | 346 | New 380 kV substation Tilburg; New 380 kV double circuit line 2645MVA between Rilland and Tilburg | 2029 | 3 |  | Rescheduled | TRUE | ACTransmissionLine | Rilland | Tilburg | AC | None | 80 | 1090 | 5.5 | 10% | ++ | ++ | +
1546 | NoordWest380 | 348 | Upgrade of existing 220kV circuits between Eemshaven and Vierverlaten to 2* 380kV – 2645MVA circuits; New 380kV substation Vierverlaten | 2023 | 4 |  | Rescheduled | TRUE | ACTransmissionLine | Eemshaven Oude Schip | Vierverlaten | AC | None | 40 | 411 | 2.1 | 10% | ++ | ++ | + |  |  |  |  | More info: https://www.rvo.nl/onderwerpen/bureau-energieprojecten/lopende-projecten/hoogspanning/eemshaven-os-vierverlaten-380-kv
1638 | Mares Cable 1: Cross Irish Sea Interconnector Cable | 349 | HVDC 750MW 320kV bipole interconnector between UKNG and EIRGRID | 2025 | 2 |  | Rescheduled | TRUE | DCTransmissionLine | Bodelwyddan | Maynooth | DC | None | 211 | 253 | 1 | 15% | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1639 | Enabling Works 1: Bellacorick-Oldstreet 2 x 245kV OHL | 349 | 2 x 400MW 275kV OHL | 2025 | 2 |  | New Investment | FALSE | ACTransmissionLine | Bellacorick Replacement | Oldstreet 400kV | AC | None | 160 | 100 | 0.5 |  | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1640 | Mares Cable 2: Cross Ireland Interconnector Cable | 349 | 750MW 320kV VSC HVDC Interconnector | 2025 | 2 |  | New Investment | FALSE | DCTransmissionLine | Maynooth | Bellacorick Replacement | DC | None | 255 | 186 | 1 | 15% | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1641 | Mares Converter Station 3 | 349 | 750MW 320kV VSC HVDC Convertor Station to connect to EIRGRID AC | 2025 | 2 |  | New Investment | FALSE | OnshoreSubstation | Bellacorick replacement | Bellacorick replacement | DC | None | 0 | 105 | 3 |  | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1642 | Mares Converter Station 2 | 349 | 750MW 320kV VSC HVDC Convertor Station to connect to EIRGRID AC | 2025 | 2 |  | New Investment | FALSE | OnshoreSubstation | Maynooth | Maynooth | DC | None | 0 | 105 | 3 | +/- 15% | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1646 | Mares Converter Station 1 | 349 | 750MW 320kV VSC HVDC Convertor Station to connect to UKNG | 2025 | 2 |  | New Investment | FALSE | OnshoreSubstation | Bodelwyddan | Bodelwyddan | DC | None | 0 | 105 | 3 |  | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1647 | MAREX Wind infeed cable 1 | 349 | 245kV 400MW AC cable | 2025 | 2 |  | New Investment | FALSE | OnshoreACTransmissionCable | MAREX Wind 1 | Bellacorick Replacement | AC | None | 25 | 25 | 0.2 | 15% | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1648 | MAREX Wind Infeed cable 2 | 349 | 245kV 400MW AC cable | 2025 | 2 |  | New Investment | FALSE | OnshoreACTransmissionCable | MAREX Wind 2 | Bellacorick Replacement | AC | None | 25 | 25 | 0.2 | 15% | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1649 | MAREX Wind Infeed cable 3 | 349 | 245kV 400MW AC cable | 2025 | 2 |  | New Investment | FALSE | OnshoreACTransmissionCable | Marex Wind 3 | Bellacorick Replacement | AC | None | 25 | 25 | 0.2 | 15% | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1650 | MAREX Wind Infeed Cable 4 | 349 | 245kV 400MW AC cable | 2025 | 2 |  | New Investment | FALSE | OnshoreACTransmissionCable | MAREX Wind 4 | Bellacorick Replacement | AC | None | 20 | 20 | 0.2 | 15% | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1651 | Enabling Works 2: Glinsk Bellacorick Replacement 10 x 245kV bay substation | 349 | 12 bay 245kV substation | 2025 | 2 |  | New Investment | FALSE | OnshoreSubstation | Bellacorick Replacement | Bellacorick Replacement | AC | None | 0 | 15 | 0.04 | 15% | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1652 | Enabling Works 3: 2 x 245kV Connection bays UKNG and associated works | 349 | AC Connection to UKNG system Bodelwyddan 2 number 245kV bays and associated works | 2025 | 2 |  | New Investment | FALSE | OnshoreSubstation | Bodelwyddan | Bodelwyddan | AC | None | 0 | 5 | 0.005 | 15% | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1653 | Enabling Works 4: EIRGRID 2 x 245kV Connection bays at Maynooth and associated works | 349 | EIRGRID 2 x 245kV Connection bays at Maynooth and associated works | 2025 | 2 |  | New Investment | FALSE | OnshoreSubstation | Maynooth | Maynooth | AC | None | 0 | 5 | 0.005 | 15% | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1654 | Enabling Works 5: EIRGRID 2 x 245kV Connection bays at Oldstreet and associated works | 349 | 2 x 245kV Connection bays at Oldstreet and associated works | 2025 | 2 |  | New Investment | FALSE | OnshoreSubstation | Oldstreet 220/400kV | Oldstreet 220/400kV | AC | None | 0 | 3 | 0.005 |  | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1655 | Enabling Works 6: 2 x 245/400 transformer at EIRGRID 220/400kV Substation Oldstreet | 349 | 2 x 245/400 transformer at EIRGRID 220/400kV Substation Oldstreet | 2025 | 2 |  | New Investment | FALSE | PhaseShiftingTransformer | Oldstreet 220/400kV | Oldstreet 220/400kV | AC | None | 0 | 15 | 0.02 | 15 | ++ | ++ | [5 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1622 | 400kV OHL SS Bitola - SS Elbasan | 350 | New 150km cross-border single circuit 400kV OHL between existing substation Bitola(Macedoonia) and Elbasan(Albania). | 2020 | 4 |  | New Investment | TRUE | ACTransmissionLine | Bitola | Elbasan | AC | None | 161 | 63.733 | 2.867 | 0 % | ++ | ++
1623 | 400 kV SS Ohrid | 350 | New 400/110 kV substation in Ohrid area connected in/out to the new 400 kV line Bitola-Elbasan. This SS will contribute to the security of supply in the internal southern network of the country. | 2020 | 4 |  | New Investment | FALSE | OnshoreSubstation | missing value | missing value | AC | None | 0 | 17.68 | 1.414 | 0% | ++ | ++
1555 | Lienz (AT) - Veneto region (IT) | 375 | Reconstruction of the existing 220kV-interconnection line between Lienz and Veneto Region (IT) | 2027 | 2 |  | New Investment | TRUE | ACTransmissionLine | Lienz (AT) | Veneto region (IT) | AC | None | 140 | 175 | 0.9 | 10 | ++ | ++ |  | 31 | 3 | Other | -
1559 | Refurbishment of the 400kV Meliti (GR)-Bitola (MK) interconnector | 376 | Reconductoring of the existing 400kV interconnection line Meliti (GR)-Bitola (MK) | 2036 | 1 |  | New Investment | TRUE | ACTransmissionLine | Meliti (GR) | Bitola (MK) | AC | None | 35.512 | 5.625 | 0.215 | ±20% | ++ | ++
1561 | BE-NL interconnector: upgrade VanEyck-Maasbracht | 377 | Upgrade of existing interconnection between Van Eyck (BE) and Maasbracht (NL), by adding PST(s) and/or replacing existing conductors by HTLS. The study is to confirm the appropriate implementation option and phasing of this implementation also with respect to evolution of DE-NL interconnectors. | 2030 | 1 |  | Investment on time | TRUE | ACTransmissionLine | VanEyck | Maasbracht | AC | None | 12 | 50 | 0.1 | 25% | ++ | ++
1584 | Transformer Gatica | 378 | Only 400 to 220 kV transformer. Not the whole substation | 2025 | 2 |  | New Investment | TRUE | OnshoreSubstation | GATICA 400 | GATICA 220 | AC | None | 0 | 8.16 | 0.1224 | 10%
1593 | Uprate Gatica-Guenes | 379 | Uprate 400 kV Gatica-Guenes substation | 2025 | 1 |  | New Investment | TRUE | ACTransmissionLine | Gatica | Guenes | AC | None | 38.8 | 0.22 | 0.0033 | 10% | ++ | ++
1595 | Uprate Gatica-Amorebieta-Ichaso | 379 | Uprate the 400 kV axis Gatica-Amorebieta-Ichaso | 2025 | 1 |  | New Investment | FALSE | ACTransmissionLine | Gatica | Ichaso | AC | None | 69.12 | 1.65 | 0.02475 | 10% | ++ | ++
1597 | Uprate Gatica-Azpeitia | 379 | Uprate the 400 kV Gatica-Azpeitia line | 2025 | 1 |  | New Investment | FALSE | ACTransmissionLine | Gatica | Azpeitia | AC | None | 57 | 0.31 | 0.00465 | 10% | ++ | ++
1692 | HVDC from Wilhelmshaven to Uentrop | 1034 | HVDC line from Wilhelmshaven to Uentrop to integrate onshore and offshore wind energy in Northern Germany and transport it to the load centers in Western Germany | 2030 | 2 |  | New Investment | TRUE | DCTransmissionLine | Wilhelmshaven | Uentrop | DC | Bipolar | 267 | 1735 | 13.9 | 10
1693 | HVDC from Heide/West to Polsum | 1034 | HVDC line from Heide/West to Polsum to integrate onshore and offshore wind energy in Northern Germany and transport it to the load centers in Western Germany | 2030 | 2 |  | New Investment | FALSE | DCTransmissionLine | Heide/West | Polsum | DC | Bipolar | 407 | 2646 | 21.2 | 10
1675 | SE North-south Long-term reinforcements | 1039 | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. The need for capacity is driven by RES integration in northern Sweden and nuclear decommission in southern Sweden. | 2040 | 1 |  | Investment on time | TRUE | ACTransmissionLine | SE2 | SE3 | AC | None | 950 | 2500 | 1 | +-10%
1677 | LirIC | 1040 | New HVDC VSC Monopole sub sea cable between Kilroot 275kV substation in Northern Ireland (TBC) and Hunterston 400kV sub station in Scotland (TBC) | 2027 | 1 | N/A | New Investment | TRUE | OffshoreDCTransmissionCable | NI Kilroot 275kV (TBC) | GB Hunterston 400kV (TBC) | DC | Monopolar | 133 | 446 | 9.93 | 20
1682 | Wadi El Natroon - Acharnes HVDC | 1041 | Wadi El Natroon - Acharnes HVDC Link. This investment includes two LCC converter stations at both ends of the bipolar 600kV HVDC link along with the grounding electrodes. The interconnection circuits consist of approximately 500km of overhead HVDC lines (ACSR/PLOVER), approximately 30km length of underground cables (Al 1800mm2) and approximately 843km of submarine Cables (Cu 1000mm2, Al 1300mm2). | 2028 | 1 |  |  | TRUE | DCTransmissionLine | Wadi El Natroon | Acharnes | DC | Bipolar | 1373 | 3525 | 76.186 | 10 |  |  |  | 83 | 18.5 | HabitatsDirective
1687 | AC Overhead Line 1 (Ras Ghareb-Nile West) | 1041 | AC 500KV interconnection line (double circuit OHL) which connects Wind Farms of Ras Ghareb to Nile West point | 2028 | 1 |  |  | TRUE | ACTransmissionLine | Ras Ghareb Wind Farms Substation | Nile West | AC | None | 420 | 232 | 0.772 | 10
1690 | AC Overhead Line 2 (Nile West-Wadi El Natroon EHV) | 1041 | AC 500KV Interconnection Lines (two double-circuit OHLs) which connect Nile West Point with Wadi El Natroon EHV Center | 2028 | 1 |  |  | TRUE | ACTransmissionLine | NILE WEST POINT | WADI EL NATROON | AC | None | 220 | 243 | 0.814 | 10
1694 | New 330 kV OHL Darbenai-Musa | 1042 | New 330 kV OHL Darbenai-Musa | 2030 | 1 | Investment depends on plans to build offshore wind farms | Delayed | TRUE | ACTransmissionLine | Darbnai | Muša | AC | None | 170 | 66 | 0.143 | +5%, - 5%
1695 | New 330 kV OHL Panevezys-Musa | 1042 | New 330 kV OHL Panevežys-Muša | 2030 | 1 | Investment depends on plans to build offshore wind farms | Delayed | FALSE | ACTransmissionLine | Panevežys | Muša | AC | None | 72 | 21.6 | 0.047 | +5%, - 5%
1685 | Dollern - Stade | 1043 | New 380kV double circuit OHL Dollern - Stade including new 380kV switchgear in Stade. Length 14km. | 2021 | 4 | Due to complex and long permisstin process | Delayed | FALSE | ACTransmissionLine | Dollern (DE) | Stade (DE) | AC | None | 14 | 20 | 0.2 | +-10%
1686 | Wahle - Mecklar | 1043 | New 380kV double circuit OHL Wahle - Mecklar including two new substations. Length: 210km. | 2024 | 4 | Due to complex and long permitting process | Investment on time | TRUE | ACTransmissionLine | Wahle (DE) | Mecklar (DE) | AC | None | 210 | 610 | 4.9 | +-10%
1688 | Nuojuankangas-Huutokoski | 1046 | New single circuit 400 kV OHLs will be built from central part of Finland to the northern area to increase the capacity between North and South Finland. Enables integration of renewables to the northern part of the country. | 2028 | 3 |  | New Investment | TRUE | ACTransmissionLine | Nuojuankangas | Huutokoski | AC | None | 290 | 120 | 0.1 | +/- 10
1689 | Tuomela B-Nuojuankangas | 1046 | New single circuit 400 kV OHL will be built to the northern part of Finland. Enables the integration of renewables to the northern part of the country and the increasing power transfer from North to South . | 2029 | 3 |  | New Investment | FALSE | ACTransmissionLine | Tuomela B | Nuojuankangas | AC | None | 100 | 70 | 0.1 | +/- 10
1697 | Petäjävesi-Hikiä | 1046 | New single circuit 400 kV OHL will be built to the central part of Finland. Enables the integration of renewables and the utilization of full transfer capacity from North to South . | 2030 | 2 |  | New Investment | FALSE | ACTransmissionLine | Petäjävesi | Hikiä | AC | None | 175 | 65 | 0.1 | +/-10
1691 | Emden-Eemshaven | 1047 |  | 2035 | 1 |  | New Investment | TRUE | OffshoreACTransmissionCable | Emden | Eemshaven | AC | None | 31 | 200 | 1.6 | +-10%
1709 | Greece Africa Power Interconnector | 1048 | 2 HVDC Subsea cables interconnecting the Northern coast of Egypt with the island of Crete at Atherinolakkos. At both connection points bipolar HVDC conversion stations will be constructed for the connection to the national HV grids. | 2028 | 1 |  | New Investment | TRUE | OffshoreDCTransmissionCable | Atherinolakkos (Crete) | Mersa Matruh | DC | Bipolar | 450 | 1700 | 25 | 5%
1706 | Converter Stations & Subsea Cabling | 1049 | 1.4 GW HVDC electricity interconnector between UK and Belgium Voltage Source Converter (VSC)/Bipolar Grid connection point (substations name): Kemsley (UK) and near Zeebrugge (Belgium), exact substation location subject to grid study in Belgium. Total cable length (substation to substation) 230km (1km in UK and 30km in France) Two cables (XLPE) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load. The annual Availability is 98.1% availability, with 1.8% planned outages, and 0.1% forced outages. The maximum single failure according to the design is 1.4GW. The project will enable the reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. There are no material anticipated environmental impacts during construction and operation. | 2025 | 1 |  | New Investment | TRUE | OffshoreDCTransmissionCable | Kemsley | Zeebrugge | DC | Bipolar | 230 | 746 | 28 | 6 |  |  |  | 1 |  |  |  | No other residual impact
1707 | Converter stations and Subsea Cabling | 1050 | 1.4 GW HVDC electricity interconnector between UK and Germany Voltage Source Converter (VSC)/Bipolar Grid connection point (substations name): Corringham (UK) and near Emden (Germany), exact substation location subject to grid study in Germany. Total cable length (substation to substation) 610km (35km in UK and 25km in Germany) Two cables (XLPE) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load. The annual Availability is 98.1% availability, with 1.8% planned outages, and 0.1% forced outages. The maximum single failure according to the design is 1.4GW. The project will enable the reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. There are no material anticipated environmental impacts during construction and operation | 2028 | 1 |  | New Investment | TRUE | OffshoreDCTransmissionCable | corrignham | emden | DC | Bipolar | 610 | 1260 | 23 | 3%
1708 | Converter stations and Subsea cables | 1051 | 1.4 GW HVDC electricity interconnector between UK and Germany Voltage Source Converter (VSC)/Bipolar Grid connection point (substations name): Norwich Main (UK) and near Revsing (Denmark), exact substation location subject to grid study in Denmark. Total cable length (substation to substation) 610km (35km in UK and 25km in Germany) Two cables (XLPE) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load. The annual Availability is 98.1% availability, with 1.8% planned outages, and 0.1% forced outages. The maximum single failure according to the design is 1.4GW. The project will enable the reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. There are no material anticipated environmental impacts during construction and operation. | 2028 | 1 |  | New Investment | TRUE | OffshoreDCTransmissionCable | Norwich Main | Revsing | DC | Bipolar | 640 | 1151 | 28 | 6 |  |  |  | 0
1713 | Lienz (AT) - Obersielach (AT) | 1052 | upgrade from 220 kV to 380 kV | 2030 | 2 | Tests and gaining of experience for novel technical solution in progress. | Rescheduled | TRUE | ACTransmissionLine | Lienz (AT) | Obersielach (AT) | AC | None | 170 | 175 | 1.4 | 10 |  |  |  | 4 | 81 | None
1715 | Westtirol (AT) - Zell/Ziller (AT) | 1054 | Upgrade of the existing 220kV-line Westtirol - Zell-Ziller and erection of an additional 220/380kV-Transformer. Line length 105km. | 2027 | 2 | Tests and gaining of experience for novel technical solution in progress. | Rescheduled | TRUE | ACTransmissionLine | Westtirol (AT) | Zell-Ziller (AT) | AC | None | 105 | 45 | 1 | 10 |  |  |  | 11 | 74 | None
1716 | Interconnection between Crete and Peloponnese (Phase I) | 1055 | New 150 kV AC double circuit submarine and underground cables between Crete and Peloponnese | 2020 | 4 |  | New Investment | FALSE | ACTransmissionLine | Chania I | Molai (through Sklavouna Terminal) | AC | None | 179 | 356.42 | 1.2 | 9 |  |  |  | 25 11 2 | 9.63 | HabitatsDirective
1717 | Interconnection between Crete and Attica (Phase II) | 1055 | New symmetric bipolar submarine HVDC-VSC link between Crete and Attica | 2022 | 3 |  | New Investment | TRUE | DCTransmissionLine | Damasta | Koumoundouros | DC | Bipolar | 373 | 1020 | 1.5 | 9 |  |  |  | 5.2 4.48 | 14.9 | HabitatsDirective
1718 | SS 400 kV ZONE 5 | 1056 | New 400 kV substation interpolated in existing 400 kV line Konjsko - Mostar | 2035 | 1 |  | New Investment | TRUE | OnshoreSubstation |  |  | AC | None | 0 | 8 | 0.0112 | 10
1719 | SS 400/220 kV ZONE 6 | 1056 | New 400 kV substation for connetion of new generation and increase of security of supply in the southern area near city of Ploce | 2035 | 1 |  | New Investment | FALSE | OnshoreSubstation |  |  | AC | None | 0 | 17.5 | 0.0245 | 10
1723 | OHL 2x400 kV ZONE 5 - ZONE 6 | 1056 | Double 400 kV line connecting SS ZONE 5 and ZONE 6 | 2035 | 1 |  | New Investment | FALSE | ACTransmissionLine | ZONE 5 | ZONE 6 | AC | None | 90 | 45 | 0.063
1724 | OHL 2x220 kV ZONE 6 – Plat | 1056 | Double 220 kV line connecting SS ZONE 6 and SS Plat | 2035 | 1 |  | New Investment | FALSE | ACTransmissionLine | ZONE 6 | Plat | AC | None | 105 | 36.75 | 0.05145 | 10
1725 | SS 220/110 kV Plat | 1056 | Construction of two addiotional OHL bays for connection of OHL 220 kV ZONE 6 - Plat | 2035 | 1 |  | New Investment | FALSE | OnshoreSubstation | ZONE 6 | Plat | AC | None | 0 | 2 | 0.0028 | 10
1722 | HVDC Line C3 | 1057 | New HVDC line to integrate the additional wind power capacity in the northern Germany in order to supply it to the load centers and storage units in the southern parts of the country. | 2035 | 1 |  | New Investment | TRUE | DCTransmissionLine | Schleswig Holstein area | Baden-Württemberg area | DC | Bipolar | 700 | 5600 | 44.8 | ±20%
1726 | HVDC Line DE-CH | 1058 | The concept of extending German HVDC-Lines towards Switzerland and Italy offers a further potential to realize a new N-S HVDC corridor. Large developments of variable wind and photovoltaic power, coal and nuclear phaseout, mainly gas-based thermal generation, and the pump storage potentials in the Alps are the main drivers of power system evolution that will challenge the future transmission system in central southern Europe. | 2040 | 1 |  | New Investment | TRUE | DCTransmissionLine | Wendlingen (DE) | Mettlen (CH) | DC | None | 0 | 2500 | 20 | ±20%
645 | ITA-3 | 1059 | New 400kV OHL between the existing substations of Laino and Altomonte in Calabria (investment previously included in P127). | 2027 | 3 |  | Rescheduled | FALSE | ACTransmissionLine | Laino (IT) | Altomonte (IT) | AC | None | 50 | 186 | 2.41 | +/- 10%
1727 | Montecorvino-Avellino and Nord-Ben. in Campania | 1059 | New 400 kV between Montecorvino-Avellino and Nord-Ben. in Campania | 2030 | 3 |  | New Investment | TRUE | ACTransmissionLine | Montecorvino (IT) | Benevento (IT) | AC | None | 0 | 212 | 1.97 | +/- 10%
1729 | Reactive compensation | 1061 | Reactive compensation in substations to increase the transfer capacity from North to South Finland: installation of STATCOM(s), SVC(s) and/or shunt compensation. | 2022 | 1 |  |  | TRUE | ReactiveCompensationDevice | North Finland | South Finland | AC | None | 0 | 20 | 0.1 | +/- 100%
1730 | Reactive compensation | 1062 | Reactive compensation measures in substations to increase the transfer capacity from North to South Finland: installation of STATCOM(s), SVC(s) and/or shunt compensation. | 2029 | 1 |  |  | TRUE | ReactiveCompensationDevice | North Finland | South Finland | AC | None | 0 | 30 | 0.1 | +/- 100%
1731 | ZuidWest380 West | 1063 | New 380 kV substation Rilland; New 380 kV double circuit line 2645MVA between Borssele and Rilland; Upgrade of existing 380 kV line Borssele-Geertruidenberg to 1975MVA. | 2022 | 4 |  |  | TRUE | ACTransmissionLine | Borssele | Rilland | AC | None | 40 | 564 | 2.8 | 10 | [7 empty] | More info: https://www.rvo.nl/onderwerpen/bureau-energieprojecten/lopende-projecten/hoogspanning/zuid-west-380-kv-west
1736 | 400kV OHL, Maritsa East 2 (BG) – Vize Havza (TR) | 1066 | New interconnection line BG-TR by a 150km single circuit 400kV OHL. | 2036 | 1 |  | New Investment | TRUE | ACTransmissionLine | Maritsa East 2 (BG) | Vize Havza (TR) | AC | None | 150 | 60 | 1.2 | +-10%
1738 | New AC 400 kV interconnection line Greece - Turkey | 1067 | New AC 400 kV Overhead line Greece - Turkey | 2036 | 1 |  | New Investment | TRUE | ACTransmissionLine | Nea Santa (GR) | Babaeski (TR) | AC | None | 130 | 32.55 | 0.64 | ± 10%
1740 | LaSGo Link - Gotland to Latvia | 1068 | New monopolar HVDC VSC monopole sub-sea cable running from a new substation in Gotland (TBC) to Grobina in Latvia (or Ventspils or a possible a new substation inbetween Grobina and Ventspils) (TBC). This investment consists of two VSC HVDC converter stations connected via two 320kV HVDC XLPE cables. | 2036 | 1 |  | New Investment | TRUE | OffshoreDCTransmissionCable | New substation on Gotland (TBC) | Grobina (TBC) | DC | Monopolar | 195 | 511.5 | 8 | +/-15%
1741 | LaSGo Link - Sweden to Gotland | 1068 | New monopolar HVDC VSC monopole sub-sea cable running from the vicinity of Oskarshamn in mainland Sweden (TBC) to a new substation in Gotland (TBC). This investment consists of one HVDC VSC converter station connected via two 320kV HVDC XLPE cables to a Converter Station being built as part of the LaSGo Link Gotland to Latvia investment. | 2036 | 1 |  | New Investment | FALSE | OffshoreDCTransmissionCable | Oskarshamn (TBC) | New substation on Gotland (TBC) | DC | Monopolar | 125 | 287.5 | 4 | +/-15%
1742 | 400 kV OHL SS Subotica 3 – SS Sándorfalva | 1074 | New 400 kV interconnection OHL between SS Subotica (RS) and SS Sándorfalva (HU). This is the main investment of the project and a part of the new North-South corridor for energy transmission. | 2036 | 1 | No delay on this investment yet. | New Investment | TRUE | ACTransmissionLine | SS Subotica 3 | SS Sándorfalva | AC | None | 50.6 | 24.1 | 0.4 | 10
1743 | 400 kV OHL SS Sombor 3 – SS Srbobran | 1074 | New 400 kV OHL from existing substation Sombor 3 to existing substation Srbobran (both in Serbia). | 2036 | 1 | No delay on this investment yet. | New Investment | FALSE | ACTransmissionLine | SS Sombor 3 | SS Srbobran | AC | None | 80 | 19.5 | 0.26 | 5
1744 | 400 kV OHL SS Srbobran – SS Sremska Mitrovica 2 | 1074 | New 400 kV OHL from existing substation Srbobran to existing substation Sremska Mitrovica 2 (both in Serbia). | 2036 | 1 | No delay on this investment yet. | New Investment | FALSE | ACTransmissionLine | SS Srbobran | SS Sremska Mitrovica 2 | AC | None | 90 | 21.2 | 0.272 | 5
1746 | Crete-Northern Greece | 1077 | The project will have a DC voltage of +/-525 kV. It will transmit 2000MW through bipolar HVDC cables. Converter technology is VSC. It will connect to LEG1 converter station of Linoperamata (Crete). | 2036 | 1 |  |  | TRUE | OffshoreDCTransmissionCable | Linoperamata | Thessaloniki | DC | Bipolar | 600 | 1900 | 30 | 20
1747 | Northern Greece-North Macedonia | 1077 | The project will have a DC voltage of +/-525 kV. It will transmit 2000MW through bipolar HVDC cables. Converter technology is VSC. | 2036 | 1 |  |  | FALSE | DCTransmissionLine | Thessaloniki | Dubrovo | DC | Bipolar | 110 | 800 | 30 | 20
1748 | North Macedonia-Bulgaria | 1077 | The project will have a DC voltage of +/-525 kV. It will transmit 2000MW through bipolar HVDC cables. Converter technology is VSC. | 2036 | 1 |  |  | FALSE | DCTransmissionLine | Dubrovo | Ch. Mogila | DC | Bipolar | 170 | 1100 | 30 | 20
1745 | Libya Greece | 1081 | The HVDC interconnector will link Libya to Greece with XLPE or MI submarine cables, and use VSC converters. | 2036 | 1 |  | New Investment | TRUE | OffshoreDCTransmissionCable | Tobruk | Arachtos | DC | Bipolar | 1070 | 3400 | 30 | 20
1749 | Greece Albania | 1081 | The HVDC interconnector will link Greece to Albania with XLPE underground cables or OHL, and use VSC converters. | 2036 | 1 |  | New Investment | FALSE | DCTransmissionLine | Arachtos | Elbasan | DC | Bipolar | 180 | 1100 | 30 | 20
1750 | Sea-Socket | 1082 | Floating substation platform facilitating 700-MW multiple offshore wind connections and transmitted via 220kV subsea AC cables to onshore substation(s) located along the Shannon Estuary | 2035 | 1 |  | New Investment | TRUE | OffshoreSubstation | New substation connection to 400kV/220kV lines in the Shannon Estuary | Not applicable - offshore connection point at Sea-Socket Platform | AC | None | 40 | 375 | 12 | 25%

## Stor.Projects
TYNDP 2020 - General description of storage projects | [15 empty] | Needs addressed by the project |  | Projects costs |  |  | Technical characteristics of the project | [5 empty] | Residual impact of the project
Project ID | Project Name | Promoters | Country | National development plan(s) | Storage technology | Project description | Commissioning Year | Status ID 1 : Under Consideration 2 : In Planning but not permitting 3 : In permitting 4 : Under Construction | Progress of the project since TYNDP2018 | Explanation in case of delay or reclustering | Comments on CBA results by the project promoter (to be provided after results are shared) | Type of project - Is it an upgrade of existing infrastructure? | Is the project on the 4th PCI list? | PCI number | Is the project in the reference grid? | Needs addressed by the project | Explanation by the promoter on how the project addresses the system needs | Estimated CAPEX (MEUR) | Estimated OPEX (MEUR) | Cost Uncertainty Range | Total Storage Capacity (MW) | Total turbining capacity (MW) | Storage Capacity (GWh) | Voltage at connection point (kV) | Roundtrip efficiency (%) | Operational lifetime (Years) | Residual Environmental Impact | Residual Social Impact | Other Residual Impact

## 2025NT
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | kg / year | kg / year | kg / year | kg / year | kg / year | kg / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 24 | 25 | 23 | 4 | 5 | 2 | 19 | 21 | 17 | -153 | -87 | -203 | 18 | 6 | 12 | 25 | -1 | -2 | -3 | 402 | 437 | 353 | 1154 | 409 | 21 | 687 | 1284 | 39 | 1272 | 35 | 2
4 | Interconnection Portugal-Spain | TOOT | 18 | 25 | 15 | 3 | 4 | 3 | 6 | 7 | 5 | -128 | -110 | -178 | 24 | 5 | 10 | 21 | -1 | -2 | -5 | 130 | 159 | 109 |  | 40 | 9 | 77 | 3408 | 19 | 3404 | 37 | 2
16 | Biscay Gulf | TOOT | 124 | 145 | 104 | 12 | 22 | 5 | 26 | 30 | 21 | -523 | -199 | -947 | 516 | 19 | 40 | 87 | -24 | -49 | -106 | 541 | 651 | 424 |  | -1187 | -181 | -319 | 14611 | -80 | 14621 | 1298 | 57
23 | FR-BE: Avelin/Mastaing-Avelgem-Horta HTLS | TOOT
26 | Reschenpass Interconnector Project | TOOT | 10 | 14 | 7 | -5 | -2 | -12 | 1 | 2 | 0 | 227 | 507 | 96 | 120 | -8 | -17 | -38 | -4 | -9 | -21 | 17 | 43 | 0 |  | 444 | -7 | 727 | 811 | 27 | 781 | 241 | 11
28 | Italy-Montenegro | PINT | 14 | 19 | 10 | -7 | 3 | -17 | 1 | 2 | 0 | 300 | 760 | -142 | 155 | -11 | -23 | -50 | -6 | -12 | -26 | 14 | 33 | 2 |  | 1177 | -22 | 1466 | 143 | 77 | 22 | 261 | 12
29 | Italy-Tunisia | PINT | 18 | 26 | 12 | -18 | -13 | -26 | 1 | 1 | 0 | 791 | 1123 | 550 | 97 | -29 | -61 | -131 | -3 | -6 | -14 | 14 | 21 | 1 |  | -218 | -31 | 13 | -22 | -19 | -11 | 162 | 8
33 | Central Northern Italy | TOOT | 1 | 1 | 0 | 0 | 0 | -1 | 0 | 1 | 0 | 10 | 36 | -9 | -2 | 0 | -1 | -2 | 0 | 0 | 0 | 9 | 27 | 1 |  | 18 | 0 | 37 | -74 | 2 | -76 | -3 | 0
35 | CZ Southwest-east corridor | PINT | 10 | 13 | 8 | 10 | 13 | 5 | 6 | 7 | 6 | -416 | -234 | -568 | 24 | 15 | 32 | 69 | -1 | -2 | -4 | 129 | 159 | 111 |  | -1171 | 0 | -1234 | 1802 | -60 | 1903 | 77 | 1
36 | Kriegers Flak CGS
37 | Norway - Germany, NordLink | TOOT
39 | DKW-DE, step 3
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 2 | 2 | 2 | 1 | 1 | 0 | 5 | 5 | 5 | -28 | -22 | -34 | 0 | 1 | 2 | 5 | 0 | 0 | 0 | 94 | 96 | 92 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 11 | 15 | 7 | 4 | 6 | 2 | 6 | 7 | 5 | -179 | -104 | -272 | 71 | 7 | 14 | 30 | -2 | -5 | -12 | 128 | 161 | 110 |  | -237 | 4 | -310 | 886 | -7 | 905 | 141 | 5
48 | New SK-HU intercon. - phase 1 | TOOT | 6 | 7 | 4 | -6 | -2 | -12 | 1 | 2 | 0 | 280 | 502 | 97 | 87 | -10 | -22 | -46 | -3 | -7 | -15 | 16 | 41 | 0 |  | 256 | -15 | 528 | 510 | 3 | 498 | 123 | 5
62 | Estonia-Latvia 3rd IC | TOOT | 6 | 8 | 4 | 1 | 2 | 0 | 1 | 1 | 0 | -38 | -13 | -87 | 8 | 1 | 3 | 6 | -1 | 0 | -1 | 12 | 25 | 0 |  | -426 | -2 | -351 | 259 | 35 | 269 | 19 | 1
78 | South West Cluster | TOOT | [12 empty] | -73 |  |  |  | 3 | 5 | 12 |  |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | -129 | -5
81 | North South Interconnector | TOOT | 14 | 22 | 11 | 1 | 2 | 1 | 3 | 4 | 3 | -53 | -22 | -83 | -1 | 2 | 4 | 9 | 0 | 0 | 0 | 72 | 93 | 59 |  | -95 | -10 | -2 | 261 | -5 | 266 | 6 | 0
82 | RIDP I | PINT | 26 | 29 | 23 | 5 | 5 | 5 | 26 | 27 | 24 | -227 | -218 | -235 | -46 | 8 | 18 | 38 | 2 | 4 | 8 | 536 | 543 | 527 | 300 | 300 | 18 | 449 | -244 | 38 | -260 | -167 | -4
85 | Integration of RES in Alentejo | TOOT | 22 | 25 | 20 | 4 | 4 | 4 | 23 | 24 | 22 | -167 | -155 | -176 | 12 | 6 | 13 | 28 | 0 | -1 | -2 | 469 | 471 | 466 | 258 | 365 | 18 | 608 | -302 | 35 | -313 | 17 | 1
92 | ALEGrO
94 | GerPol Improvements
103 | Reinforcements Ring NL phase I | TOOT | 1 | 2 | 1 | 0 | 0 | -3 | 0 | 1 | 0 | 20 | 142 | -17 | 4 | -1 | -2 | -3 | 0 | 0 | -1 | 7 | 13 | 0 |  | -26 | -1 | -61 | -28 | 1 | -30 | 9 | 0
107 | Celtic Interconnector | PINT | 51 | 53 | 49 | 10 | 11 | 9 | 19 | 23 | 16 | -435 | -371 | -472 | 349 | 16 | 34 | 72 | -5 | -27 | -58 | 389 | 477 | 311 |  | -1082 | -44 | -1415 | 1806 | -34 | 1830 | 678 | 30
110 | Norway-Great Britain, North Sea Link | TOOT
111 | 3rd AC Finland-Sweden north | TOOT | 17 | 20 | 14 | 4 | 4 | 4 | 1 | 1 | 0 | -165 | -162 | -169 | -95 | 6 | 13 | 27 | 5 | 7 | 16 | 12 | 24 | 0 |  | 1338574 | 59394 | 1590079 | 3923977 | 89806 | 3859101 | 150 | 7
120 | MOG II: connection of up to 2 GW additional offshore wind Belgium | TOOT | 327 | 329 | 323 | 68 | 69 | 66 | 378 | 380 | 375 | -2949 | -2889 | -2987 | -181 | 109 | 227 | 490 | 8 | 14 | 30 | 7540 | 7550 | 7529 | 2000 | 2725 | 201 | 5141 | -6959 | 426 | -7046 | -357 | -15
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 11 | 12 | 9 | 3 | 3 | 2 | 1 | 1 | 0 | -114 | -99 | -134 | -66 | 4 | 9 | 19 | 6 | 5 | 11 | 14 | 22 | 7 |  | -374 | -22 | -451 | 1234 | -18 | 1242 | -13 | -1
123 | LitPol Link Stage 2 | TOOT | 28 | 38 | 19 | 17 | 20 | 10 | 1 | 4 | 0 | -719 | -426 | -867 | 10 | 27 | 55 | 119 | -2 | -4 | -9 | 31 | 87 | 8 |  | -1623 | 27 | -3200 | 4683 | -28 | 4737 | 73 | 4
124 | NordBalt phase 2 | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 4 | 4 | 4 | 1 | 1 | 0 | 0 | 1 | 0 | -24 | -19 | -30 | -45 | 1 | 2 | 4 | 2 | 3 | 8 | 7 | 13 | 0 |  | -238 | -24 | -565 | -79 | -68 | -67 | 58 | 2
127 | Central Southern Italy | TOOT | 1 | 3 | 0 | 0 | 1 | -2 | 0 | 1 | 0 | 9 | 71 | -43 | -76 | 0 | -1 | -1 | 3 | 6 | 13 | 10 | 25 | 3 |  | 59 | 0 | 106 | 4 | 2 | 3 | -125 | -7
130 | HVDC SuedOstLink Wolmirstedt to area Isar | PINT | 49 | 49 | 49 | -1 | -1 | -1 | 16 | 16 | 16 | 38 | 38 | 38 | -147 | -1 | -3 | -6 | 5 | 11 | 24 | 353 | 353 | 353 |  | 366416 | -28505 | 739333 | 26498 | 17655 | -9161 | -309 | -9
132 | HVDC Line A-North | TOOT | 54 | 54 | 54 | -4 | -4 | -4 | 17 | 17 | 17 | 152 | 152 | 152 | -203 | -6 | -12 | -25 | 8 | 16 | 34 | 374 | 374 | 374 |  | 771367 | -29276 | 1672888 | 15040 | 9948 | -6718 | -406 | -17
138 | Black Sea Corridor | TOOT | 5 | 8 | 3 | -3 | 0 | -6 | 1 | 3 | 0 | 119 | 249 | 12 | 3 | -4 | -9 | -20 | 0 | 0 | 0 | 20 | 63 | 0 |  | 440 | -11 | 656 | 41 | 19 | 7 | 4 | 0
142 | CSE4 | TOOT | 10 | 18 | 4 | -10 | -4 | -17 | 0 | 1 | 0 | 417 | 746 | 193 | 21 | -15 | -32 | -69 | -1 | -2 | -4 | 8 | 26 | 0 |  | 1629 | -19 | 2308 | 110 | 82 | -11 | 22 | 1
144 | Mid Continental East corridor | TOOT | 1 | 2 | 1 | -1 | 1 | -3 | 0 | 1 | 0 | 28 | 145 | -24 | -151 | -1 | -2 | -5 | 6 | 12 | 25 | 10 | 26 | 3 |  | -12 | -2 | 2 | 18 | -2 | 19 | -247 | -12
150 | Italy-Slovenia | PINT | 17 | 23 | 14 | -13 | -7 | -20 | 0 | 0 | 0 | 572 | 882 | 295 | 167 | -21 | -44 | -95 | -6 | -13 | -29 | 0 | 1 | -2 |  | 1671 | -32 | 2763 | -223 | 61 | -316 | 308 | 14
153 | France-Alderney-Britain | PINT | 29 | 32 | 27 | 9 | 11 | 7 | 1 | 2 | 1 | -371 | -317 | -458 | 151 | 14 | 29 | 62 | -6 | -12 | -25 | 30 | 41 | 19 |  | -1099 | -56 | -1325 | 6387 | -69 | 6431 | 359 | 16
167 | Viking DKW-GB
170 | Baltic States Synchronization with Continental Europe | PINT | 33 | 38 | 27 | 18 | 19 | 17 | 3 | 4 | 1 | -792 | -746 | -837 | -7 | 29 | 61 | 131 | 0 | 1 | 1 | 53 | 87 | 18 |  | 0 | 0 | 0 | 0 | 0 | 0 | -14 | -1
172 | ElecLink | TOOT | 29 | 30 | 28 | 9 | 10 | 7 | 2 | 2 | 1 | -395 | -317 | -438 | 169 | 15 | 30 | 66 | -3 | -13 | -28 | 32 | 43 | 20 |  | -951 | -46 | -1086 | 6697 | -55 | 6737 | 93 | 8
173 | FR-BE: PSTs Aubange-Moulaine
174 | Greenconnector | PINT | 24 | 27 | 17 | -6 | 1 | -9 | 1 | 4 | 0 | 258 | 408 | -58 | 359 | -10 | -20 | -43 | -13 | -28 | -60 | 22 | 84 | 0 |  | 866 | -58 | 1609 | 892 | 39 | 810 | 625 | 28
176 | Hansa PowerBridge I | PINT | 24 | 25 | 22 | 5 | 8 | 1 | 5 | 8 | 1 | -207 | -31 | -346 | 23 | 8 | 16 | 34 | -7 | -3 | -4 | 108 | 163 | 19 |  | -745 | -33 | -1073 | 731 | -23 | 738 | 64 | 5
179 | DKE - DE (Kontek2) | PINT | 3 | 4 | 2 | 1 | 2 | 1 | 0 | 0 | 0 | -45 | -23 | -72 | -32 | 2 | 3 | 7 | 4 | 2 | 5 | 3 | 7 | 0 |  | -131 | -10 | -203 | 410 | -5 | 407 | -59 | -2
183 | DKW-DE, Westcoast | TOOT | 3 | 4 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | -38 | -23 | -48 | 19 | 1 | 3 | 6 | -3 | -1 | -3 | 21 | 22 | 19 |  | 1260 | 63 | 3026 | 940 | 219 | 892 | 39 | 2
186 | East of Austria | TOOT | 144 | 148 | 139 | 20 | 21 | 19 | 93 | 102 | 86 | -869 | -825 | -934 | -77 | 32 | 67 | 144 | 0 | 6 | 13 | 1864 | 1872 | 1856 | 850 | 45169 | 5245 | 2159 | 3543 | 2344 | 1515 | -135 | -6
187 | St. Peter (AT) - Pleinting (DE) | PINT | 24 | 29 | 20 | 9 | 14 | 6 | 14 | 17 | 11 | -410 | -256 | -622 | 132 | 15 | 32 | 68 | -6 | -10 | -23 | 290 | 368 | 227 |  | -510 | 0 | -529 | 3037 | -14 | 3075 | 275 | 8
190 | NorthConnect | TOOT | 60 | 66 | 52 | 9 | 12 | 7 | 3 | 9 | 1 | -405 | -316 | -533 | -66 | 15 | 31 | 67 | 1 | 5 | 11 | 75 | 206 | 25 |  | -1348 | -48 | -229 | 5713 | 107 | 5745 | 149 | 12
197 | N-S Finland P1 stage 2 | TOOT | 3 | 3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 26 | 26 | 26 | 26 | -1 | -2 | -4 | -1 | -2 | -4 | 174 | 174 | 174 |  | -5766 | -536 | -2146 | -399 | -254 | -164 | -86 | -4
200 | CZ Northwest-South corridor | TOOT | 12 | 15 | 9 | 10 | 13 | 5 | 7 | 8 | 6 | -413 | -237 | -560 | 61 | 15 | 32 | 69 | -2 | -5 | -10 | 137 | 168 | 124 |  | -1205 | -2 | -1309 | 1908 | -63 | 2008 | 136 | 4
207 | Reinforcement Northwestern DE
208 | N-S Western DE_section North_1
210 | Wurmlach (AT) - Somplago (IT) interconnection | PINT | 5 | 8 | 2 | -2 | -1 | -3 | 1 | 2 | 0 | 69 | 134 | 37 | 20 | -3 | -5 | -11 | -1 | -2 | -3 | 11 | 40 | 1 |  | 4 | -15 | 88 | 139 | -5 | 133 | 46 | 2
219 | EuroAsia Interconnector | PINT | 126 | 166 | 92 | -6 | -3 | -8 | 0 | 1 | 0 | 243 | 355 | 131 | 513 | -9 | -19 | -40 | -18 | -37 | -81 | 5 | 12 | 1 |  | 1268 | -53 | 388 | 1335 | 115 | 1067 | 817 | 38
225 | 2nd interconnector Belgium - Germany | light PINT | 7 | 7 | 7 | 0 | 1 | 0 | 11 | 11 | 11 | -6 | 14 | -26 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 230 | 237 | 223 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
227 | Transbalkan Corridor | PINT | 2 | 10 | 0 | 0 | 2 | -4 | 0 | 1 | 0 | 9 | 157 | -105 | -21 | 0 | -1 | -2 | 1 | 2 | 3 | 4 | 17 | 0 |  | -5 | 0 | -22 | -7 | 1 | -8 | -29 | -1
228 | Muhlbach - Eichstetten | PINT | 8 | 10 | 7 | 2 | 4 | 0 | 3 | 4 | 3 | -85 | -17 | -160 | 51 | 3 | 7 | 14 | -2 | -4 | -9 | 72 | 87 | 56 |  | -278 | -9 | -328 | 689 | -14 | 702 | 110 | 4
229 | GerPol Power Bridge II | light PINT | 43 | 43 | 43 | 35 | 35 | 35 | 16 | 16 | 16 | -1540 | -1540 | -1540 | 0 | 57 | 119 | 256 | 0 | 0 | 0 | 308 | 308 | 308 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
230 | GerPol Power Bridge I | TOOT | 90 | 107 | 71 | 79 | 86 | 71 | 21 | 29 | 19 | -3416 | -3071 | -3749 | 578 | 126 | 263 | 567 | -21 | -45 | -96 | 441 | 613 | 370 |  | -8679 | 30 | -14941 | 5291 | -203 | 5557 | 1032 | 53
231 | Beznau - Tiengen | PINT | 16 | 26 | 10 | 2 | 5 | 1 | 9 | 11 | 7 | -101 | -45 | -208 | 126 | 4 | 8 | 17 | -5 | -10 | -21 | 177 | 214 | 141 |  | -136 | 1 | -39 | 1439 | 2 | 1452 | 273 | 8
233 | Connection of Aragon Pumping hydro | PINT | 33 | 39 | 28 | 5 | 6 | 4 | 18 | 23 | 15 | -226 | -190 | -271 | 0 | 8 | 17 | 37 | 0 | 0 | 0 | 365 | 474 | 301 |  | -2036 | -142.5 | -2288.5 | 5491 | -156 | 5561 | 308 | 12.5
234 | DKE - PL-1 | PINT | 18 | 24 | 15 | 19 | 23 | 13 | 4 | 5 | 3 | -827 | -582 | -1001 | 208 | 31 | 64 | 137 | -10 | -12 | -34 | 82 | 105 | 58 |  | -2141 | 28 | -3518 | 3175 | -38 | 3261 | 326 | 12
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Grafenrheinfeld | PINT | 130 | 130 | 130 | -1 | -1 | -1 | 46 | 46 | 46 | 22 | 22 | 22 | -480 | -1 | -2 | -4 | 18 | 37 | 80 | 1056 | 1056 | 1056 |  | 870337 | -72197 | 2174508 | 26190 | 17940 | -20456 | -1087 | -41
239 | Fenno-Skan 1 renewal | light PINT | 12 | 12 | 12 | 5 | 5 | 5 | 0 | 0 | 0 | -203 | -203 | -203 | 0 | 8 | 16 | 34 | 0 | 0 | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines | PINT | 8 | 13 | 6 | -3 | 3 | -6 | 1 | 1 | 0 | 124 | 271 | -118 | 47 | -5 | -10 | -21 | -2 | -4 | -8 | 11 | 30 | 0 |  | 400 | -13 | 351 | 63 | 38 | -4 | 81 | 4
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 9 | 9 | 9 | -4 | -4 | -4 | 0 | 0 | 0 | 183 | 183 | 183 | 0 | -7 | -14 | -30 | 0 | 0 | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
244 | Vigy - Uchtelfangen area | PINT | 36 | 43 | 32 | 11 | 15 | 8 | 17 | 20 | 16 | -469 | -337 | -654 | 271 | 17 | 36 | 78 | -10 | -21 | -45 | 361 | 432 | 313 |  | -1583 | -48 | -2132 | 2547 | -82 | 2616 | 555 | 19
245 | Upgrade Meeden - Diele
247 | AQUIND Interconnector | PINT | 40 | 45 | 37 | 11 | 15 | 7 | 2 | 2 | 1 | -463 | -298 | -639 | 161 | 17 | 36 | 77 | -7 | -12 | -27 | 36 | 54 | 13 |  | -1349 | -72 | -1656 | 8710 | -82 | 8758 | 266 | 13
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 5 | 8 | 4 | -1 | 0 | -2 | 0 | 1 | 0 | 51 | 87 | -18 | 77 | -2 | -4 | -8 | -3 | -3 | -13 | 3 | 13 | -2 |  | 220119 | 21512 | 328368 | -920528 | 28949 | -925171 | 819 | 6
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | light PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -997 | -116 | -27 | -80 | -51 | -35 | 0 | 0
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT - A2 | 13 | 16 | 11 | 8 | 15 | 4 | 0 | 0 | 0 | -343 | -188 | -655 | 91 | 13 | 26 | 57 | -3 | -7 | -15 | 1 | 5 | -1 |  | -1712 | -35 | -1991 | 11125 | -83 | 11230 | 165 | 6
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 57 | 57 | 57 | -9 | -9 | -9 | 4 | 4 | 4 | 302 | 302 | 302 | 18 | -11 | -23 | -50 | -1 | -1 | -3 | 93 | 93 | 93 |  | 1066512 | -39434 | 1694067 | 79562 | 53264 | -13266 | 19 | 1
258 | Westcoast line | No assessment
259 | HU-RO | PINT | 8 | 11 | 6 | -3 | 2 | -6 | 0 | 1 | 0 | 115 | 281 | -101 | 82 | -4 | -9 | -19 | -3 | -6 | -14 | 7 | 19 | 0 |  | 676 | -13 | 497 | 146 | 48 | 56 | 159 | 8
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 24 | 25 | 22 | 4 | 5 | 3 | 19 | 20 | 17 | -184 | -115 | -229 | 210 | 7 | 14 | 31 | -12 | -16 | -35 | 393 | 438 | 337 |  | -684 | -33 | -885 | -1925 | -33 | -1907 | 530 | 22
262 | Belgium-Netherlands: Zandvliet-Rilland | TOOT | 9 | 10 | 8 | 2 | 2 | 1 | 13 | 14 | 12 | -74 | -61 | -96 | 9 | 3 | 6 | 12 | -1 | -3 | -6 | 265 | 297 | 237 |  | -345 | -6 | -541 | -2273 | -14 | -2261 | 108 | 3
263 | Lake Constance East | light PINT | 21 | 22 | 20 | 7 | 9 | 5 | 13 | 14 | 12 | -298 | -221 | -375 | 0 | 11 | 23 | 49 | 0 | 0 | 0 | 263 | 273 | 254 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
264 | Swiss Roof I | light PINT | 33 | 34 | 33 | 3 | 6 | 0 | 17 | 17 | 16 | -130 | -1 | -260 | 0 | 5 | 10 | 22 | 0 | 0 | 0 | 332 | 345 | 320 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
265 | Tessin | light PINT
266 | Swiss Ellipse I | PINT | 20 | 25 | 16 | 5 | 8 | 1 | 10 | 12 | 9 | -199 | -34 | -343 | 7 | 7 | 15 | 33 | 0 | -1 | -1 | 208 | 254 | 172 |  | 263 | 2 | 222 | -1700 | 7 | -1720 | 28 | -2
267 | Hansa PowerBridge II | light PINT | 25 | 25 | 25 | 6 | 6 | 6 | 8 | 8 | 8 | -244 | -244 | -244 | 0 | 9 | 19 | 40 | 0 | 0 | 0 | 163 | 163 | 163 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 57 | 69 | 45 | 4 | 11 | 0 | 12 | 21 | 9 | -180 | 0 | -470 | 626 | 7 | 14 | 30 | -23 | -48 | -104 | 245 | 422 | 180 |  | -762 | -93 | -583 | 5906 | -51 | 5910 | 1201 | 51
276 | FR-ES project -Navarra-Landes | PINT | 57 | 69 | 45 | 4 | 11 | 0 | 12 | 21 | 9 | -180 | 0 | -470 | 626 | 7 | 14 | 30 | -23 | -48 | -104 | 245 | 422 | 180 |  | -762 | -93 | -583 | 5906 | -51 | 5910 | 1201 | 51
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 18 | 22 | 15 | 6 | 9 | 4 | 0 | 1 | 0 | -258 | -158 | -375 | 152 | 10 | 20 | 43 | -6 | -12 | -25 | 6 | 10 | 2 |  | -712 | -29 | -835 | 4146 | -40 | 4178 | 265 | 11
283 | TuNur | PINT | 576 | 585 | 570 | 112 | 115 | 109 | 577 | 628 | 531 | -4861 | -4759 | -4997 | 112 | 180 | 374 | 807 | -4 | -9 | -19 | 11432 | 11490 | 11324 | 4000 | -239018 | -18496 | -172262 | -136026 | -12783 | -126702 | 713 | 12
284 | LEG1 | PINT | 110 | 129 | 91 | -61 | -43 | -78 | 0 | 0 | 0 | 2639 | 3396 | 1883 | 579 | -98 | -203 | -438 | -19 | -39 | -84 | 0 | 0 | 0 | 2000 | 4550 | -152 | 8905 | 1544 | 316 | 1212 | 1075 | 48
285 | GridLink | PINT | 29 | 32 | 27 | 9 | 11 | 7 | 1 | 2 | 1 | -371 | -317 | -458 | 213 | 14 | 29 | 62 | -11 | -16 | -35 | 30 | 41 | 19 |  | -1099 | -56 | -1325 | 6387 | -69 | 6431 | 355 | 18
286 | Greenlink | PINT | 30 | 33 | 28 | 5 | 6 | 4 | 14 | 17 | 12 | -223 | -166 | -281 | 62 | 8 | 17 | 37 | -2 | -4 | -8 | 291 | 363 | 236 |  | -565 | -18 | -804 | -782 | -10 | -774 | 114 | 4
293 | Southern Aegean Interconnector | PINT | 45 | 47 | 43 | 11 | 14 | 9 | 48 | 50 | 46 | -482 | -404 | -597 | 13 | 18 | 37 | 80 | 0 | -1 | -2 | 993 | 1003 | 990 | 582 | -252 | 19 | 36 | 22 | 12 | 63 | 23 | 1
296 | Britib | PINT | 92 | 94 | 89 | 14 | 16 | 13 | 13 | 14 | 12 | -612 | -564 | -690 | 10 | 23 | 47 | 102 | 0 | -1 | -12 | 271 | 310 | 236 |  | -2183 | -165 | -2248 | 13144 | -139 | 13208 | 253 | -1
297 | BRABO II + III | PINT | 6 | 7 | 5 | 0 | 0 | 0 | 11 | 12 | 9 | -15 | -15 | -17 | 34 | 1 | 1 | 3 | -1 | -3 | -6 | 228 | 264 | 187 |  | -30 | -3 | -60 | -2053 | 0 | -2056 | 99 | 2
299 | SACOI3 | TOOT | 25 | 32 | 21 | 3 | 6 | 2 | 0 | 1 | 0 | -141 | -65 | -266 | 37 | 5 | 11 | 23 | -1 | -3 | -6 | 10 | 16 | 5 |  | -167 | -27 | -11 | -38 | -20 | -31 | 88 | 3
309 | NeuConnect | TOOT | 29 | 35 | 26 | 7 | 9 | 5 | 18 | 19 | 17 | -312 | -225 | -411 | 390 | 12 | 24 | 52 | -14 | -30 | -65 | 362 | 404 | 305 |  | -1005 | -33 | -1416 | -1854 | -44 | -1825 | 713 | 33
312 | St. Peter (AT) - Tauern (AT) | TOOT | 162 | 171 | 157 | 18 | 28 | 9 | 41 | 43 | 37 | -764 | -387 | -1186 | -205 | 28 | 59 | 127 | 4 | 10 | 21 | 834 | 928 | 763 |  | 59927 | 7058 | 1680 | 11591 | 3040 | 8958 | -325 | 1
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 47 | 56 | 42 | 16 | 26 | 7 | 26 | 28 | 21 | -697 | -321 | -1120 | -88 | 26 | 54 | 116 | 3 | 7 | 15 | 520 | 615 | 448 |  | -636 | 0 | 41 | 6731 | -38 | 6838 | -131 | 8
320 | Slovenia-Hungary/Croatia interconnection | TOOT | 0 | 1 | 0 | 0 | 0 | -1 | 0 | 1 | 0 | 10 | 40 | -11 | 2 | 0 | -1 | -2 | 0 | 0 | 0 | 9 | 28 | 0 |  | 43 | -6 | 167 | -57 | -6 | -53 | 3 | 0
322 | Wullenstetten - Border Area (DE-AT) | PINT | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 14 | -12 | -1 | -1 | -2 | 0 | 1 | 2 | -11 | -11 | -11 |  | -45481 | 909 | -86186 | -1144 | -790 | 160 | -21 | -1
323 | Dekani (SI) - Zaule (IT) interconnection | PINT | 2 | 3 | 1 | -2 | -1 | -3 | 0 | 1 | 0 | 70 | 120 | 32 | 37 | -3 | -5 | -12 | -1 | -3 | -6 | 6 | 29 | 0 |  | 57 | -6 | 146 | -6 | 0 | -9 | 56 | 3
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | PINT | 2 | 3 | 1 | -1 | 1 | -3 | 0 | 1 | 0 | 37 | 121 | -24 | 46 | -1 | -3 | -6 | -2 | -4 | -8 | 3 | 13 | 0 |  | 95 | -2 | 175 | -1 | 4 | -6 | 69 | 4
325 | Obersielach (AT) - Podlog (SI) | PINT | 5 | 14 | 2 | 2 | 5 | -1 | 1 | 4 | 0 | -83 | 23 | -227 | 55 | 3 | 6 | 14 | -2 | -4 | -9 | 26 | 91 | 3 |  | -451 | -18 | -578 | 235 | -31 | 256 | 98 | 5
328 | Interconnector DE-LUX | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2 | 3 | -8 | -15 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 0 | 0 |  | -9 | 0 | -21 | -7 | 0 | -7 | -28 | -1
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 327 | 327 | 327 | 68 | 68 | 68 | 378 | 378 | 378 | -3 | -3 | -3 | -11 | 0 | 0 | 0 | 0 | 1 | 2 | 7540 | 7540 | 7540 |  | 2725 | 201 | 5141 | -6959 | 426 | -7046 | -20 | -1
330 | 4th 400kV CZ-SK interconnector | light PINT | 2 | 2 | 2 | -1 | -1 | -1 | 0 | 0 | 0 | 45 | 45 | 45 | 0 | -2 | -3 | -8 | 0 | 0 | 0 | 0 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
333 | PST Foretaille | PINT - A1 | 30 | 37 | 25 | 14 | 18 | 11 | 0 | 0 | 0 | -623 | -457 | -770 | 199 | 23 | 48 | 103 | -7 | -15 | -33 | 1 | 5 | 0 |  | -1209 | -24 | -1386 | 7901 | -58 | 7976 | 358 | 13
335 | Project 335 - North Sea Wind Power Hub | light PINT | 2166 | 2166 | 2166 | 493 | 493 | 493 | 2462 | 2462 | 2462 | -21440 | -21440 | -21440 | 0 | 793 | 1651 | 3559 | 0 | 0 | 0 | 48931 | 48931 | 48931 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
336 | Prati (IT) – Steinach (AT) | No assessment
338 | Adriatic HVDC link | PINT | 10 | 16 | 5 | -4 | -1 | -7 | 1 | 3 | 0 | 158 | 287 | 55 | 18 | -6 | -12 | -26 | -1 | -1 | -3 | 16 | 55 | 1 |  | 706 | -47 | 1762 | -74 | -18 | -81 | 74 | 2
339 | Italian HVDC tri-terminal link | PINT | 4 | 5 | 1 | 0 | 2 | -2 | 0 | 1 | 0 | 6 | 70 | -104 | 379 | 0 | 0 | -1 | -13 | -29 | -65 | 8 | 28 | 0 |  | -35 | -19 | 130 | -21 | -17 | -16 | 691 | 33
340 | Avelgem-Center: new corridor (Boucle du Hainaut) | TOOT | 218 | 218 | 218 | 45 | 45 | 45 | 252 | 252 | 252 | -2 | -2 | -2 | -46 | 0 | 0 | 0 | 1 | 4 | 8 | 5027 | 5027 | 5027 |  | 1817 | 134 | 3427 | -4639 | 284 | -4697 | -79 | -3
341 | North CSE Corridor | PINT | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | -4 | 3 | -17 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 13 | 0 |  | 6 | -1 | 9 | 0 | 0 | -1 | 0 | 0
342 | Central Balkan Corridor | PINT | 1 | 1 | 0 | 0 | 2 | -1 | 0 | 1 | 0 | -17 | 26 | -80 | -27 | 1 | 1 | 3 | 1 | 2 | 4 | 3 | 12 | 0 |  | 61 | -3 | 106 | -4 | 2 | -9 | -40 | -2
343 | CSE1 New | PINT | 11 | 15 | 6 | -5 | -1 | -7 | 1 | 2 | 0 | 216 | 305 | 46 | -1 | -8 | -17 | -36 | 0 | 0 | 0 | 13 | 48 | 0 |  | 357 | -24 | 215 | 47 | 27 | -21 | -13 | -1
344 | Reinforcements Ring NL phase II | PINT
346 | ZuidWest380 NL Oost | PINT | 6 | 7 | 5 | 0 | 0 | 0 | 11 | 12 | 9 | -15 | -15 | -17 | 18 | 1 | 1 | 3 | 0 | -1 | -3 | 228 | 264 | 187 |  | -30 | -3 | -60 | -2053 | 0 | -2056 | 70 | 1
348 | NoordWest380 NL | PINT
349 | MaresConnect | PINT | 238 | 243 | 232 | 45 | 46 | 43 | 236 | 246 | 226 | -1939 | -1885 | -1993 | 164 | 72 | 149 | 322 | -7 | -14 | -31 | 4831 | 4922 | 4739 | 1800 | 1217 | 53 | 2812 | -2077 | 195 | -2123 | 328 | 16
350 | South Balkan Corridor
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 12 | 17 | 10 | -5 | -4 | -6 | 1 | 1 | 0 | 219 | 276 | 163 | 134 | -8 | -17 | -36 | -5 | -10 | -23 | 12 | 18 | 3 |  | 548 | -27 | 968 | -110 | 18 | -150 | 279 | 13
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 6 | 7 | 5 | 0 | 0 | 0 | 11 | 12 | 9 | -15 | -15 | -17 | 40 | 1 | 1 | 3 | -1 | -3 | -7 | 228 | 264 | 187 |  | -30 | -3 | -60 | -2053 | 0 | -2056 | 112 | 3
378 | Transformer Gatica | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
379 | Uprate Gatica lines | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 55 | 55 | 55 | 11 | 11 | 11 | 31 | 31 | 31 | -407 | -407 | -407 | -295 | 15 | 31 | 68 | 11 | 23 | 49 | 707 | 707 | 707 |  | 926374 | 20028 | 1532767 | 11812 | 7598 | 9594 | -609 | -26
1039 | SE North-south long-term reinforcements | light PINT | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | -19 | -19 | -19 | 0 | 1 | 1 | 3 | 0 | 0 | 0 | 1 | 1 | 1 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1040 | LirIC | PINT | 38 | 42 | 35 | 7 | 8 | 4 | 18 | 22 | 15 | -284 | -175 | -358 | 236 | 11 | 22 | 47 | -7 | -15 | -33 | 373 | 468 | 302 |  | -712 | -22 | -1018 | -1021 | -12 | -1012 | 328 | 12
1041 | GREGY Interconnector | PINT | 79 | 85 | 73 | -189 | -177 | -202 | 0 | 1 | 0 | 8233 | 8769 | 7697 | 1412 | -305 | -634 | -1367 | -40 | -83 | -178 | 8 | 16 | 0 |  | 4553 | -200 | 4547 | 1611 | 362 | 930 | 3121 | 114
1042 | Offshore wind integration | PINT | 99 | 107 | 91 | 23 | 25 | 22 | 110 | 112 | 109 | -986 | -935 | -1083 | -38 | 36 | 76 | 164 | 2 | 2 | 6 | 2217 | 2222 | 2207 | 700 | 805 | 45 | 1555 | -840 | 100 | -860 | -36 | -2
1043 | Wahle-Mecklar
1046 | N-S Finland P1 stage 3 | PINT | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 36 | 36 | 36 | -36 | -1 | -3 | -6 | 1 | 3 | 6 | 10 | 10 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | -75 | -3
1047 | Emden-Eemshaven | light PINT | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -9 | -8 | -9 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 3 | 3 | 2 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | light PINT | 73 | 73 | 73 | -203 | -203 | -203 | 1 | 1 | 1 | 8821 | 8821 | 8821 | 0 | -326 | -679 | -1464 | 0 | 0 | 0 | 17 | 17 | 17 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1049 | Cronos Energy Ltd | PINT | 11 | 12 | 9 | 3 | 3 | 2 | 1 | 1 | 0 | -114 | -99 | -134 | -74 | 4 | 9 | 19 | 1 | 6 | 12 | 14 | 22 | 7 |  | -374 | -22 | -451 | 1234 | -18 | 1242 | -134 | -6
1050 | Tarchon Energy Ltd | PINT | 18 | 21 | 13 | 3 | 5 | -1 | 14 | 16 | 13 | -113 | 45 | -222 | 89 | 4 | 9 | 19 | -2 | -7 | -15 | 300 | 339 | 252 |  | -603 | -27 | -800 | -1417 | -26 | -1403 | 145 | 8
1051 | Aminth Energy Ltd | PINT | 16 | 18 | 13 | 3 | 5 | 0 | 14 | 15 | 12 | -112 | 15 | -207 | 32 | 4 | 9 | 19 | 0 | -2 | -5 | 285 | 328 | 248 |  | -663 | -19 | -1007 | -1695 | -25 | -1681 | 42 | 3
1052 | Lienz (AT) - Obersielach (AT) | PINT | 54 | 62 | 51 | 3 | 6 | 0 | 8 | 11 | 7 | -126 | 9 | -260 | 66 | 4 | 10 | 21 | -2 | -5 | -11 | 176 | 237 | 148 |  | 30874 | 3564 | 1357 | 2207 | 1576 | 808 | 108 | 4
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 64 | 67 | 61 | 6 | 7 | 4 | 14 | 15 | 14 | -244 | -184 | -308 | 55 | 9 | 19 | 41 | -2 | -4 | -9 | 296 | 323 | 277 |  | 32967 | 3809 | 1213 | 1738 | 1671 | 239 | 103 | 0
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 272 | 273 | 271 | 13 | 18 | 8 | 0 | 1 | 0 | -568 | -363 | -803 | 92 | 21 | 44 | 94 | -3 | -7 | -15 | 8 | 14 | 2 |  | -1630 | 62 | -5503 | 30 | -336 | 4 | 158 | 13
1056 | Croatian south connection | light PINT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1057 | HVDC CentraLink | light PINT
1058 | HVDC Interconnector DE-CH | light PINT
1059 | Southern Italy | PINT | 1 | 6 | 0 | 0 | 0 | -2 | 0 | 1 | 0 | 21 | 101 | -4 | -10 | -1 | -2 | -3 | 0 | 1 | 2 | 5 | 26 | 0 |  | 10 | 0 | 17 | 5 | 1 | 5 | -21 | -1
1061 | Reactive compensation for project 197
1062 | Reactive compensation for project 1046
1063 | ZuidWest380 West
1066 | Bulgaria - Turkey | light PINT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1068 | LaSGo Link | light PINT
1074 | Pannonian Corridor | light PINT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1077 | Crete-North Greece-North Macedonia-Bulgaria Interconnector | light PINT
1081 | LAG Interconnector (LAG) | light PINT
1082 | Sea-Socket | light PINT

## 2030NT
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | kg / year | kg / year | kg / year | kg / year | kg / year | kg / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 27 | 37 | 16 | 4 | 6 | 2 | 41 | 45 | 37 | -149 | -58 | -213 | 19 | 5 | 11 | 24 | -1 | -1 | -3 | 1102 | 1210 | 1017 | 1154 | 566 | 30 | 868 | -2122 | 51 | -2140 | 60 | 2 | N/A |  |  | N/A
4 | Interconnection Portugal-Spain | TOOT | 22 | 29 | 14 | 4 | 6 | 2 | 11 | 16 | 7 | -150 | -79 | -203 | 21 | 5 | 11 | 24 | -1 | -2 | -3 | 293 | 436 | 185 |  | -77 | -8 | -9 | -144 | -4 | -140 | 12 | 2 | 766 |  |  | 7.66
16 | Biscay Gulf | TOOT | 221 | 227 | 216 | 34 | 36 | 32 | 278 | 297 | 263 | -1225 | -1142 | -1272 | 655 | 39 | 88 | 197 | -21 | -47 | -105 | 7431 | 8156 | 6916 |  | -2247 | -145 | -1941 | -44571 | -146 | -44461 | 2711 | 56 | 7470 |  |  | 74.7
23 | FR-BE: Avelin/Mastaing-Avelgem-Horta HTLS | TOOT
26 | Reschenpass Interconnector Project | TOOT | 35 | 43 | 27 | -1 | 8 | -8 | 3 | 9 | 1 | 53 | 269 | -290 | 59 | -2 | -4 | -8 | -2 | -4 | -9 | 85 | 245 | 22 |  | -2833 | -225 | -1682 | 38122 | -100 | 38210 | 149 | 5 | 59 |  |  | 0.59
28 | Italy-Montenegro | PINT | 31 | 35 | 24 | -28 | -18 | -35 | 6 | 10 | 4 | 990 | 1263 | 646 | 200 | -32 | -71 | -159 | -6 | -14 | -32 | 159 | 275 | 101 |  | 2187 | -115 | 2829 | -1712 | 101 | -1970 | 186 | 9 | N/A |  |  | N/A
29 | Italy-Tunisia | PINT | 46 | 52 | 41 | -41 | -37 | -43 | 4 | 8 | 0 | 1453 | 1546 | 1322 | 32 | -47 | -105 | -234 | -1 | -1 | -3 | 89 | 177 | 0 |  | -573 | -115 | -291 | -18 | -57 | -36 | 64 | 2 | N/A |  |  | N/A
33 | Central Northern Italy | TOOT | 2 | 3 | 0 | 0 | 1 | 0 | 5 | 9 | 2 | -12 | -3 | -24 | 3 | 0 | 1 | 2 | 0 | 0 | 0 | 137 | 239 | 43 |  | -71 | -4 | -95 | -1175 | -7 | -1171 | 13 | 0 | 2 |  |  | 0.02
35 | CZ Southwest-east corridor | PINT | 48 | 52 | 45 | 47 | 56 | 38 | 19 | 23 | 13 | -1687 | -1355 | -1989 | 105 | 54 | 121 | 272 | -3 | -8 | -17 | 491 | 625 | 352 |  | -2610 | -3 | -2777 | 5870 | -137 | 6096 | 364 | 9 | 748.85714285714 |  |  | 7.4885714285714
36 | Kriegers Flak CGS
37 | Norway - Germany, NordLink | TOOT
39 | DKW-DE, step 3
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 8 | 10 | 7 | 4 | 5 | 3 | 7 | 8 | 7 | -144 | -95 | -179 | 0 | 5 | 10 | 23 | 0 | 0 | 0 | 188 | 196 | 182 |  | -63 | 2 | -17 | -414 | 1 | -407 | 0 | 0 | N/A |  |  | N/A
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 30 | 34 | 23 | 12 | 14 | 6 | 19 | 21 | 14 | -420 | -206 | -517 | 128 | 13 | 30 | 68 | -4 | -9 | -21 | 493 | 544 | 368 |  | 3881 | 243 | 3583 | -29224 | 197 | -29364 | 277 | 5 | 1217.14285714286 |  |  | 12.1714285714286
48 | New SK-HU intercon. - phase 1 | TOOT | 11 | 16 | 6 | 4 | 10 | 0 | 3 | 9 | 0 | -138 | -7 | -372 | 61 | 4 | 10 | 22 | -2 | -4 | -10 | 88 | 243 | 1 |  | 58 | -10 | 107 | 1169 | 4 | 1157 | 86 | 5 | 0 |  |  | 0
62 | Estonia-Latvia 3rd IC | TOOT | 23 | 27 | 20 | 7 | 9 | 6 | 2 | 3 | 1 | -259 | -220 | -328 | 29 | 8 | 19 | 42 | -1 | -2 | -5 | 53 | 73 | 27 |  | -606 | 19 | -452 | 7649 | -3 | 7717 | 114 | 4 | 1457 |  |  | 14.57
78 | South West Cluster | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 3 | 6 | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | -107 | -3 | N/A |  |  | N/A
81 | North South Interconnector | TOOT | 50 | 64 | 39 | 8 | 10 | 6 | 18 | 23 | 14 | -280 | -198 | -366 | 9 | 9 | 20 | 45 | 0 | -1 | -1 | 478 | 605 | 397 |  | 516 | 3 | 1112 | 1102 | 40 | 1087 | 44 | 1 | 5076.28571428571 |  |  | 50.7628571428571
82 | RIDP I | PINT | 14 | 15 | 12 | 3 | 4 | 3 | 11 | 11 | 10 | -118 | -105 | -131 | -9 | 4 | 8 | 19 | 0 | 1 | 1 | 286 | 287 | 285 | 300 | 424 | 37 | 447 | -572 | 49 | -592 | -80 | -1 | 198.000000000015 |  |  | 1.98000000000015
85 | Integration of RES in Alentejo | TOOT | 14 | 15 | 11 | 2 | 3 | 0 | 24 | 28 | 20 | -60 | -5 | -103 | 29 | 2 | 4 | 10 | -1 | -2 | -5 | 633 | 727 | 538 | 620 | 1803 | 107 | 2378 | -6346 | 149 | -6411 | 105 | 2 | N/A |  |  | N/A
92 | ALEGrO
94 | GerPol Improvements
103 | Reinforcements Ring NL phase I | TOOT | 9 | 14 | 7 | 5 | 7 | 3 | 6 | 7 | 5 | -162 | -109 | -249 | 8 | 5 | 12 | 26 | 0 | -1 | -1 | 152 | 175 | 126 |  | -44 | 7 | 19 | 660 | 2 | 671 | 34 | 1 | 7 |  |  | 0.07
107 | Celtic Interconnector | PINT | 124 | 126 | 121 | 23 | 24 | 22 | 68 | 73 | 66 | -823 | -768 | -853 | 206 | 26 | 59 | 132 | -7 | -21 | -33 | 1808 | 1934 | 1683 |  | -742 | -81 | -58 | 4701 | -36 | 4736 | 684 | 21 | 4826 |  |  | 48.26
110 | Norway-Great Britain, North Sea Link | TOOT
111 | 3rd AC Finland-Sweden north | TOOT | 44 | 47 | 41 | 7 | 7 | 7 | 2 | 3 | 0 | -256 | -253 | -259 | -79 | 8 | 18 | 41 | 3 | 6 | 13 | 42 | 78 | 5 |  | -1000 | -63 | -1391 | 10300 | -75 | 10338 | 247 | 12 | 105 |  |  | 0
120 | MOG II: connection of up to 2 GW additional offshore wind Belgium | TOOT | 236 | 243 | 229 | 62 | 63 | 60 | 311 | 311 | 311 | -2200 | -2140 | -2259 | 219 | 70 | 158 | 354 | -7 | -16 | -35 | 7791 | 7791 | 7791 | 2000 | 1636 | 236 | 3042 | -37831 | 226 | -37764 | 467 | 14 | N/A |  |  | N/A
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 37 | 39 | 36 | 13 | 15 | 12 | 5 | 7 | 4 | -479 | -428 | -548 | 443 | 15 | 34 | 77 | -14 | -32 | -71 | 139 | 200 | 105 |  | -1028 | -57 | -1133 | 5753 | -72 | 5800 | 901 | 31 | 3200 |  |  | 32
123 | LitPol Link Stage 2 | TOOT | 58 | 60 | 56 | 32 | 39 | 23 | 3 | 4 | 1 | -1147 | -836 | -1396 | 45 | 37 | 83 | 185 | -1 | -3 | -7 | 80 | 116 | 37 |  | -1640 | -21 | -1829 | 11125 | -97 | 11263 | 120 | 3 | 10566.5714285714 |  |  | 20
124 | NordBalt phase 2 | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | [7 empty] | 0 |  | 0 |  |  | 0
126 | SE North-south short-term reinforcements | PINT | 10 | 11 | 10 | 1 | 2 | 0 | 0 | 1 | 0 | -44 | 0 | -88 | -50 | 1 | 3 | 7 | 2 | 4 | 8 | 8 | 15 | 0 |  | 5 | -19 | -16 | -4086 | -5 | -4101 | -168 | -5 | N/A |  |  | N/A
127 | Central Southern Italy | TOOT | 10 | 12 | 9 | 4 | 5 | 3 | 6 | 9 | 4 | -128 | -102 | -178 | -176 | 4 | 9 | 21 | 6 | 13 | 28 | 141 | 207 | 86 |  | -90 | 0 | -56 | -28 | -3 | -19 | -373 | -18 | 0 |  |  | 0
130 | HVDC SuedOstLink Wolmirstedt to area Isar | PINT | 160 | 160 | 160 | 16 | 16 | 16 | 79 | 79 | 79 | -593 | -593 | -593 | -188 | 19 | 43 | 95 | 6 | 14 | 30 | 1817 | 1817 | 1817 |  | -411635 | -85085 | 664013 | -58515 | -39997 | -24125 | -396 | -9 | N/A |  |  | N/A
132 | HVDC Line A-North | TOOT | 253 | 253 | 253 | 46 | 46 | 46 | 160 | 160 | 160 | -1665 | -1665 | -1665 | -50 | 53 | 120 | 268 | 2 | 4 | 8 | 3691 | 3691 | 3691 |  | -2118291 | -117187 | -554493 | -243605 | -164425 | -28363 | -96 | -3 | N/A |  |  | N/A
138 | Black Sea Corridor | TOOT | 14 | 19 | 11 | -4 | 1 | -8 | 3 | 9 | 0 | 160 | 273 | -47 | -12 | -5 | -12 | -26 | 0 | 1 | 2 | 68 | 248 | 0 |  | 346 | -32 | 557 | 300 | 11 | 257 | 29 | 2 | 11 |  |  | 0
142 | CSE4 | TOOT | 19 | 29 | 13 | -19 | -13 | -25 | 1 | 1 | 0 | 677 | 896 | 471 | -15 | -22 | -49 | -109 | 0 | 1 | 2 | 13 | 36 | 3 |  | 1709 | -32 | 2257 | 49 | 94 | -105 | 18 | 1 | 41 |  |  | 0.41
144 | Mid Continental East corridor | TOOT | 11 | 17 | 6 | -1 | 2 | -3 | 2 | 4 | 0 | 42 | 124 | -58 | -61 | -1 | -3 | -7 | 1 | 3 | 7 | 42 | 101 | 11 |  | -1 | -22 | -6 | 967 | -3 | 948 | -31 | -2 | 109 |  |  | 1.09
150 | Italy-Slovenia | PINT | 45 | 51 | 37 | -47 | -32 | -61 | 2 | 2 | 1 | 1661 | 2190 | 1150 | 342 | -53 | -120 | -267 | -11 | -25 | -55 | 57 | 66 | 47 |  | 10090 | 132 | 11614 | -27455 | 538 | -28163 | 555 | 23 | 333 |  |  | 3.33
153 | France-Alderney-Britain | PINT | 105 | 109 | 99 | 39 | 40 | 38 | 11 | 15 | 3 | -1390 | -1365 | -1433 | 316 | 44 | 100 | 224 | -10 | -23 | -51 | 308 | 426 | 92 |  | -2180 | -96 | -2148 | 31376 | -138 | 31506 | 610 | 20 | 3660 |  |  | 36.6
167 | Viking DKW-GB
170 | Baltic States Synchronization with Continental Europe | PINT | 78 | 87 | 74 | 40 | 46 | 31 | 5 | 11 | 1 | -1421 | -1107 | -1639 | 172 | 45 | 102 | 229 | -4 | -9 | -19 | 144 | 281 | 14 |  | -590 | -10 | -571 | 3914 | -32 | 3962 | 210 | 8 | 10867.7142857143 |  |  | 28
172 | ElecLink | TOOT | 93 | 94 | 93 | 34 | 37 | 32 | 14 | 14 | 14 | -1218 | -1144 | -1324 | 163 | 39 | 88 | 196 | -5 | -12 | -26 | 371 | 386 | 362 |  | -1934 | -93 | -1937 | 25544 | -128 | 25653 | 584 | 14 | 3222 |  |  | 32.22
173 | FR-BE: PSTs Aubange-Moulaine
174 | Greenconnector | PINT | 74 | 78 | 69 | 2 | 23 | -18 | 0 | 1 | 0 | -67 | 657 | -824 | 312 | 2 | 5 | 11 | -10 | -22 | -50 | 8 | 32 | 0 |  | 580 | -67 | 1656 | 15570 | 48 | 15512 | 648 | 21 | 0 |  |  | 0
176 | Hansa PowerBridge I | PINT | 72 | 73 | 71 | 29 | 29 | 29 | 23 | 25 | 21 | -1023 | -1022 | -1025 | 85 | 33 | 74 | 165 | -1 | -6 | -7 | 592 | 630 | 554 |  | -2070 | -68 | -2207 | 12847 | -115 | 12970 | 143 | 10 | 336 |  |  | 3.36
179 | DKE - DE (Kontek2) | PINT | 13 | 14 | 10 | 6 | 8 | 3 | 2 | 2 | 0 | -215 | -105 | -297 | 19 | 7 | 15 | 35 | 0 | -1 | 0 | 43 | 70 | 0 |  | -1223 | -54 | -1577 | 3971 | -82 | 4023 | 15 | 1 | 27 |  |  | 0.27
183 | DKW-DE, Westcoast | TOOT | 11 | 14 | 5 | 6 | 9 | 3 | 5 | 6 | 4 | -202 | -91 | -337 | 149 | 6 | 15 | 33 | -5 | -11 | -24 | 135 | 145 | 116 |  | -185 | -17 | 270 | 3185 | -32 | 3229 | 205 | 8 | 0 |  |  | 0
186 | East of Austria | TOOT | 275 | 289 | 253 | 67 | 71 | 62 | 202 | 221 | 177 | -2382 | -2172 | -2516 | -167 | 76 | 172 | 384 | 5 | 11 | 25 | 4991 | 5079 | 4875 | 2000 | 6117 | 1084 | -1004 | 25215 | 467 | 25099 | -225 | -9 | N/A |  |  | N/A
187 | St. Peter (AT) - Pleinting (DE) | PINT | 69 | 74 | 61 | 28 | 33 | 21 | 46 | 49 | 44 | -983 | -743 | -1182 | 255 | 31 | 71 | 158 | -8 | -18 | -41 | 1174 | 1265 | 1070 |  | 3868 | 270 | 3788 | -26093 | 223 | -26211 | 827 | 19 | 621 |  |  | 6.21
190 | NorthConnect | TOOT | 142 | 174 | 111 | 37 | 48 | 26 | 18 | 24 | 15 | -1324 | -929 | -1728 | -55 | 42 | 95 | 213 | 9 | 4 | 43 | 467 | 637 | 366 |  | -2528 | -191 | -1804 | 44021 | -183 | 44156 | 19 | 2 | 4 |  |  | 0
197 | N-S Finland P1 stage 2 | TOOT | 16 | 16 | 16 | 1 | 1 | 1 | 0 | 0 | 0 | 24 | 24 | 24 | 24 | -1 | -2 | -4 | -1 | -2 | -4 | 953 | 953 | 953 |  | -22812 | -2658 | -629 | -1829 | -1160 | -797 | -6 | -3 | N/A |  |  | N/A
200 | CZ Northwest-South corridor | TOOT | 52 | 54 | 50 | 51 | 65 | 40 | 25 | 31 | 21 | -1838 | -1440 | -2327 | 112 | 59 | 132 | 296 | -4 | -8 | -18 | 668 | 813 | 515 |  | -2772 | -1 | -2978 | 5775 | -146 | 6018 | 380 | 11 | 980.571428571427 |  |  | 9.80571428571427
207 | Reinforcement Northwestern DE
208 | N-S Western DE_section North_1
210 | Wurmlach (AT) - Somplago (IT) interconnection | PINT | 13 | 17 | 9 | -2 | 0 | -4 | 1 | 2 | 0 | 66 | 146 | 7 | 70 | -2 | -5 | -11 | -2 | -5 | -11 | 14 | 42 | 0 |  | 4055 | 178 | 3803 | -30047 | 178 | -30243 | 232 | 4 | 152.857142857147 |  |  | 1.52857142857147
219 | EuroAsia Interconnector | PINT | 136 | 153 | 115 | -78 | -65 | -90 | 0 | 1 | 0 | 2780 | 3230 | 2328 | 510 | -89 | -200 | -448 | -16 | -35 | -79 | 8 | 21 | 0 |  | 22014 | 108 | 22142 | -167591 | 1282 | -169587 | 927 | 43 | 1191.14285714285 |  |  | 11.9114285714285
225 | 2nd interconnector Belgium - Germany | light PINT | 23 | 28 | 21 | 5 | 6 | 4 | 25 | 25 | 25 | -194 | -137 | -225 | 0 | 6 | 14 | 31 | 0 | 0 | 0 | 663 | 688 | 630 |  | 10 | -4 | 147 | -3980 | 4 | -3978 | 0 | 0 | 1590 |  |  | 16
227 | Transbalkan Corridor | PINT | 2 | 4 | 0 | -1 | 0 | -2 | 0 | 1 | 0 | 19 | 75 | -6 | -26 | -1 | -1 | -3 | 1 | 2 | 4 | 11 | 35 | 0 |  | -20 | -1 | -20 | 113 | -2 | 115 | -24 | -1 | N/A |  |  | N/A
228 | Muhlbach - Eichstetten | PINT | 30 | 32 | 29 | 12 | 14 | 11 | 12 | 12 | 11 | -436 | -383 | -497 | 48 | 14 | 31 | 70 | -2 | -3 | -8 | 311 | 339 | 285 |  | -734 | -15 | -741 | 4769 | -38 | 4823 | 209 | 4 | 675 |  |  | 6.75
229 | GerPol Power Bridge II | light PINT | 148 | 152 | 146 | 91 | 92 | 90 | 48 | 51 | 43 | -3245 | -3220 | -3271 | 0 | 104 | 234 | 522 | 0 | 0 | 0 | 1250 | 1401 | 1114 |  | -6694 | -74 | -7492 | 17997 | -338 | 18483 | 0 | 0 | N/A |  |  | N/A
230 | GerPol Power Bridge I | TOOT | 198 | 202 | 194 | 96 | 103 | 91 | 58 | 63 | 53 | -3439 | -3259 | -3674 | 119 | 110 | 248 | 554 | -4 | -9 | -19 | 1525 | 1757 | 1381 |  | -7609 | -87 | -9215 | 21663 | -324 | 22131 | 424 | 12 | N/A |  |  | N/A
231 | Beznau - Tiengen | PINT | 32 | 40 | 24 | 12 | 17 | 7 | 25 | 26 | 23 | -443 | -267 | -590 | 78 | 14 | 32 | 71 | -3 | -6 | -13 | 652 | 703 | 581 |  | -290 | 9 | -135 | -1592 | 4 | -1559 | 315 | 5 | 586 |  |  | 5.86
233 | Connection of Aragon Pumping hydro | PINT | 115 | 124 | 105 | 25 | 29 | 17 | 130 | 168 | 90 | -884 | -618 | -1026 | 0 | 28 | 64 | 142 | 0 | 0 | 0 | 3320 | 4122 | 2475 |  | -7277 | -403.5 | -8746 | -6011.5 | -550.5 | -5700.5 | 1612.5 | 26.5 | N/A |  |  | N/A
234 | DKE - PL-1 | PINT | 70 | 71 | 69 | 43 | 45 | 42 | 15 | 19 | 10 | -1536 | -1502 | -1602 | 240 | 49 | 111 | 247 | -8 | -17 | -39 | 389 | 528 | 271 |  | -2818 | -20 | -3056 | 11432 | -131 | 11646 | 399 | 20 | 680 |  |  | 6.8
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Grafenrheinfeld | PINT | 595 | 595 | 595 | 93 | 93 | 93 | 342 | 342 | 342 | -3333 | -3333 | -3333 | -62 | 107 | 240 | 537 | 2 | 4 | 10 | 7919 | 7919 | 7919 |  | -3996049 | -286378 | -572245 | -443397 | -297607 | -75018 | -230 | 1 | N/A |  |  | N/A
239 | Fenno-Skan 1 renewal | light PINT | 27 | 29 | 25 | 4 | 4 | 4 | 1 | 2 | 0 | -148 | -143 | -153 | 0 | 5 | 11 | 24 | 0 | 0 | 0 | 31 | 58 | 5 |  | 45 | -1 | 120 | -5260 | 10 | -5265 | 0 | 0 | N/A |  |  | N/A
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines | PINT | 5 | 6 | 4 | -4 | -2 | -7 | 0 | 0 | 0 | 149 | 246 | 89 | 22 | -5 | -11 | -24 | -1 | -2 | -4 | 4 | 12 | 0 |  | 150 | -15 | 110 | 817 | 10 | 786 | 26 | 2 | N/A |  |  | N/A
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 7 | 11 | 5 | -6 | -3 | -9 | 0 | 0 | 0 | 198 | 323 | 107 | 0 | -6 | -14 | -32 | 0 | 0 | 0 | 1 | 3 | 0 |  | 189 | -17 | 132 | 1194 | 13 | 1157 | 0 | 0 | N/A |  |  | N/A
244 | Vigy - Uchtelfangen area | PINT | 136 | 141 | 128 | 56 | 63 | 52 | 56 | 58 | 54 | -2011 | -1856 | -2240 | 284 | 64 | 145 | 324 | -9 | -20 | -46 | 1491 | 1622 | 1419 |  | -3359 | -67 | -3399 | 20848 | -175 | 21092 | 1100 | 23 | 2987 |  |  | 29.87
245 | Upgrade Meeden - Diele
247 | AQUIND Interconnector | PINT | 149 | 155 | 137 | 55 | 58 | 51 | 16 | 22 | 10 | -1949 | -1805 | -2072 | 245 | 62 | 140 | 314 | -15 | -18 | -74 | 423 | 605 | 270 |  | -3306 | -140 | -3354 | 43913 | -212 | 44109 | 1058 | 31 | 5129 |  |  | 51.29
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 18 | 22 | 12 | -1 | 2 | -6 | 0 | 0 | 0 | 47 | 221 | -74 | 54 | -2 | -3 | -8 | -2 | -4 | -9 | 8 | 35 | 0 |  | 101 | -15 | 325 | 3850 | 9 | 3839 | 130 | 4 | 0 |  |  | 0
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | light PINT | 22 | 22 | 22 | 4 | 4 | 4 | 11 | 11 | 11 | -137 | -137 | -137 | 0 | 4 | 10 | 22 | 0 | 0 | 0 | 281 | 281 | 281 |  | -997 | -116 | -27 | -80 | -51 | -35 | 0 | 0 | N/A |  |  | N/A
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT - A2 | 37 | 43 | 29 | 21 | 24 | 18 | 0 | 1 | 0 | -762 | -635 | -851 | 86 | 24 | 55 | 123 | -3 | -6 | -14 | 7 | 24 | 0 |  | -3404 | -36 | -3161 | 44691 | -164 | 44977 | 304 | 7 | 1087 |  |  | 10.87
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 130 | 130 | 130 | -16 | -16 | -16 | 19 | 19 | 19 | 575 | 575 | 575 | 230 | -18 | -41 | -93 | -7 | -17 | -37 | 444 | 444 | 444 |  | 1973704 | -80104 | 3547520 | 117275 | 77194 | -24596 | 391 | 16 | N/A |  |  | N/A
258 | Westcoast line | No assessment
259 | HU-RO | PINT | 8 | 12 | 3 | -7 | -2 | -10 | 1 | 2 | 0 | 240 | 357 | 87 | 145 | -8 | -17 | -39 | -5 | -10 | -23 | 14 | 41 | 1 |  | 62 | -39 | 75 | -1779 | -14 | -1808 | 155 | 8 | N/A |  |  | N/A
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 73 | 77 | 68 | 21 | 22 | 19 | 59 | 61 | 58 | -733 | -690 | -792 | 585 | 23 | 53 | 118 | -19 | -42 | -94 | 1587 | 1621 | 1548 |  | -1343 | -72 | -1534 | -4581 | -85 | -4527 | 1218 | 41 | N/A |  |  | N/A
262 | Belgium-Netherlands: Zandvliet-Rilland | TOOT | 28 | 29 | 28 | 4 | 4 | 3 | 43 | 44 | 42 | -141 | -121 | -159 | 44 | 4 | 10 | 23 | -2 | -3 | -7 | 1148 | 1164 | 1127 |  | 107 | 0 | 217 | -9427 | 13 | -9435 | 171 | 3 | 2277 |  |  | 22.77
263 | Lake Constance East | light PINT | 74 | 79 | 70 | 25 | 30 | 20 | 42 | 43 | 37 | -891 | -703 | -1074 | 0 | 29 | 64 | 143 | 0 | 0 | 0 | 1062 | 1176 | 964 |  | -276 | 53 | 51 | 6532 | 41 | 6591 | 0 | 0 | N/A |  |  | N/A
264 | Swiss Roof I | light PINT | 111 | 118 | 105 | 25 | 30 | 22 | 52 | 58 | 45 | -908 | -792 | -1077 | 0 | 29 | 65 | 146 | 0 | 0 | 0 | 1312 | 1463 | 1182 |  | 139 | -8 | 636 | 6574 | 59 | 6553 | 0 | 0 | N/A |  |  | N/A
265 | Tessin | light PINT
266 | Swiss Ellipse I | PINT | 59 | 70 | 48 | 18 | 22 | 15 | 33 | 35 | 31 | -645 | -536 | -770 | 3 | 21 | 46 | 104 | 0 | 0 | -2 | 836 | 973 | 733 |  | 510 | 8 | 345 | -1149 | 15 | -1192 | 262 | 0 | 698 |  |  | 6.98
267 | Hansa PowerBridge II | light PINT | 72 | 73 | 71 | 29 | 29 | 29 | 23 | 25 | 21 | -1023 | -1022 | -1025 | N/A | 33 | 74 | 165 | N/A | N/A | N/A | 592 | 630 | 554 |  | -2070 | -68 | -2207 | 12847 | -115 | 12970 | N/A | N/A | N/A |  |  | N/A
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 93 | 102 | 88 | 15 | 23 | 7 | 136 | 142 | 130 | -523 | -258 | -808 | 413 | 17 | 38 | 84 | -13 | -30 | -67 | 3628 | 3908 | 3403 |  | -1458 | -91 | -1444 | -24276 | -102 | -24208 | 1750 | 37 | 3623 |  |  | 36.23
276 | FR-ES project -Navarra-Landes | PINT | 93 | 102 | 88 | 15 | 23 | 7 | 136 | 142 | 130 | -523 | -258 | -808 | 413 | 17 | 38 | 84 | -13 | -30 | -67 | 3628 | 3908 | 3403 |  | -1458 | -91 | -1444 | -24276 | -102 | -24208 | 1750 | 37 | 3623 |  |  | 36.23
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 66 | 73 | 59 | 29 | 34 | 27 | 6 | 9 | 1 | -1051 | -951 | -1209 | 160 | 34 | 76 | 169 | -5 | -12 | -26 | 157 | 244 | 36 |  | -1804 | -54 | -1760 | 19440 | -104 | 19565 | 512 | 13 | 256 |  |  | 2.56
283 | TuNur | PINT | 550 | 574 | 525 | 133 | 138 | 127 | 423 | 423 | 423 | -4736 | -4532 | -4939 | 101 | 152 | 341 | 762 | -3 | -7 | -16 | 10793 | 10793 | 10793 | 4000 | -226292 | -18498 | -148286 | -191272 | -12675 | -182050 | 610 | 8 | N/A |  |  | N/A
284 | LEG1 | PINT | 172 | 175 | 169 | -110 | -100 | -117 | 1 | 3 | 0 | 3911 | 4167 | 3581 | 698 | -125 | -282 | -630 | -19 | -43 | -97 | 28 | 82 | 0 | 2000 | 24957 | 4 | 29759 | -169189 | 1431 | -171249 | 1150 | 53 | N/A |  |  | N/A
285 | GridLink | PINT | 105 | 109 | 99 | 39 | 40 | 38 | 11 | 15 | 3 | -1390 | -1365 | -1433 | 440 | 44 | 100 | 224 | -12 | -32 | -71 | 308 | 426 | 92 |  | -2180 | -96 | -2148 | 31376 | -138 | 31506 | 1155 | 31 | 3660 |  |  | 36.6
286 | Greenlink | PINT | 63 | 65 | 62 | 6 | 7 | 5 | 46 | 50 | 42 | -231 | -188 | -267 | 39 | 7 | 17 | 37 | -3 | -2 | -4 | 1207 | 1253 | 1147 |  | -55 | -38 | 391 | -4255 | 3 | -4260 | 244 | 5 | 2748 |  |  | 20
293 | Southern Aegean Interconnector | PINT | 62 | 71 | 54 | 31 | 38 | 26 | 48 | 50 | 45 | -1091 | -925 | -1346 | 33 | 35 | 79 | 176 | -1 | -2 | -5 | 1268 | 1292 | 1234 | 582 | -752 | 32 | -545 | -73 | -16 | 24 | 40 | 2 | N/A |  |  | N/A
296 | Britib | PINT | 254 | 275 | 233 | 71 | 76 | 68 | 175 | 181 | 169 | -2543 | -2419 | -2718 | 153 | 81 | 183 | 409 | -5 | -11 | -25 | 4698 | 4963 | 4433 |  | -4435 | -223 | -4397 | 11718 | -294 | 11962 | 952 | 16 | 4555 |  |  | 45.55
297 | BRABO II + III | PINT | 17 | 19 | 14 | 2 | 3 | 2 | 29 | 31 | 26 | -85 | -74 | -96 | 44 | 3 | 6 | 14 | -1 | -3 | -7 | 770 | 830 | 670 |  | 78 | 6 | 104 | -7433 | 11 | -7437 | 163 | 3 | 1550 |  |  | 15.5
299 | SACOI3 | TOOT | 41 | 49 | 34 | 2 | 4 | 2 | 6 | 7 | 5 | -85 | -55 | -141 | 96 | 3 | 6 | 14 | -3 | -7 | -16 | 162 | 185 | 119 |  | 87 | -43 | 382 | 1513 | 0 | 1486 | 196 | 6 | 781 |  |  | 7.81
309 | NeuConnect | TOOT | 75 | 81 | 69 | 21 | 23 | 19 | 46 | 52 | 43 | -752 | -679 | -834 | 435 | 24 | 54 | 121 | -14 | -31 | -70 | 1183 | 1235 | 1107 |  | -1430 | -81 | -1598 | 1007 | -91 | 1063 | 799 | 30 | 2077 |  |  | 20.77
312 | St. Peter (AT) - Tauern (AT) | TOOT | 275 | 283 | 268 | 66 | 72 | 57 | 89 | 92 | 86 | -2368 | -2038 | -2590 | 254 | 76 | 170 | 381 | -7 | -15 | -35 | 2212 | 2264 | 2127 |  | 2938 | 580 | -840 | 9971 | 214 | 9957 | 1114 | 20 | 2379 |  |  | 23.79
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 144 | 152 | 137 | 66 | 72 | 57 | 80 | 83 | 77 | -2363 | -2033 | -2585 | 275 | 76 | 170 | 380 | -9 | -20 | -44 | 1984 | 2036 | 1899 |  | -1412 | 73 | -960 | 9971 | -7 | 9805 | 1210 | 22 | 2379 |  |  | 23.79
320 | Slovenia-Hungary/Croatia interconnection | TOOT | 3 | 9 | 0 | 3 | 5 | 2 | 2 | 7 | 0 | -95 | -60 | -163 | -23 | 3 | 7 | 15 | 1 | 2 | 4 | 57 | 171 | 11 |  | -282 | 2 | -343 | 2730 | -12 | 2752 | -3 | -2 | 39 |  |  | 0
322 | Wullenstetten - Border Area (DE-AT) | PINT | 0 | 0 | 0 | -2 | -2 | -2 | -15 | -15 | -15 | 53 | 53 | 53 | -27 | -2 | -4 | -9 | 1 | 2 | 4 | -347 | -347 | -347 |  | 110792 | 8435 | 515693 | -13815 | -11425 | 4142 | -97 | -2 | N/A |  |  | N/A
323 | Dekani (SI) - Zaule (IT) interconnection | PINT | 7 | 9 | 4 | -9 | -4 | -13 | 1 | 3 | 0 | 317 | 480 | 154 | 25 | -10 | -23 | -51 | -1 | -2 | -4 | 23 | 76 | 0 |  | 786 | -13 | 1069 | 238 | 43 | 171 | 65 | 3 | 62 |  |  | 0.62
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | PINT | 5 | 7 | 1 | -7 | -2 | -11 | 0 | 0 | 0 | 260 | 376 | 69 | 5 | -8 | -19 | -42 | 0 | 0 | -1 | 2 | 4 | 0 |  | 780 | -14 | 1053 | 134 | 42 | 67 | 26 | 1 | 53 |  |  | 0.53
325 | Obersielach (AT) - Podlog (SI) | PINT | 23 | 29 | 16 | 26 | 30 | 22 | 3 | 6 | 1 | -943 | -785 | -1085 | 168 | 30 | 68 | 152 | -5 | -12 | -27 | 71 | 161 | 31 |  | 1097 | 156 | 279 | -26082 | 3 | -26049 | 272 | 11 | N/A |  |  | N/A
328 | Interconnector DE-LUX | PINT | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3 | 2 | -11 | -19 | 0 | 0 | 0 | 1 | 1 | 3 | 3 | 8 | 0 |  | -3 | -1 | 2 | -2 | -1 | -2 | -37 | -1 | 159 |  |  | 1.59
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 236 | 236 | 236 | 62 | 62 | 62 | 311 | 311 | 311 | -2200 | -2200 | -2200 | -22 | 70 | 158 | 354 | 1 | 2 | 4 | 7791 | 7791 | 7791 |  | 2725 | 201 | 5141 | -6959 | 426 | -7046 | -79 | -2 | N/A |  |  | N/A
330 | 4th 400kV CZ-SK interconnector | light PINT | 4 | 8 | 1 | -2 | -1 | -3 | 0 | 0 | 0 | 68 | 109 | 38 | N/A | -2 | -5 | -11 | N/A | N/A | N/A | 5 | 8 | 3 |  | 292 | -6 | 350 | 382 | 16 | 353 | N/A | N/A | N/A |  |  | N/A
333 | PST Foretaille | PINT - A1 | 96 | 103 | 85 | 52 | 61 | 46 | 0 | 1 | 0 | -1843 | -1633 | -2168 | 191 | 59 | 133 | 297 | -6 | -14 | -40 | 4 | 14 | 0 |  | -2350 | -26 | -2174 | 31121 | -114 | 31318 | 630 | 16 | 238 |  |  | 2.38
335 | Project 335 - North Sea Wind Power Hub | light PINT | 1231 | 1231 | 1231 | 381 | 384 | 379 | 1505 | 1546 | 1463 | -13622 | -13543 | -13700 | 0 | 436 | 981 | 2193 | 0 | 0 | 0 | 39795 | 40199 | 39391 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | N/A
336 | Prati (IT) – Steinach (AT) | No assessment
338 | Adriatic HVDC link | PINT | 24 | 38 | 12 | 0 | 2 | -2 | 8 | 13 | 4 | 2 | 61 | -61 | 253 | 0 | 0 | 0 | -8 | -18 | -41 | 207 | 346 | 94 |  | 248 | -26 | 465 | 1307 | 12 | 1274 | 497 | 26 | 13 |  |  | 0
339 | Italian HVDC tri-terminal link | PINT | 8 | 13 | 4 | 2 | 4 | 1 | 2 | 3 | 1 | -74 | -38 | -142 | 198 | 2 | 5 | 12 | -6 | -14 | -32 | 56 | 83 | 22 |  | -286 | -17 | -308 | -37 | -22 | -22 | 415 | 24 | N/A |  |  | N/A
340 | Avelgem-Center: new corridor (Boucle du Hainaut) | TOOT | 157 | 157 | 157 | 41 | 41 | 41 | 207 | 207 | 207 | -1467 | -1467 | -1467 | -76 | 47 | 106 | 236 | 2 | 5 | 12 | 5194 | 5194 | 5194 |  | 1817 | 134 | 3427 | -4639 | 284 | -4697 | -160 | -6 | N/A |  |  | N/A
341 | North CSE Corridor | PINT | 3 | 5 | 0 | -1 | 1 | -6 | 0 | 1 | 0 | 32 | 203 | -29 | 3 | -1 | -2 | -5 | 0 | 0 | -1 | 8 | 28 | 1 |  | -95 | -2 | -112 | 301 | -6 | 307 | 12 | 0 | N/A |  |  | N/A
342 | Central Balkan Corridor | PINT | 4 | 6 | 1 | 0 | 2 | -3 | 0 | 0 | 0 | 15 | 109 | -71 | -40 | 0 | -1 | -2 | 1 | 3 | 6 | 3 | 7 | 0 |  | 24 | -8 | 59 | 132 | 0 | 126 | -35 | -2 | N/A |  |  | N/A
343 | CSE1 New | PINT | 10 | 13 | 8 | -10 | -6 | -15 | 0 | 1 | 0 | 352 | 552 | 201 | -33 | -11 | -25 | -57 | 1 | 2 | 5 | 12 | 25 | 0 |  | 594 | -25 | 732 | 533 | 29 | 465 | -42 | -2 | N/A |  |  | N/A
344 | Reinforcements Ring NL phase II | PINT
346 | ZuidWest380 NL Oost | PINT | 17 | 19 | 14 | 2 | 3 | 2 | 29 | 31 | 26 | -85 | -74 | -96 | 26 | 3 | 6 | 14 | -1 | -2 | -4 | 770 | 830 | 670 |  | 78 | 6 | 104 | -7433 | 11 | -7437 | 122 | 1 | 1550 |  |  | 15.5
348 | NoordWest380 NL | PINT
349 | MaresConnect | PINT | 217 | 218 | 217 | 33 | 39 | 24 | 201 | 203 | 198 | -1173 | -865 | -1384 | 165 | 38 | 84 | 189 | -5 | -12 | -27 | 5197 | 5350 | 5044 | 1800 | 3134 | 115 | 5383 | -12917 | 283 | -13032 | 426 | 14 | 3091 |  |  | 30.91
350 | South Balkan Corridor
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 45 | 52 | 39 | -10 | -3 | -14 | 2 | 4 | 0 | 365 | 492 | 98 | 178 | -12 | -26 | -59 | -6 | -13 | -29 | 46 | 113 | 23 |  | 4922 | 114 | 5191 | -26117 | 223 | -26417 | 324 | 12 | 51 |  |  | 0.51
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 3 | 5 | 2 | -3 | -1 | -5 | 0 | 1 | 0 | 106 | 190 | 31 | N/A | -3 | -8 | -17 | N/A | N/A | N/A | 10 | 20 | 5 |  | 107 | -3 | 165 | 141 | 6 | 131 | N/A | N/A | N/A |  |  | N/A
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 17 | 19 | 14 | 2 | 3 | 2 | 29 | 31 | 26 | -85 | -74 | -96 | 47 | 3 | 6 | 14 | -2 | -3 | -8 | 770 | 830 | 670 |  | 78 | 6 | 104 | -7433 | 11 | -7437 | 192 | 3 | 1550 |  |  | 15.5
378 | Transformer Gatica | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | N/A
379 | Uprate Gatica lines | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | N/A
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 275 | 275 | 275 | 60 | 60 | 60 | 188 | 188 | 188 | -2160 | -2160 | -2160 | -65 | 69 | 156 | 348 | 2 | 5 | 11 | 4343 | 4343 | 4343 |  | -3908614 | -114618 | -4205656 | -243283 | -159127 | -35654 | -129 | -4 | N/A |  |  | N/A
1039 | SE North-south long-term reinforcements | light PINT | 17 | 29 | 8 | 3 | 4 | 2 | 19 | 19 | 19 | -105 | -55 | -149 | 0 | 3 | 8 | 17 | 0 | 0 | 0 | 491 | 517 | 465 |  | -37 | -3 | 63 | -4420 | 9 | -4422 | 0 | 0 | N/A |  |  | N/A
1040 | LirIC | PINT | 83 | 84 | 82 | 9 | 11 | 8 | 59 | 63 | 56 | -324 | -277 | -376 | 308 | 10 | 23 | 52 | -9 | -20 | -44 | 1563 | 1666 | 1497 |  | -128 | -50 | 445 | -5726 | 1 | -5729 | 315 | 18 | 2917 |  |  | 28
1041 | GREGY Interconnector | PINT | 186 | 191 | 180 | -377 | -333 | -417 | 2 | 7 | 0 | 13476 | 14891 | 11905 | 1635 | -431 | -970 | -2170 | -41 | -92 | -205 | 62 | 184 | 0 |  | 32889 | -191 | 36417 | -165035 | 1903 | -168119 | 3467 | 126 | N/A |  |  | N/A
1042 | Offshore wind integration | PINT | 79 | 82 | 75 | 22 | 25 | 19 | 114 | 122 | 107 | -782 | -693 | -901 | -58 | 25 | 56 | 126 | 2 | 4 | 9 | 2739 | 2744 | 2734 | 700 | 768 | 99 | 1090 | -12341 | 101 | -12339 | -70 | -5 | N/A |  |  | N/A
1043 | Wahle-Mecklar
1046 | N-S Finland P1 stage 3 | PINT | 6 | 10 | 2 | -6 | 1 | -12 | 4 | 8 | 0 | -206 | 32 | -443 | -32 | 7 | 15 | 33 | 1 | 2 | 5 | 103 | 130 | 76 |  | 315 | 37 | 9 | 25 | 16 | 11 | -88 | -5 | N/A |  |  | N/A
1047 | Emden-Eemshaven | light PINT | 11 | 12 | 9 | 6 | 8 | 4 | 6 | 7 | 5 | -216 | -158 | -287 | 0 | 7 | 16 | 35 | 0 | 0 | 0 | 169 | 181 | 148 |  | 27 | 9 | 141 | 1139 | 11 | 1146 | 0 | 0 | N/A |  |  | N/A
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | light PINT | 147 | 154 | 140 | -282 | -247 | -312 | 1 | 3 | 0 | 10066 | 11141 | 8823 | 0 | -322 | -725 | -1621 | 0 | 0 | 0 | 28 | 81 | 0 |  | 9433 | -270 | 11808 | -34007 | 595 | -35034 | 0 | 0 | N/A |  |  | N/A
1049 | Cronos Energy Ltd | PINT | 37 | 39 | 36 | 13 | 15 | 12 | 5 | 7 | 4 | -479 | -428 | -548 | 171 | 15 | 34 | 77 | -5 | -12 | -28 | 139 | 200 | 105 |  | -1028 | -57 | -1133 | 5753 | -72 | 5800 | 872 | 25 | 3200 |  |  | 32
1050 | Tarchon Energy Ltd | PINT | 58 | 61 | 55 | 15 | 16 | 13 | 38 | 42 | 37 | -540 | -482 | -584 | 254 | 17 | 39 | 87 | -8 | -18 | -41 | 1009 | 1051 | 976 |  | -1083 | -60 | -1277 | -849 | -68 | -809 | 833 | 32 | 1575 |  |  | 15.75
1051 | Aminth Energy Ltd | PINT | 49 | 49 | 49 | 11 | 13 | 10 | 31 | 33 | 27 | -405 | -365 | -459 | 197 | 13 | 29 | 65 | -6 | -14 | -32 | 821 | 906 | 704 |  | -914 | -21 | -1136 | -2683 | -32 | -2644 | 1037 | 37 | 1570 |  |  | 15.7
1052 | Lienz (AT) - Obersielach (AT) | PINT | 110 | 113 | 106 | 34 | 46 | 22 | 10 | 14 | 8 | -1207 | -790 | -1661 | 159 | 38 | 87 | 194 | -5 | -11 | -25 | 272 | 369 | 219 |  | 3504 | 364 | 103 | 27412 | 236 | 27169 | 242 | 10 | N/A |  |  | N/A
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 104 | 108 | 98 | 12 | 14 | 11 | 27 | 28 | 27 | -448 | -385 | -521 | 85 | 14 | 32 | 72 | -2 | -6 | -12 | 713 | 728 | 703 |  | -213 | 181 | -3393 | 29532 | -8 | 29508 | 296 | 5 | 316 |  |  | 3.16
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 246 | 247 | 245 | 0 | 4 | -6 | 2 | 3 | 1 | 1 | 227 | -143 | 137 | 0 | 0 | 0 | -4 | -10 | -22 | 49 | 67 | 38 |  | 1047 | 29 | -909 | 306 | -148 | 127 | 183 | 15 | 11 |  |  | 0.11
1056 | Croatian south connection | light PINT | [12 empty] | 0 |  |  |  | 0 | 0 | 0 | [10 empty] | 0 | 0 | N/A |  |  | N/A
1057 | HVDC CentraLink | light PINT
1058 | HVDC Interconnector DE-CH | light PINT
1059 | Southern Italy | PINT | 1 | 3 | 0 | -1 | 1 | -2 | 0 | 1 | 0 | 25 | 87 | -39 | -11 | -1 | -2 | -4 | 0 | 1 | 2 | 12 | 46 | 0 |  | -54 | -2 | -59 | -27 | -4 | -23 | -34 | -1 | N/A |  |  | N/A
1061 | Reactive compensation for project 197
1062 | Reactive compensation for project 1046
1063 | ZuidWest380 West
1066 | Bulgaria - Turkey | light PINT | 236 | 241 | 232 | -16 | -12 | -20 | 0 | 1 | 0 | 569 | 710 | 428 | N/A | -18 | -41 | -92 | N/A | N/A | N/A | 10 | 17 | 2 |  | 1893 | -170 | -466 | 2058 | 383 | 1399 | N/A | N/A | N/A |  |  | N/A
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 128 | 135 | 124 | -9 | -7 | -13 | 0 | 0 | 0 | 320 | 469 | 237 | N/A | -10 | -23 | -52 | N/A | N/A | N/A | 4 | 9 | 0 |  | 1077 | -104 | 85 | 1420 | 196 | 1074 | N/A | N/A | N/A |  |  | N/A
1068 | LaSGo Link | light PINT | 54 | 55 | 52 | 16 | 17 | 15 | 15 | 15 | 14 | -562 | -525 | -598 | N/A | 18 | 40 | 90 | N/A | N/A | N/A | 406 | 429 | 384 |  | -589 | -20 | -739 | 3635 | -26 | 3663 | N/A | N/A | N/A |  |  | N/A
1074 | Pannonian Corridor | light PINT | 8 | 11 | 6 | -5 | -4 | -6 | 1 | 3 | 0 | 170 | 211 | 134 | N/A | -5 | -12 | -27 | N/A | N/A | N/A | 26 | 71 | 0 |  | 247 | -16 | 249 | 1124 | 16 | 1085 | N/A | N/A | N/A |  |  | N/A
1077 | Crete-North Greece-North Macedonia-Bulgaria Interconnector | light PINT | 3 | 5 | 2 | -2 | -1 | -3 | 0 | 0 | 0 | 71 | 115 | 27 | N/A | -2 | -5 | -11 | N/A | N/A | N/A | 3 | 4 | 1 |  | 111 | -3 | 206 | 358 | 8 | 349 | N/A | N/A | N/A |  |  | N/A
1081 | LAG Interconnector (LAG) | light PINT | 241 | 280 | 201 | -310 | -270 | -349 | 0 | 0 | 0 | 11055 | 12472 | 9637 | N/A | -354 | -796 | -1780 | N/A | N/A | N/A | 44 | 90 | -3 | [7 empty] | N/A | N/A | N/A |  |  | N/A
1082 | Sea-Socket | light PINT | 47 | 50 | 45 | 10 | 10 | 9 | 39 | 41 | 38 | -348 | -336 | -356 | N/A | 11 | 25 | 56 | N/A | N/A | N/A | 1050 | 1065 | 1035 | 700 | 1520 | 87 | 2219 | -1705 | 134 | -1755 | N/A | N/A | N/A |  |  | N/A

## 2030GA
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_market_SEW |  |  | ΔRES |  |  | ΔRES_MW
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | low | mid | high | weighted avg | max | min | Explicit
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW
1 | RES in north of Portugal | TOOT | 18 | 21 | 14 | 4 | 5 | 3 | 31 | 31 | 31 | -105 | -79 | -144 | 3 | 7 | 16 | 721 | 747 | 695 | 1154
4 | Interconnection Portugal-Spain | TOOT | 91 | 96 | 85 | 23 | 31 | 18 | 104 | 120 | 86 | -650 | -505 | -898 | 16 | 42 | 100 | 2400 | 2748 | 1995
16 | Biscay Gulf | TOOT | 227 | 230 | 225 | 50 | 59 | 45 | 283 | 294 | 276 | -1436 | -1284 | -1698 | 36 | 93 | 221 | 6610 | 7070 | 6372
23 | FR-BE: Avelin/Mastaing-Avelgem-Horta HTLS | TOOT
26 | Reschenpass Interconnector Project | TOOT | 18 | 25 | 13 | -12 | -8 | -14 | 3 | 7 | 0 | 333 | 410 | 220 | -8 | -22 | -51 | 64 | 161 | 25
28 | Italy-Montenegro | PINT | 22 | 24 | 19 | -77 | -73 | -84 | 6 | 15 | 2 | 2206 | 2404 | 2079 | -55 | -143 | -340 | 126 | 325 | 36
29 | Italy-Tunisia | PINT | 29 | 37 | 23 | -38 | -36 | -40 | 12 | 16 | 10 | 1082 | 1156 | 1018 | -27 | -70 | -167 | 268 | 386 | 198
33 | Central Northern Italy | TOOT | 3 | 6 | 1 | 1 | 2 | 0 | 2 | 6 | 0 | -19 | 6 | -59 | 0 | 1 | 3 | 54 | 156 | 4
35 | CZ Southwest-east corridor | PINT | 33 | 41 | 28 | 25 | 28 | 22 | 17 | 20 | 15 | -707 | -619 | -789 | 18 | 46 | 109 | 378 | 452 | 325
36 | Kriegers Flak CGS
37 | Norway - Germany, NordLink | TOOT
39 | DKW-DE, step 3
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 11 | 11 | 10 | 8 | 9 | 7 | 1 | 2 | 1 | -230 | -197 | -257 | 6 | 15 | 35 | 31 | 36 | 24
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 32 | 34 | 28 | 17 | 20 | 8 | 17 | 19 | 13 | -482 | -221 | -566 | 12 | 31 | 74 | 376 | 454 | 294
48 | New SK-HU intercon. - phase 1 | TOOT | 18 | 24 | 13 | 10 | 14 | 5 | 3 | 7 | 0 | -280 | -129 | -393 | 7 | 18 | 43 | 69 | 166 | 2
62 | Estonia-Latvia 3rd IC | TOOT | 17 | 20 | 12 | 1 | 4 | 0 | 2 | 3 | 0 | -42 | 3 | -124 | 1 | 3 | 7 | 46 | 77 | 4
78 | South West Cluster | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
81 | North South Interconnector | TOOT | 45 | 61 | 37 | 9 | 11 | 8 | 28 | 33 | 20 | -271 | -220 | -319 | 7 | 18 | 42 | 633 | 765 | 483
82 | RIDP I | PINT | 20 | 27 | 15 | 3 | 4 | 2 | 15 | 17 | 13 | -82 | -56 | -107 | 2 | 5 | 13 | 337 | 377 | 294 | 300
85 | Integration of RES in Alentejo | TOOT | 14 | 15 | 14 | 4 | 7 | 2 | 23 | 31 | 19 | -110 | -62 | -208 | 3 | 7 | 17 | 529 | 690 | 448 | 494
92 | ALEGrO
94 | GerPol Improvements
103 | Reinforcements Ring NL phase I | TOOT | 8 | 11 | 5 | 9 | 10 | 7 | 2 | 4 | 0 | -243 | -194 | -296 | 6 | 16 | 37 | 43 | 102 | 10
107 | Celtic Interconnector | PINT | 136 | 139 | 132 | 28 | 32 | 22 | 74 | 78 | 70 | -792 | -622 | -902 | 20 | 51 | 122 | 1706 | 1784 | 1655
110 | Norway-Great Britain, North Sea Link | TOOT
111 | 3rd AC Finland-Sweden north | TOOT | 29 | 31 | 27 | 3 | 6 | -1 | 2 | 3 | 1 | -76 | 20 | -172 | 2 | 5 | 12 | 40 | 63 | 17
120 | MOG II: connection of up to 2 GW additional offshore wind Belgium | TOOT | 293 | 295 | 291 | 73 | 76 | 70 | 354 | 358 | 350 | -2076 | -1987 | -2157 | 52 | 135 | 320 | 7860 | 7975 | 7746 | 2000
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 45 | 49 | 41 | 15 | 16 | 12 | 13 | 17 | 11 | -424 | -348 | -466 | 11 | 28 | 65 | 313 | 378 | 267
123 | LitPol Link Stage 2 | TOOT | 51 | 61 | 40 | 31 | 40 | 20 | 6 | 8 | 4 | -875 | -564 | -1147 | 22 | 57 | 135 | 136 | 180 | 103
124 | NordBalt phase 2 | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 6 | 6 | 6 | 0 | 1 | -1 | 1 | 2 | 0 | -8 | 21 | -36 | 0 | 1 | 1 | 28 | 55 | 0
127 | Central Southern Italy | TOOT | 22 | 23 | 21 | 6 | 8 | 3 | 17 | 24 | 9 | -161 | -92 | -231 | 4 | 10 | 25 | 390 | 483 | 223
130 | HVDC SuedOstLink Wolmirstedt to area Isar | PINT | 150 | 158 | 136 | 9 | 11 | 6 | 74 | 81 | 64 | -322 | -227 | -398 | 8 | 21 | 50 | 1589 | 1771 | 1400
132 | HVDC Line A-North | TOOT | 259 | 269 | 225 | 40 | 48 | 27 | 170 | 182 | 136 | -1406 | -963 | -1700 | 35 | 91 | 217 | 3688 | 4001 | 2969
138 | Black Sea Corridor | TOOT | 6 | 8 | 5 | 3 | 4 | 1 | 3 | 8 | 1 | -79 | -35 | -114 | 2 | 5 | 12 | 72 | 179 | 28
142 | CSE4 | TOOT | 47 | 51 | 42 | -49 | -38 | -57 | 13 | 18 | 9 | 1393 | 1618 | 1090 | -35 | -91 | -214 | 307 | 408 | 208
144 | Mid Continental East corridor | TOOT | 19 | 23 | 16 | -11 | -3 | -15 | 5 | 7 | 0 | 303 | 438 | 79 | -8 | -20 | -47 | 114 | 165 | 0
150 | Italy-Slovenia | PINT | 31 | 38 | 28 | -64 | -45 | -81 | 1 | 2 | 0 | 1828 | 2303 | 1291 | -46 | -119 | -282 | 15 | 61 | -1
153 | France-Alderney-Britain | PINT | 134 | 143 | 129 | 44 | 48 | 37 | 7 | 10 | 4 | -1259 | -1063 | -1365 | 31 | 82 | 194 | 162 | 238 | 84
167 | Viking DKW-GB
170 | Baltic States Synchronization with Continental Europe | PINT | 52 | 73 | 29 | 34 | 41 | 27 | 6 | 9 | 2 | -974 | -780 | -1168 | 24 | 63 | 150 | 140 | 216 | 42
172 | ElecLink | TOOT | 117 | 124 | 110 | 43 | 46 | 40 | 7 | 9 | 5 | -1223 | -1147 | -1308 | 31 | 80 | 188 | 154 | 209 | 114
173 | FR-BE: PSTs Aubange-Moulaine
174 | Greenconnector | PINT | 51 | 65 | 42 | -21 | -18 | -25 | 4 | 12 | 0 | 613 | 708 | 524 | -15 | -40 | -94 | 83 | 276 | -2
176 | Hansa PowerBridge I | PINT | 101 | 102 | 100 | 42 | 44 | 40 | 14 | 16 | 12 | -1194 | -1137 | -1250 | 30 | 78 | 184 | 312 | 363 | 262
179 | DKE - DE (Kontek2) | PINT | 23 | 28 | 15 | 12 | 16 | 8 | 2 | 2 | 0 | -341 | -227 | -457 | 9 | 22 | 53 | 39 | 59 | 7
183 | DKW-DE, Westcoast | TOOT | 18 | 21 | 11 | 15 | 20 | 8 | 3 | 3 | 2 | -415 | -234 | -558 | 10 | 27 | 64 | 59 | 75 | 36
186 | East of Austria | TOOT | 236 | 247 | 228 | 82 | 88 | 78 | 218 | 240 | 198 | -2352 | -2215 | -2511 | 59 | 153 | 362 | 4819 | 4989 | 4600 | 2000
187 | St. Peter (AT) - Pleinting (DE) | PINT | 75 | 79 | 70 | 41 | 45 | 33 | 41 | 43 | 39 | -1184 | -934 | -1286 | 30 | 77 | 182 | 908 | 1053 | 790
190 | NorthConnect | TOOT | 172 | 224 | 115 | 48 | 66 | 31 | 11 | 13 | 9 | -1374 | -887 | -1898 | 34 | 89 | 212 | 246 | 302 | 201
197 | N-S Finland P1 stage 2 | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
200 | CZ Northwest-South corridor | TOOT | 33 | 36 | 30 | 27 | 30 | 24 | 16 | 16 | 15 | -776 | -682 | -870 | 19 | 50 | 119 | 372 | 398 | 354
207 | Reinforcement Northwestern DE
208 | N-S Western DE_section North_1
210 | Wurmlach (AT) - Somplago (IT) interconnection | PINT | 9 | 10 | 6 | -7 | -3 | -15 | 2 | 4 | 1 | 208 | 440 | 82 | -5 | -14 | -32 | 39 | 96 | 11
219 | EuroAsia Interconnector | PINT | 103 | 104 | 102 | -102 | -94 | -109 | 13 | 16 | 9 | 2901 | 3102 | 2678 | -73 | -189 | -447 | 289 | 382 | 221
225 | 2nd interconnector Belgium - Germany | light PINT | 25 | 26 | 24 | 14 | 16 | 11 | 12 | 13 | 11 | -386 | -311 | -450 | 10 | 25 | 59 | 279 | 307 | 235
227 | Transbalkan Corridor | PINT | 4 | 12 | 1 | 1 | 2 | 0 | 1 | 2 | 0 | -24 | -10 | -49 | 1 | 2 | 4 | 19 | 42 | 0
228 | Muhlbach - Eichstetten | PINT | 38 | 38 | 37 | 17 | 17 | 16 | 11 | 11 | 10 | -479 | -468 | -490 | 12 | 31 | 74 | 244 | 265 | 225
229 | GerPol Power Bridge II | light PINT | 82 | 87 | 78 | 56 | 60 | 51 | 22 | 29 | 19 | -1599 | -1459 | -1708 | 40 | 104 | 246 | 512 | 667 | 429
230 | GerPol Power Bridge I | TOOT | 132 | 143 | 122 | 68 | 76 | 56 | 34 | 39 | 32 | -1952 | -1591 | -2160 | 49 | 127 | 301 | 789 | 910 | 719
231 | Beznau - Tiengen | PINT | 32 | 37 | 25 | 16 | 19 | 10 | 22 | 25 | 20 | -454 | -273 | -551 | 11 | 30 | 70 | 516 | 592 | 435
233 | Connection of Aragon Pumping hydro | PINT | 104 | 115 | 94 | 26 | 32 | 20 | 107 | 129 | 85 | -737 | -557 | -908 | 18 | 48 | 114 | 2427 | 2838 | 2052
234 | DKE - PL-1 | PINT | 59 | 64 | 52 | 38 | 41 | 33 | 10 | 11 | 10 | -1073 | -952 | -1171 | 27 | 70 | 165 | 231 | 268 | 212
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Grafenrheinfeld | PINT | 658 | 742 | 478 | 75 | 109 | 32 | 404 | 490 | 237 | -2678 | -1132 | -3893 | 67 | 174 | 412 | 8725 | 10686 | 5191
239 | Fenno-Skan 1 renewal | light PINT | 18 | 18 | 18 | 2 | 2 | 1 | 1 | 1 | 0 | -46 | -38 | -54 | 1 | 3 | 7 | 18 | 30 | 5
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines | PINT | 11 | 13 | 7 | -29 | -14 | -47 | 1 | 3 | 0 | 833 | 1348 | 408 | -21 | -54 | -128 | 25 | 69 | 0
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 13 | 17 | 9 | -24 | -16 | -29 | 4 | 11 | 0 | 678 | 843 | 452 | -17 | -44 | -104 | 86 | 236 | 0
244 | Vigy - Uchtelfangen area | PINT | 171 | 174 | 168 | 73 | 74 | 72 | 49 | 50 | 47 | -2092 | -2059 | -2124 | 52 | 136 | 322 | 1142 | 1215 | 1045
245 | Upgrade Meeden - Diele
247 | AQUIND Interconnector | PINT | 184 | 186 | 181 | 67 | 69 | 66 | 8 | 14 | 1 | -1928 | -1871 | -1968 | 48 | 125 | 297 | 201 | 343 | 103
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 12 | 14 | 9 | -7 | -3 | -16 | 1 | 5 | 0 | 195 | 445 | 92 | -5 | -13 | -30 | 23 | 107 | 0
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | light PINT | 15 | 15 | 15 | 6 | 6 | 6 | 9 | 9 | 9 | -175 | -175 | -175 | 4 | 11 | 27 | 209 | 209 | 209
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT - A2 | 52 | 55 | 50 | 30 | 33 | 28 | 1 | 4 | 0 | -848 | -789 | -944 | 21 | 55 | 131 | 30 | 93 | 6
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 161 | 197 | 150 | -27 | -25 | -34 | 23 | 27 | 19 | 963 | 1229 | 877 | -24 | -63 | -148 | 503 | 583 | 399
258 | Westcoast line | No assessment
259 | HU-RO | PINT | 18 | 21 | 12 | -27 | -25 | -29 | 4 | 6 | 1 | 771 | 829 | 712 | -19 | -50 | -119 | 95 | 137 | 15
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 74 | 80 | 65 | 19 | 22 | 16 | 52 | 53 | 49 | -554 | -446 | -622 | 14 | 36 | 85 | 1207 | 1230 | 1192
262 | Belgium-Netherlands: Zandvliet-Rilland | TOOT | 29 | 31 | 29 | 11 | 12 | 10 | 21 | 22 | 20 | -311 | -285 | -355 | 8 | 20 | 48 | 487 | 494 | 475
263 | Lake Constance East | light PINT | 70 | 79 | 61 | 35 | 41 | 27 | 35 | 41 | 27 | -989 | -764 | -1164 | 25 | 64 | 152 | 796 | 987 | 639
264 | Swiss Roof I | light PINT | 105 | 110 | 97 | 34 | 40 | 25 | 47 | 48 | 44 | -961 | -721 | -1155 | 24 | 62 | 148 | 1037 | 1101 | 965
265 | Tessin | light PINT
266 | Swiss Ellipse I | PINT | 55 | 64 | 48 | 23 | 25 | 20 | 28 | 30 | 26 | -646 | -566 | -725 | 16 | 42 | 100 | 632 | 727 | 567
267 | Hansa PowerBridge II | light PINT | 101 | 102 | 100 | 42 | 44 | 40 | 14 | 16 | 12 | -1194 | -1137 | -1250 | 30 | 78 | 184 | 312 | 363 | 262
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 93 | 114 | 68 | 16 | 20 | 9 | 121 | 144 | 86 | -454 | -271 | -566 | 11 | 30 | 70 | 2790 | 3292 | 1907
276 | FR-ES project -Navarra-Landes | PINT | 93 | 114 | 68 | 16 | 20 | 9 | 121 | 144 | 86 | -454 | -271 | -566 | 11 | 30 | 70 | 2790 | 3292 | 1907
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 87 | 90 | 83 | 32 | 34 | 30 | 15 | 15 | 14 | -904 | -854 | -968 | 23 | 59 | 139 | 347 | 378 | 331
283 | TuNur | PINT | 579 | 606 | 549 | 156 | 157 | 154 | 525 | 547 | 503 | -4448 | -4402 | -4492 | 111 | 289 | 685 | 11191 | 11226 | 11156 | 4000
284 | LEG1 | PINT | 142 | 142 | 142 | -132 | -129 | -134 | 12 | 15 | 8 | 3759 | 3838 | 3681 | -94 | -244 | -579 | 282 | 344 | 165 | 2000
285 | GridLink | PINT | 134 | 143 | 129 | 44 | 48 | 37 | 7 | 10 | 4 | -1259 | -1063 | -1365 | 31 | 82 | 194 | 162 | 238 | 84
286 | Greenlink | PINT | 66 | 68 | 64 | 10 | 11 | 9 | 53 | 55 | 48 | -288 | -249 | -321 | 7 | 19 | 44 | 1198 | 1245 | 1144
293 | Southern Aegean Interconnector | PINT | 53 | 56 | 48 | 28 | 29 | 27 | 50 | 55 | 46 | -810 | -777 | -843 | 20 | 53 | 125 | 1153 | 1237 | 1102 | 582
296 | Britib | PINT | 287 | 291 | 279 | 82 | 83 | 81 | 155 | 163 | 147 | -2334 | -2303 | -2376 | 58 | 152 | 359 | 3635 | 3927 | 3342
297 | BRABO II + III | PINT | 15 | 17 | 13 | 4 | 6 | 3 | 13 | 13 | 13 | -117 | -85 | -162 | 3 | 8 | 18 | 297 | 308 | 286
299 | SACOI3 | TOOT | 32 | 35 | 29 | 3 | 5 | 2 | 3 | 4 | 2 | -100 | -65 | -132 | 2 | 6 | 15 | 72 | 100 | 47
309 | NeuConnect | TOOT | 85 | 94 | 71 | 31 | 37 | 27 | 43 | 46 | 41 | -893 | -762 | -1069 | 22 | 58 | 138 | 972 | 1004 | 931
312 | St. Peter (AT) - Tauern (AT) | TOOT | 140 | 149 | 131 | 85 | 92 | 78 | 69 | 75 | 63 | -2423 | -2228 | -2617 | 61 | 157 | 373 | 1577 | 1767 | 1467
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 140 | 149 | 131 | 85 | 91 | 78 | 70 | 75 | 64 | -2420 | -2228 | -2604 | 61 | 157 | 373 | 1579 | 1767 | 1480
320 | Slovenia-Hungary/Croatia interconnection | TOOT | 1 | 2 | 0 | -2 | 0 | -3 | 0 | 1 | 0 | 47 | 80 | 13 | -1 | -3 | -7 | 10 | 27 | 0
322 | Wullenstetten - Border Area (DE-AT) | PINT | -16 | 4 | -23 | -2 | -2 | -2 | -11 | -8 | -13 | 76 | 87 | 55 | -2 | -5 | -12 | -225 | -160 | -281
323 | Dekani (SI) - Zaule (IT) interconnection | PINT | 6 | 13 | 1 | -8 | -5 | -10 | 2 | 4 | 0 | 235 | 278 | 143 | -6 | -15 | -36 | 37 | 99 | 4
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | PINT | 5 | 10 | 3 | -9 | -5 | -13 | 2 | 4 | 0 | 257 | 378 | 139 | -6 | -17 | -40 | 32 | 88 | 0
325 | Obersielach (AT) - Podlog (SI) | PINT | 11 | 13 | 8 | 13 | 17 | 8 | 3 | 5 | 1 | -385 | -217 | -476 | 10 | 25 | 59 | 57 | 119 | 17
328 | Interconnector DE-LUX | PINT | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 10 | -9 | 0 | 0 | 0 | 9 | 13 | 5
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 293 | 293 | 293 | 73 | 73 | 73 | 354 | 354 | 354 | -2076 | -2076 | -2076 | 52 | 135 | 320 | 7860 | 7860 | 7860
330 | 4th 400kV CZ-SK interconnector | light PINT | 7 | 13 | 3 | 1 | 1 | 1 | 4 | 9 | 1 | -36 | -33 | -40 | 1 | 2 | 6 | 92 | 194 | 16
333 | PST Foretaille | PINT - A1 | 123 | 126 | 120 | 74 | 78 | 69 | 1 | 1 | 0 | -2107 | -1963 | -2215 | 53 | 137 | 325 | 11 | 20 | 0
335 | Project 335 - North Sea Wind Power Hub | light PINT | 1623 | 1623 | 1623 | 568 | 582 | 555 | 1909 | 1926 | 1892 | -16238 | -15854 | -16622 | 406 | 1055 | 2501 | 42397 | 42669 | 42124
336 | Prati (IT) – Steinach (AT) | No assessment
338 | Adriatic HVDC link | PINT | 19 | 29 | 15 | -5 | 2 | -9 | 8 | 17 | 2 | 144 | 255 | -47 | -4 | -9 | -22 | 172 | 365 | 37
339 | Italian HVDC tri-terminal link | PINT | 18 | 25 | 14 | 2 | 5 | -6 | 12 | 19 | 9 | -64 | 159 | -146 | 2 | 4 | 10 | 267 | 420 | 191
340 | Avelgem-Center: new corridor (Boucle du Hainaut) | TOOT | 195 | 195 | 195 | 49 | 49 | 49 | 236 | 236 | 236 | -1384 | -1384 | -1384 | 35 | 90 | 213 | 5240 | 5240 | 5240
341 | North CSE Corridor | PINT | 6 | 10 | 4 | -1 | 0 | -2 | 4 | 7 | 2 | 24 | 71 | -10 | -1 | -2 | -4 | 81 | 153 | 33
342 | Central Balkan Corridor | PINT | 6 | 9 | 4 | 0 | 0 | -1 | 4 | 10 | 2 | 9 | 22 | -4 | 0 | -1 | -1 | 99 | 230 | 42
343 | CSE1 New | PINT | 13 | 18 | 6 | -32 | -21 | -41 | 2 | 4 | 0 | 902 | 1158 | 612 | -23 | -59 | -139 | 51 | 89 | 7
344 | Reinforcements Ring NL phase II | PINT
346 | ZuidWest380 NL Oost | PINT | 15 | 17 | 13 | 4 | 6 | 3 | 13 | 13 | 13 | -117 | -85 | -162 | 3 | 8 | 18 | 297 | 308 | 286
348 | NoordWest380 NL | PINT
349 | MaresConnect | PINT | 249 | 251 | 248 | 52 | 53 | 50 | 236 | 236 | 236 | -1474 | -1421 | -1527 | 37 | 96 | 227 | 5257 | 5257 | 5257 | 1800
350 | South Balkan Corridor
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 27 | 34 | 22 | -18 | -11 | -22 | 2 | 4 | 1 | 508 | 620 | 305 | -13 | -33 | -78 | 55 | 85 | 22
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 16 | 21 | 13 | -8 | -2 | -13 | 6 | 8 | 4 | 220 | 382 | 58 | -6 | -14 | -34 | 133 | 177 | 89
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 15 | 17 | 13 | 4 | 6 | 3 | 13 | 13 | 13 | -117 | -85 | -162 | 3 | 8 | 18 | 297 | 308 | 286
378 | Transformer Gatica | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
379 | Uprate Gatica lines | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 408 | 442 | 336 | 44 | 62 | 19 | 266 | 310 | 166 | -1577 | -668 | -2203 | 39 | 103 | 243 | 5744 | 6771 | 3630
1039 | SE North-south long-term reinforcements | light PINT | 8 | 13 | 3 | 3 | 6 | 1 | 9 | 14 | 3 | -91 | -24 | -158 | 2 | 6 | 14 | 186 | 295 | 78
1040 | LirIC | PINT | 86 | 88 | 83 | 12 | 14 | 10 | 67 | 70 | 61 | -344 | -278 | -398 | 9 | 22 | 53 | 1533 | 1600 | 1470
1041 | GREGY Interconnector | PINT | 136 | 151 | 121 | -430 | -427 | -434 | 11 | 15 | 7 | 12300 | 12409 | 12190 | -307 | -799 | -1894 | 234 | 311 | 156
1042 | Offshore wind integration | PINT | 91 | 93 | 88 | 27 | 32 | 21 | 123 | 130 | 118 | -764 | -596 | -903 | 19 | 50 | 118 | 2639 | 2646 | 2627 | 700
1043 | Wahle-Mecklar
1046 | N-S Finland P1 stage 3 | PINT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1047 | Emden-Eemshaven | light PINT | 10 | 12 | 9 | 11 | 15 | 9 | 1 | 3 | 0 | -313 | -254 | -418 | 8 | 20 | 48 | 27 | 60 | 6
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | light PINT | 101 | 116 | 86 | -326 | -310 | -343 | 18 | 24 | 13 | 9303 | 9814 | 8869 | -233 | -605 | -1433 | 412 | 578 | 269
1049 | Cronos Energy Ltd | PINT | 45 | 49 | 41 | 15 | 16 | 12 | 13 | 17 | 11 | -424 | -348 | -466 | 11 | 28 | 65 | 313 | 378 | 267
1050 | Tarchon Energy Ltd | PINT | 64 | 69 | 58 | 22 | 26 | 17 | 37 | 39 | 35 | -632 | -480 | -756 | 16 | 41 | 97 | 855 | 899 | 816
1051 | Aminth Energy Ltd | PINT | 56 | 59 | 52 | 13 | 16 | 11 | 36 | 38 | 35 | -380 | -324 | -469 | 9 | 25 | 58 | 843 | 848 | 835
1052 | Lienz (AT) - Obersielach (AT) | PINT | 13 | 17 | 10 | 14 | 18 | 8 | 3 | 5 | 2 | -398 | -217 | -503 | 10 | 26 | 61 | 71 | 119 | 41
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 31 | 33 | 29 | 18 | 20 | 16 | 18 | 19 | 16 | -521 | -458 | -566 | 13 | 34 | 80 | 400 | 454 | 350
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 223 | 224 | 223 | 6 | 8 | 5 | 3 | 3 | 2 | -178 | -144 | -225 | 4 | 12 | 27 | 62 | 73 | 47
1056 | Croatian south connection | light PINT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1057 | HVDC CentraLink | light PINT
1058 | HVDC Interconnector DE-CH | light PINT
1059 | Southern Italy | PINT | 4 | 13 | 1 | 1 | 2 | 1 | 3 | 5 | 2 | -34 | -19 | -55 | 1 | 2 | 5 | 61 | 106 | 40
1061 | Reactive compensation for project 197
1062 | Reactive compensation for project 1046
1063 | ZuidWest380 West
1066 | Bulgaria - Turkey | light PINT | 264 | 295 | 233 | -46 | -44 | -48 | 6 | 10 | 3 | 1308 | 1366 | 1249 | -33 | -85 | -201 | 147 | 232 | 63
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 135 | 156 | 118 | 0 | 2 | -1 | 10 | 11 | 6 | -12 | 32 | -56 | 0 | 1 | 2 | 221 | 276 | 138
1068 | LaSGo Link | light PINT | 38 | 58 | 1 | 14 | 21 | 1 | 14 | 24 | 1 | -387 | 0 | -613 | 10 | 25 | 60 | 320 | 585 | 0
1074 | Pannonian Corridor | light PINT | 14 | 21 | 9 | -18 | -14 | -21 | 2 | 4 | 0 | 500 | 609 | 392 | -13 | -33 | -77 | 51 | 92 | 1
1077 | Crete-North Greece-North Macedonia-Bulgaria Interconnector | light PINT | 21 | 33 | 1 | -13 | 1 | -24 | 7 | 10 | 1 | 387 | 698 | 0 | -10 | -25 | -60 | 148 | 251 | 0
1081 | LAG Interconnector (LAG) | light PINT | 174 | 320 | 2 | -303 | 2 | -470 | 6 | 16 | 0 | 8671 | 13429 | 0 | -217 | -564 | -1335 | 244 | 413 | 0
1082 | Sea-Socket | light PINT | 43 | 58 | 2 | 11 | 14 | 2 | 36 | 49 | 2 | -295 | 0 | -414 | 7 | 19 | 45 | 834 | 1147 | 0

## 2030DE
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_market_SEW |  |  | ΔRES |  |  | ΔRES_MW
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | low | mid | high | weighted avg | max | min | Explicit
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW
1 | RES in north of Portugal | TOOT | 35 | 37 | 32 | 10 | 11 | 8 | 60 | 93 | 24 | -186 | -143 | -209 | 1 | 9 | 25 | 1131 | 1659 | 573 | 1154
4 | Interconnection Portugal-Spain | TOOT | 60 | 72 | 50 | 16 | 19 | 10 | 64 | 81 | 53 | -295 | -191 | -358 | 2 | 14 | 40 | 1305 | 1532 | 1102
16 | Biscay Gulf | TOOT | 259 | 259 | 258 | 61 | 62 | 59 | 379 | 406 | 351 | -1144 | -1120 | -1174 | 8 | 54 | 156 | 7748 | 8530 | 7090
23 | FR-BE: Avelin/Mastaing-Avelgem-Horta HTLS | TOOT
26 | Reschenpass Interconnector Project | TOOT | 15 | 20 | 11 | 6 | 11 | 2 | 4 | 9 | 2 | -112 | -32 | -198 | 1 | 5 | 15 | 75 | 142 | 41
28 | Italy-Montenegro | PINT | 19 | 27 | 12 | 11 | 21 | 4 | 10 | 20 | 5 | -213 | -74 | -401 | 1 | 10 | 29 | 182 | 356 | 111
29 | Italy-Tunisia | PINT | 30 | 40 | 22 | -43 | -38 | -48 | 21 | 22 | 18 | 807 | 915 | 715 | -6 | -38 | -110 | 410 | 520 | 300
33 | Central Northern Italy | TOOT | 5 | 7 | 2 | 1 | 4 | -1 | 4 | 4 | 4 | -20 | 19 | -74 | 0 | 1 | 3 | 77 | 106 | 63
35 | CZ Southwest-east corridor | PINT | 22 | 23 | 21 | 5 | 11 | 1 | 10 | 14 | 7 | -95 | -22 | -216 | 1 | 4 | 13 | 195 | 256 | 126
36 | Kriegers Flak CGS
37 | Norway - Germany, NordLink | TOOT
39 | DKW-DE, step 3
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 12 | 13 | 11 | 13 | 13 | 12 | 2 | 3 | 2 | -241 | -227 | -252 | 2 | 11 | 33 | 44 | 47 | 40
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 33 | 41 | 29 | 18 | 26 | 12 | 13 | 16 | 10 | -339 | -226 | -481 | 2 | 16 | 46 | 239 | 270 | 187
48 | New SK-HU intercon. - phase 1 | TOOT | 16 | 21 | 12 | 16 | 19 | 14 | 2 | 4 | 0 | -299 | -264 | -356 | 2 | 14 | 41 | 52 | 92 | 5
62 | Estonia-Latvia 3rd IC | TOOT | 27 | 33 | 23 | -13 | -11 | -15 | 6 | 9 | 4 | 239 | 277 | 212 | -2 | -11 | -33 | 123 | 158 | 74
78 | South West Cluster | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
81 | North South Interconnector | TOOT | 33 | 44 | 11 | 15 | 22 | 9 | 29 | 50 | 11 | -276 | -176 | -415 | 2 | 13 | 37 | 560 | 894 | 205
82 | RIDP I | PINT | 21 | 27 | 17 | 10 | 13 | 6 | 26 | 46 | 12 | -181 | -112 | -248 | 1 | 9 | 25 | 489 | 798 | 301 | 300
85 | Integration of RES in Alentejo | TOOT | 10 | 14 | 4 | 1 | 4 | -3 | 23 | 30 | 15 | -15 | 48 | -72 | 0 | 1 | 2 | 449 | 517 | 376 | 706
92 | ALEGrO
94 | GerPol Improvements
103 | Reinforcements Ring NL phase I | TOOT | 3 | 5 | 0 | 4 | 5 | 4 | 1 | 6 | -2 | -83 | -70 | -89 | 1 | 4 | 11 | 27 | 108 | -37
107 | Celtic Interconnector | PINT | 161 | 166 | 154 | 53 | 55 | 50 | 98 | 102 | 95 | -998 | -940 | -1042 | 7 | 47 | 136 | 1786 | 1912 | 1660
110 | Norway-Great Britain, North Sea Link | TOOT
111 | 3rd AC Finland-Sweden north | TOOT | 113 | 119 | 106 | 6 | 6 | 6 | 1 | 2 | 1 | -115 | -110 | -119 | 1 | 5 | 16 | 22 | 35 | 9
120 | MOG II: connection of up to 2 GW additional offshore wind Belgium | TOOT | 386 | 397 | 375 | 122 | 127 | 119 | 385 | 443 | 326 | -2304 | -2248 | -2388 | 16 | 108 | 313 | 7814 | 7930 | 7699 | 2000
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 57 | 59 | 55 | 29 | 31 | 28 | 3 | 6 | -1 | -542 | -521 | -580 | 4 | 25 | 74 | 71 | 120 | -16
123 | LitPol Link Stage 2 | TOOT | 54 | 63 | 47 | 27 | 35 | 17 | 7 | 14 | 4 | -505 | -323 | -662 | 4 | 24 | 69 | 126 | 251 | 65
124 | NordBalt phase 2 | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 25 | 29 | 22 | 10 | 10 | 10 | -4 | 0 | -8 | -186 | -186 | -186 | 1 | 9 | 25 | -69 | 3 | -140
127 | Central Southern Italy | TOOT | 24 | 26 | 23 | 17 | 18 | 14 | 19 | 25 | 15 | -314 | -265 | -346 | 2 | 15 | 43 | 359 | 415 | 286
130 | HVDC SuedOstLink Wolmirstedt to area Isar | PINT | 272 | 323 | 192 | 20 | 24 | 15 | 159 | 175 | 115 | -732 | -533 | -873 | 5 | 34 | 100 | 2411 | 2727 | 1661
132 | HVDC Line A-North | TOOT | 469 | 516 | 351 | 169 | 291 | 44 | 327 | 357 | 269 | -6030 | -1557 | -10391 | 42 | 283 | 820 | 4938 | 5564 | 3870
138 | Black Sea Corridor | TOOT | 17 | 19 | 15 | 6 | 11 | 2 | 10 | 12 | 8 | -111 | -38 | -204 | 1 | 5 | 15 | 194 | 230 | 156
142 | CSE4 | TOOT | 40 | 46 | 35 | 5 | 13 | -1 | 14 | 18 | 11 | -92 | 13 | -237 | 1 | 4 | 13 | 269 | 315 | 211
144 | Mid Continental East corridor | TOOT | 26 | 30 | 19 | 10 | 11 | 8 | 7 | 13 | 1 | -188 | -144 | -215 | 1 | 9 | 26 | 150 | 295 | 22
150 | Italy-Slovenia | PINT | 21 | 29 | 15 | -2 | 5 | -7 | 2 | 3 | 2 | 38 | 125 | -101 | 0 | -2 | -5 | 43 | 51 | 36
153 | France-Alderney-Britain | PINT | 259 | 269 | 250 | 109 | 118 | 102 | 1 | 7 | -7 | -2064 | -1929 | -2225 | 14 | 97 | 281 | 37 | 180 | -113
167 | Viking DKW-GB
170 | Baltic States Synchronization with Continental Europe | PINT | 57 | 78 | 30 | 23 | 24 | 22 | 9 | 15 | 5 | -433 | -422 | -445 | 3 | 20 | 59 | 178 | 263 | 123
172 | ElecLink | TOOT | 216 | 232 | 201 | 94 | 98 | 88 | 6 | 8 | 4 | -1768 | -1653 | -1846 | 12 | 83 | 240 | 129 | 170 | 79
173 | FR-BE: PSTs Aubange-Moulaine
174 | Greenconnector | PINT | 34 | 45 | 27 | 5 | 7 | 1 | 5 | 15 | 0 | -92 | -15 | -139 | 1 | 4 | 13 | 91 | 273 | 8
176 | Hansa PowerBridge I | PINT | 70 | 70 | 69 | 28 | 32 | 21 | 14 | 20 | 6 | -530 | -394 | -607 | 4 | 25 | 72 | 254 | 356 | 138
179 | DKE - DE (Kontek2) | PINT | 14 | 16 | 12 | 8 | 10 | 6 | 1 | 2 | 0 | -145 | -122 | -183 | 1 | 7 | 20 | 23 | 42 | 2
183 | DKW-DE, Westcoast | TOOT | 13 | 15 | 10 | 10 | 12 | 8 | 6 | 12 | 2 | -196 | -156 | -222 | 1 | 9 | 27 | 108 | 205 | 49
186 | East of Austria | TOOT | 273 | 293 | 253 | 105 | 111 | 99 | 287 | 290 | 285 | -1980 | -1862 | -2091 | 14 | 93 | 269 | 4846 | 4884 | 4809 | 2000
187 | St. Peter (AT) - Pleinting (DE) | PINT | 71 | 78 | 63 | 31 | 39 | 25 | 32 | 36 | 26 | -582 | -481 | -739 | 4 | 27 | 79 | 589 | 627 | 515
190 | NorthConnect | TOOT | 141 | 147 | 137 | 47 | 65 | 32 | 11 | 12 | 7 | -888 | -608 | -1220 | 6 | 42 | 121 | 192 | 233 | 128
197 | N-S Finland P1 stage 2 | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
200 | CZ Northwest-South corridor | TOOT | 27 | 29 | 25 | 2 | 6 | -3 | 9 | 13 | 3 | -36 | 53 | -111 | 0 | 2 | 5 | 173 | 231 | 61
207 | Reinforcement Northwestern DE
208 | N-S Western DE_section North_1
210 | Wurmlach (AT) - Somplago (IT) interconnection | PINT | 10 | 17 | 7 | 4 | 7 | 1 | 1 | 3 | 0 | -77 | -28 | -138 | 1 | 4 | 10 | 23 | 59 | -8
219 | EuroAsia Interconnector | PINT | 109 | 113 | 104 | -64 | -63 | -65 | 25 | 28 | 22 | 1207 | 1224 | 1191 | -8 | -57 | -164 | 504 | 681 | 409
225 | 2nd interconnector Belgium - Germany | light PINT | 27 | 29 | 25 | 21 | 23 | 20 | 17 | 20 | 14 | -404 | -379 | -428 | 3 | 19 | 55 | 345 | 351 | 334
227 | Transbalkan Corridor | PINT | 9 | 16 | 0 | 3 | 7 | 0 | 5 | 9 | 0 | -52 | -3 | -125 | 0 | 2 | 7 | 86 | 178 | 6
228 | Muhlbach - Eichstetten | PINT | 62 | 65 | 60 | 32 | 34 | 30 | 8 | 11 | 6 | -609 | -568 | -639 | 4 | 29 | 83 | 167 | 195 | 120
229 | GerPol Power Bridge II | light PINT | 108 | 112 | 101 | 96 | 106 | 84 | 30 | 33 | 25 | -1818 | -1592 | -1994 | 13 | 85 | 247 | 578 | 625 | 529
230 | GerPol Power Bridge I | TOOT | 176 | 182 | 171 | 149 | 170 | 131 | 42 | 48 | 32 | -2818 | -2478 | -3205 | 20 | 132 | 383 | 797 | 902 | 744
231 | Beznau - Tiengen | PINT | 25 | 29 | 20 | 11 | 13 | 8 | 17 | 19 | 16 | -210 | -145 | -245 | 1 | 10 | 29 | 345 | 401 | 305
233 | Connection of Aragon Pumping hydro | PINT | 193 | 235 | 147 | 61 | 70 | 50 | 278 | 313 | 243 | -1144 | -937 | -1328 | 8 | 54 | 156 | 5168 | 5481 | 4855
234 | DKE - PL-1 | PINT | 56 | 61 | 52 | 42 | 45 | 35 | 11 | 12 | 9 | -787 | -655 | -854 | 6 | 37 | 107 | 213 | 272 | 165
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Grafenrheinfeld | PINT | 1007 | 1167 | 677 | 112 | 143 | 73 | 693 | 824 | 477 | -4000 | -2613 | -5123 | 28 | 188 | 544 | 10515 | 12826 | 6867
239 | Fenno-Skan 1 renewal | light PINT | 73 | 79 | 66 | 0 | 6 | -5 | -2 | 0 | -3 | -6 | 98 | -111 | 0 | 0 | 1 | -27 | 0 | -55
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines | PINT | 15 | 23 | 9 | -1 | 3 | -4 | 5 | 9 | 1 | 10 | 66 | -53 | 0 | 0 | -1 | 96 | 161 | 23
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 15 | 20 | 11 | -3 | 0 | -5 | 6 | 14 | 1 | 64 | 94 | -8 | 0 | -3 | -9 | 119 | 266 | 28
244 | Vigy - Uchtelfangen area | PINT | 292 | 298 | 283 | 150 | 159 | 143 | 41 | 51 | 36 | -2826 | -2697 | -2998 | 20 | 133 | 384 | 823 | 890 | 692
245 | Upgrade Meeden - Diele
247 | AQUIND Interconnector | PINT | 367 | 372 | 358 | 148 | 155 | 142 | -1 | 4 | -7 | -2789 | -2674 | -2923 | 20 | 131 | 379 | -15 | 77 | -124
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 9 | 12 | 7 | 3 | 8 | 0 | 2 | 9 | 0 | -56 | -2 | -154 | 0 | 3 | 8 | 37 | 166 | 3
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | light PINT | 10 | 10 | 10 | 6 | 6 | 6 | 8 | 8 | 8 | -121 | -121 | -121 | 1 | 6 | 16 | 152 | 152 | 152
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT - A2 | 79 | 81 | 76 | 41 | 45 | 37 | 0 | 1 | 0 | -773 | -699 | -856 | 5 | 36 | 105 | 8 | 23 | 1
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 179 | 199 | 153 | -20 | -18 | -22 | 27 | 29 | 24 | 729 | 802 | 660 | -5 | -34 | -99 | 405 | 446 | 348
258 | Westcoast line | No assessment
259 | HU-RO | PINT | 21 | 25 | 15 | 0 | 4 | -2 | 4 | 7 | 1 | -9 | 31 | -72 | 0 | 0 | 1 | 84 | 179 | 21
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 105 | 109 | 99 | 66 | 71 | 62 | 40 | 45 | 34 | -1237 | -1169 | -1347 | 9 | 58 | 168 | 803 | 852 | 711
262 | Belgium-Netherlands: Zandvliet-Rilland | TOOT | 42 | 44 | 40 | 29 | 30 | 27 | 23 | 28 | 18 | -543 | -503 | -571 | 4 | 26 | 74 | 462 | 487 | 443
263 | Lake Constance East | light PINT | 79 | 86 | 70 | 40 | 48 | 31 | 32 | 37 | 26 | -757 | -582 | -904 | 5 | 36 | 103 | 580 | 698 | 494
264 | Swiss Roof I | light PINT | 107 | 113 | 99 | 51 | 56 | 47 | 42 | 50 | 35 | -959 | -894 | -1055 | 7 | 45 | 130 | 745 | 861 | 615
265 | Tessin | light PINT
266 | Swiss Ellipse I | PINT | 60 | 70 | 49 | 29 | 37 | 24 | 24 | 25 | 21 | -551 | -452 | -695 | 4 | 26 | 75 | 462 | 526 | 425
267 | Hansa PowerBridge II | light PINT | 70 | 70 | 69 | 28 | 32 | 21 | 14 | 20 | 6 | -530 | -394 | -607 | 4 | 25 | 72 | 254 | 356 | 138
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 120 | 122 | 116 | 30 | 39 | 23 | 173 | 196 | 151 | -559 | -430 | -739 | 4 | 26 | 76 | 3507 | 4191 | 2656
276 | FR-ES project -Navarra-Landes | PINT | 120 | 122 | 116 | 30 | 39 | 23 | 173 | 196 | 151 | -559 | -430 | -739 | 4 | 26 | 76 | 3507 | 4191 | 2656
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 160 | 163 | 156 | 74 | 78 | 65 | 3 | 5 | 1 | -1392 | -1231 | -1477 | 10 | 65 | 189 | 64 | 133 | 23
283 | TuNur | PINT | 617 | 654 | 575 | 198 | 214 | 181 | 535 | 651 | 420 | -3734 | -3418 | -4039 | 26 | 175 | 508 | 10484 | 10773 | 10195 | 4000
284 | LEG1 | PINT | 133 | 153 | 109 | -107 | -106 | -108 | 19 | 20 | 18 | 2015 | 2031 | 1999 | -14 | -95 | -274 | 332 | 336 | 327 | 2000
285 | GridLink | PINT | 259 | 269 | 250 | 109 | 118 | 102 | 1 | 7 | -7 | -2064 | -1929 | -2225 | 14 | 97 | 281 | 37 | 180 | -113
286 | Greenlink | PINT | 76 | 79 | 73 | 22 | 25 | 19 | 73 | 77 | 70 | -409 | -354 | -473 | 3 | 19 | 56 | 1301 | 1348 | 1223
293 | Southern Aegean Interconnector | PINT | 62 | 68 | 58 | 26 | 33 | 21 | 43 | 49 | 36 | -481 | -397 | -616 | 3 | 23 | 65 | 866 | 1045 | 632
296 | Britib | PINT | 456 | 463 | 453 | 163 | 163 | 162 | 210 | 235 | 186 | -3069 | -3055 | -3084 | 21 | 144 | 417 | 4247 | 5069 | 3268
297 | BRABO II + III | PINT | 21 | 22 | 20 | 16 | 19 | 13 | 12 | 17 | 7 | -298 | -240 | -363 | 2 | 14 | 40 | 254 | 319 | 125
299 | SACOI3 | TOOT | 38 | 42 | 33 | 9 | 11 | 6 | 7 | 9 | 6 | -173 | -104 | -215 | 1 | 8 | 23 | 147 | 169 | 104
309 | NeuConnect | TOOT | 106 | 111 | 100 | 66 | 67 | 64 | 45 | 48 | 42 | -1238 | -1210 | -1269 | 9 | 58 | 168 | 787 | 827 | 739
312 | St. Peter (AT) - Tauern (AT) | TOOT | 133 | 143 | 124 | 59 | 66 | 50 | 56 | 61 | 46 | -1111 | -952 | -1250 | 8 | 52 | 151 | 970 | 1065 | 853
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 133 | 143 | 124 | 59 | 66 | 50 | 56 | 61 | 46 | -1111 | -952 | -1250 | 8 | 52 | 151 | 970 | 1065 | 853
320 | Slovenia-Hungary/Croatia interconnection | TOOT | 4 | 6 | 2 | 0 | 2 | -3 | 1 | 1 | 0 | -4 | 64 | -35 | 0 | 0 | 1 | 12 | 20 | 0
322 | Wullenstetten - Border Area (DE-AT) | PINT | -7 | 20 | -22 | 0 | 1 | -1 | 365 | 504 | -9 | 2 | 28 | -18 | 0 | 0 | 0 | -68 | -50 | -126
323 | Dekani (SI) - Zaule (IT) interconnection | PINT | 5 | 11 | 1 | 1 | 4 | -3 | 2 | 6 | -1 | -19 | 54 | -81 | 0 | 1 | 3 | 31 | 115 | -12
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | PINT | 5 | 11 | 3 | 2 | 7 | -2 | 0 | 5 | -7 | -34 | 40 | -130 | 0 | 2 | 5 | 3 | 95 | -128
325 | Obersielach (AT) - Podlog (SI) | PINT | 11 | 13 | 9 | 7 | 16 | 4 | 4 | 7 | 1 | -136 | -74 | -310 | 1 | 6 | 18 | 65 | 133 | 16
328 | Interconnector DE-LUX | PINT | 1 | 1 | 0 | 0 | 1 | -1 | 1 | 1 | 0 | 1 | 15 | -10 | 0 | 0 | 0 | 12 | 29 | 4
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 386 | 386 | 386 | 122 | 122 | 122 | 385 | 385 | 385 | -2304 | -2304 | -2304 | 16 | 108 | 313 | 7814 | 7814 | 7814
330 | 4th 400kV CZ-SK interconnector | light PINT | 9 | 11 | 7 | 10 | 16 | 6 | 4 | 6 | 3 | -198 | -118 | -302 | 1 | 9 | 27 | 84 | 110 | 65
333 | PST Foretaille | PINT - A1 | 183 | 192 | 176 | 99 | 110 | 86 | 1 | 2 | 0 | -1861 | -1619 | -2082 | 13 | 87 | 253 | 19 | 43 | 0
335 | Project 335 - North Sea Wind Power Hub | light PINT | 2316 | 2318 | 2313 | 845 | 850 | 840 | 2601 | 2601 | 2601 | -15942 | -15845 | -16039 | 112 | 749 | 2168 | 45179 | 45179 | 45179
336 | Prati (IT) – Steinach (AT) | No assessment
338 | Adriatic HVDC link | PINT | 34 | 44 | 25 | 11 | 14 | 7 | 13 | 19 | 4 | -215 | -132 | -271 | 2 | 10 | 29 | 261 | 440 | 61
339 | Italian HVDC tri-terminal link | PINT | 17 | 27 | 12 | 4 | 6 | 2 | 9 | 15 | 3 | -67 | -44 | -116 | 0 | 3 | 9 | 166 | 271 | 58
340 | Avelgem-Center: new corridor (Boucle du Hainaut) | TOOT | 257 | 257 | 257 | 81 | 81 | 81 | 257 | 257 | 257 | -1536 | -1536 | -1536 | 11 | 72 | 209 | 5209 | 5209 | 5209
341 | North CSE Corridor | PINT | 11 | 20 | 8 | 7 | 13 | 4 | 4 | 6 | 3 | -128 | -71 | -246 | 1 | 6 | 17 | 85 | 115 | 48
342 | Central Balkan Corridor | PINT | 14 | 15 | 12 | 10 | 13 | 7 | 7 | 8 | 5 | -196 | -131 | -253 | 1 | 9 | 27 | 128 | 152 | 93
343 | CSE1 New | PINT | 14 | 18 | 9 | -2 | 8 | -9 | 3 | 8 | -1 | 30 | 163 | -144 | 0 | -1 | -4 | 69 | 143 | -12
344 | Reinforcements Ring NL phase II | PINT
346 | ZuidWest380 NL Oost | PINT | 21 | 22 | 20 | 16 | 19 | 13 | 12 | 17 | 7 | -298 | -240 | -363 | 2 | 14 | 40 | 254 | 319 | 125
348 | NoordWest380 NL | PINT
349 | MaresConnect | PINT | 283 | 289 | 277 | 87 | 91 | 83 | 204 | 204 | 204 | -1635 | -1557 | -1712 | 11 | 77 | 222 | 4947 | 4947 | 4947 | 1800
350 | South Balkan Corridor
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 24 | 28 | 17 | 9 | 12 | 3 | 2 | 5 | 0 | -161 | -51 | -225 | 1 | 8 | 22 | 44 | 117 | 0
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 11 | 16 | 5 | 6 | 15 | 1 | 5 | 6 | 4 | -104 | -17 | -274 | 1 | 5 | 14 | 101 | 113 | 87
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 21 | 22 | 20 | 16 | 19 | 13 | 12 | 17 | 7 | -298 | -240 | -363 | 2 | 14 | 40 | 254 | 319 | 125
378 | Transformer Gatica | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
379 | Uprate Gatica lines | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 613 | 700 | 396 | 68 | 83 | 43 | 66 | 290 | -3 | -2417 | -1536 | -2973 | 17 | 114 | 329 | 6602 | 7852 | 4171
1039 | SE North-south long-term reinforcements | light PINT | 17 | 18 | 17 | 10 | 14 | 8 | 33 | 36 | 29 | -193 | -152 | -262 | 1 | 9 | 26 | 661 | 726 | 597
1040 | LirIC | PINT | 97 | 101 | 94 | 27 | 30 | 24 | 93 | 94 | 91 | -501 | -449 | -575 | 4 | 24 | 68 | 1680 | 1760 | 1600
1041 | GREGY Interconnector | PINT | 128 | 128 | 128 | -375 | -282 | -468 | 41 | 45 | 37 | 7074 | 8821 | 5327 | -50 | -332 | -962 | 704 | 739 | 670
1042 | Offshore wind integration | PINT | 142 | 160 | 129 | 54 | 58 | 46 | 139 | 161 | 103 | -1018 | -868 | -1102 | 7 | 48 | 138 | 2615 | 2672 | 2509 | 700
1043 | Wahle-Mecklar
1046 | N-S Finland P1 stage 3 | PINT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1047 | Emden-Eemshaven | light PINT | 5 | 5 | 4 | 5 | 7 | 4 | 1 | 2 | -1 | -102 | -81 | -131 | 1 | 5 | 14 | 18 | 38 | -15
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | light PINT | 105 | 116 | 95 | -264 | -188 | -344 | 35 | 37 | 34 | 4989 | 6485 | 3555 | -35 | -234 | -678 | 613 | 616 | 609
1049 | Cronos Energy Ltd | PINT | 57 | 59 | 55 | 29 | 31 | 28 | 3 | 6 | -1 | -542 | -521 | -580 | 4 | 25 | 74 | 71 | 120 | -16
1050 | Tarchon Energy Ltd | PINT | 86 | 90 | 83 | 53 | 60 | 43 | 34 | 42 | 27 | -993 | -809 | -1141 | 7 | 47 | 135 | 656 | 729 | 539
1051 | Aminth Energy Ltd | PINT | 77 | 79 | 74 | 43 | 51 | 38 | 30 | 33 | 26 | -813 | -721 | -971 | 6 | 38 | 111 | 609 | 638 | 581
1052 | Lienz (AT) - Obersielach (AT) | PINT | 12 | 15 | 10 | 9 | 16 | 4 | 3 | 7 | -2 | -163 | -74 | -310 | 1 | 8 | 22 | 50 | 133 | -36
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 32 | 40 | 29 | 17 | 21 | 12 | 14 | 16 | 11 | -313 | -229 | -393 | 2 | 15 | 43 | 258 | 278 | 223
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 289 | 290 | 288 | 25 | 26 | 23 | 4 | 6 | 2 | -468 | -435 | -500 | 3 | 22 | 64 | 81 | 112 | 48
1056 | Croatian south connection | light PINT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1057 | HVDC CentraLink | light PINT
1058 | HVDC Interconnector DE-CH | light PINT
1059 | Southern Italy | PINT | 4 | 9 | 1 | 4 | 8 | 1 | 2 | 3 | 0 | -73 | -18 | -148 | 1 | 3 | 10 | 31 | 50 | -4
1061 | Reactive compensation for project 197
1062 | Reactive compensation for project 1046
1063 | ZuidWest380 West
1066 | Bulgaria - Turkey | light PINT | 143 | 209 | 77 | 54 | 84 | 24 | 22 | 30 | 14 | -1023 | -452 | -1594 | 7 | 48 | 139 | 493 | 720 | 266
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 51 | 102 | 16 | 25 | 48 | 9 | 22 | 28 | 16 | -471 | -167 | -912 | 3 | 22 | 64 | 447 | 537 | 297
1068 | LaSGo Link | light PINT | 40 | 77 | 1 | 17 | 25 | 1 | 12 | 19 | 1 | -306 | 0 | -472 | 2 | 14 | 42 | 259 | 467 | 0
1074 | Pannonian Corridor | light PINT | 16 | 23 | 10 | -2 | -1 | -4 | 5 | 8 | 1 | 39 | 72 | 20 | 0 | -2 | -5 | 100 | 149 | 13
1077 | Crete-North Greece-North Macedonia-Bulgaria Interconnector | light PINT | 10 | 23 | 1 | 1 | 2 | 1 | 5 | 9 | 1 | -19 | 0 | -39 | 0 | 1 | 3 | 88 | 177 | 0
1081 | LAG Interconnector (LAG) | light PINT | 156 | 295 | 2 | -275 | 2 | -444 | 16 | 45 | 0 | 5194 | 8368 | 0 | -36 | -244 | -706 | 520 | 810 | 0
1082 | Sea-Socket | light PINT | 44 | 59 | 2 | 15 | 21 | 2 | 36 | 53 | 2 | -273 | 0 | -395 | 2 | 13 | 37 | 715 | 974 | 0 | 700

## 2030CT
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_market_SEW |  |  | ΔRES |  |  | ΔRES_MW
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | low | mid | high | weighted avg | max | min | Explicit
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW
1 | RES in north of Portugal | TOOT | 37 | 41 | 33 | 7 | 8 | 6 | 46 | 51 | 40 | -255 | -216 | -290 | 8 | 18 | 41 | 851 | 965 | 736 | 1154
4 | Interconnection Portugal-Spain | TOOT | 20 | 23 | 15 | 5 | 9 | 3 | 8 | 10 | 4 | -191 | -96 | -307 | 6 | 14 | 31 | 146 | 202 | 82
16 | Biscay Gulf | TOOT | 134 | 144 | 127 | 19 | 22 | 17 | 76 | 88 | 59 | -692 | -597 | -788 | 22 | 50 | 111 | 1437 | 1661 | 1069
23 | FR-BE: Avelin/Mastaing-Avelgem-Horta HTLS | TOOT
26 | Reschenpass Interconnector Project | TOOT | 8 | 15 | 4 | -2 | 0 | -6 | 1 | 3 | 0 | 79 | 200 | -6 | -3 | -6 | -13 | 16 | 66 | 0
28 | Italy-Montenegro | PINT | 6 | 10 | 3 | -2 | 1 | -5 | 1 | 3 | 0 | 76 | 183 | -32 | -2 | -6 | -12 | 18 | 64 | 0
29 | Italy-Tunisia | PINT | 7 | 9 | 6 | -31 | -27 | -34 | 0 | 0 | 0 | 1090 | 1215 | 981 | -35 | -79 | -176 | 3 | 7 | 0
33 | Central Northern Italy | TOOT | 2 | 5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | -10 | 0 | -20 | 0 | 1 | 2 | 0 | 1 | 0
35 | CZ Southwest-east corridor | PINT | 13 | 16 | 11 | 8 | 13 | 5 | 9 | 13 | 7 | -295 | -172 | -473 | 9 | 21 | 48 | 172 | 258 | 122
36 | Kriegers Flak CGS
37 | Norway - Germany, NordLink | TOOT
39 | DKW-DE, step 3
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 2 | 3 | 1 | 2 | 2 | 1 | 1 | 1 | 0 | -55 | -29 | -75 | 2 | 4 | 9 | 12 | 15 | 7
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 15 | 17 | 12 | 5 | 11 | 2 | 10 | 13 | 8 | -182 | -55 | -395 | 6 | 13 | 29 | 180 | 264 | 144
48 | New SK-HU intercon. - phase 1 | TOOT | 7 | 13 | 4 | -5 | -2 | -9 | 0 | 1 | 0 | 192 | 334 | 82 | -6 | -14 | -31 | 5 | 16 | 0
62 | Estonia-Latvia 3rd IC | TOOT | 6 | 12 | 3 | 3 | 3 | 2 | 0 | 0 | 0 | -97 | -82 | -107 | 3 | 7 | 16 | 1 | 3 | 0
78 | South West Cluster | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
81 | North South Interconnector | TOOT | 17 | 22 | 9 | 3 | 6 | -4 | 9 | 16 | 2 | -96 | 125 | -203 | 3 | 7 | 15 | 177 | 293 | 31
82 | RIDP I | PINT | 25 | 35 | 20 | 5 | 6 | 3 | 26 | 33 | 22 | -163 | -104 | -220 | 5 | 12 | 26 | 482 | 564 | 425 | 300
85 | Integration of RES in Alentejo | TOOT | 32 | 34 | 31 | 6 | 7 | 5 | 39 | 41 | 37 | -214 | -196 | -244 | 7 | 15 | 34 | 739 | 749 | 731 | 447
92 | ALEGrO
94 | GerPol Improvements
103 | Reinforcements Ring NL phase I | TOOT | 3 | 8 | 0 | 0 | 1 | -3 | 1 | 2 | 0 | 16 | 114 | -19 | -1 | -1 | -3 | 16 | 34 | 5
107 | Celtic Interconnector | PINT | 63 | 65 | 62 | 11 | 12 | 10 | 41 | 44 | 40 | -395 | -358 | -432 | 13 | 28 | 64 | 782 | 836 | 723
110 | Norway-Great Britain, North Sea Link | TOOT
111 | 3rd AC Finland-Sweden north | TOOT | 12 | 22 | 6 | 2 | 3 | 1 | 3 | 9 | 0 | -79 | -30 | -120 | 3 | 6 | 13 | 60 | 173 | 1
120 | MOG II: connection of up to 2 GW additional offshore wind Belgium | TOOT | 363 | 366 | 360 | 77 | 78 | 77 | 399 | 413 | 385 | -2759 | -2748 | -2769 | 88 | 199 | 444 | 7546 | 7552 | 7541 | 2000
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 16 | 17 | 14 | 4 | 5 | 2 | 0 | 1 | 0 | -127 | -56 | -168 | 4 | 9 | 20 | 8 | 17 | 3
123 | LitPol Link Stage 2 | TOOT | 14 | 19 | 10 | 6 | 9 | 2 | 1 | 2 | 0 | -207 | -75 | -314 | 7 | 15 | 33 | 13 | 42 | 0
124 | NordBalt phase 2 | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | SE North-south short-term reinforcements | PINT | 6 | 11 | 4 | 1 | 1 | 0 | 3 | 9 | 0 | -19 | 3 | -38 | 1 | 1 | 3 | 60 | 175 | 0
127 | Central Southern Italy | TOOT | 6 | 10 | 3 | 2 | 3 | 0 | 0 | 1 | 0 | -57 | -16 | -101 | 2 | 4 | 9 | 3 | 12 | 0
130 | HVDC SuedOstLink Wolmirstedt to area Isar | PINT | 156 | 164 | 141 | -1 | 2 | -8 | 48 | 56 | 38 | 38 | 280 | -60 | -1 | -3 | -6 | 1013 | 1188 | 780
132 | HVDC Line A-North | TOOT | 226 | 256 | 175 | 9 | 14 | 4 | 103 | 126 | 72 | -318 | -142 | -493 | 10 | 23 | 51 | 2164 | 2677 | 1474
138 | Black Sea Corridor | TOOT | 5 | 12 | 3 | -1 | -1 | -2 | 0 | 0 | 0 | 50 | 70 | 26 | -2 | -4 | -8 | 3 | 7 | 0
142 | CSE4 | TOOT | 11 | 16 | 7 | -7 | -4 | -8 | 0 | 1 | 0 | 232 | 284 | 153 | -7 | -17 | -37 | 4 | 14 | 0
144 | Mid Continental East corridor | TOOT | 9 | 12 | 7 | -4 | -2 | -9 | 2 | 5 | 0 | 143 | 309 | 68 | -5 | -10 | -23 | 31 | 105 | 2
150 | Italy-Slovenia | PINT | 8 | 13 | 3 | -4 | 2 | -12 | 0 | 0 | 0 | 145 | 426 | -66 | -5 | -10 | -23 | 1 | 2 | 0
153 | France-Alderney-Britain | PINT | 47 | 54 | 42 | 13 | 17 | 9 | 1 | 1 | 0 | -465 | -315 | -607 | 15 | 33 | 75 | 12 | 28 | 2
167 | Viking DKW-GB
170 | Baltic States Synchronization with Continental Europe | PINT | 4 | 4 | 4 | 3 | 6 | 1 | 2 | 7 | 0 | -112 | -25 | -229 | 4 | 8 | 18 | 46 | 137 | 0
172 | ElecLink | TOOT | 47 | 49 | 45 | 13 | 16 | 11 | 1 | 1 | 0 | -478 | -392 | -565 | 15 | 34 | 77 | 13 | 24 | 3
173 | FR-BE: PSTs Aubange-Moulaine
174 | Greenconnector | PINT | 9 | 17 | 4 | -4 | 0 | -9 | 3 | 10 | 0 | 138 | 311 | 8 | -4 | -10 | -22 | 53 | 203 | 0
176 | Hansa PowerBridge I | PINT | 25 | 27 | 22 | 4 | 5 | 3 | 8 | 11 | 4 | -143 | -106 | -180 | 5 | 10 | 23 | 150 | 197 | 80
179 | DKE - DE (Kontek2) | PINT | 6 | 7 | 4 | 0 | 1 | -1 | 0 | 1 | 0 | 5 | 44 | -25 | 0 | 0 | -1 | 5 | 11 | 0
183 | DKW-DE, Westcoast | TOOT | 4 | 5 | 3 | 1 | 1 | 1 | 1 | 2 | 1 | -35 | -24 | -49 | 1 | 2 | 6 | 21 | 27 | 15
186 | East of Austria | TOOT | 221 | 222 | 218 | 49 | 55 | 46 | 231 | 234 | 228 | -1764 | -1641 | -1978 | 56 | 127 | 284 | 4161 | 4215 | 4061 | 2000
187 | St. Peter (AT) - Pleinting (DE) | PINT | 34 | 39 | 32 | 11 | 16 | 5 | 22 | 23 | 20 | -382 | -187 | -555 | 12 | 28 | 62 | 397 | 446 | 359
190 | NorthConnect | TOOT | 52 | 59 | 47 | 13 | 16 | 11 | 3 | 8 | 0 | -471 | -404 | -575 | 15 | 34 | 76 | 50 | 163 | 6
197 | N-S Finland P1 stage 2 | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
200 | CZ Northwest-South corridor | TOOT | 19 | 27 | 12 | 12 | 17 | 6 | 8 | 9 | 7 | -445 | -203 | -622 | 14 | 32 | 72 | 157 | 176 | 147
207 | Reinforcement Northwestern DE
208 | N-S Western DE_section North_1
210 | Wurmlach (AT) - Somplago (IT) interconnection | PINT | 3 | 4 | 1 | 0 | 4 | -3 | 1 | 6 | 0 | -6 | 109 | -158 | 0 | 0 | 1 | 26 | 110 | 1
219 | EuroAsia Interconnector | PINT | 88 | 89 | 87 | -5 | -5 | -6 | 0 | 1 | 0 | 189 | 209 | 169 | -6 | -14 | -30 | 6 | 16 | 0
225 | 2nd interconnector Belgium - Germany | light PINT | 11 | 12 | 10 | 2 | 4 | 0 | 15 | 16 | 15 | -81 | -14 | -147 | 3 | 6 | 13 | 288 | 306 | 270
227 | Transbalkan Corridor | PINT | 1 | 1 | 0 | 1 | 5 | 0 | 1 | 5 | 0 | -47 | 0 | -175 | 2 | 3 | 8 | 28 | 108 | 0
228 | Muhlbach - Eichstetten | PINT | 13 | 15 | 11 | 4 | 6 | 2 | 5 | 5 | 5 | -154 | -83 | -204 | 5 | 11 | 25 | 92 | 100 | 87
229 | GerPol Power Bridge II | light PINT | 44 | 48 | 40 | 28 | 36 | 19 | 21 | 23 | 18 | -987 | -673 | -1273 | 32 | 71 | 159 | 381 | 403 | 337
230 | GerPol Power Bridge I | TOOT | 82 | 103 | 68 | 58 | 62 | 54 | 25 | 27 | 23 | -2060 | -1931 | -2232 | 66 | 148 | 332 | 474 | 528 | 419
231 | Beznau - Tiengen | PINT | 19 | 27 | 15 | 5 | 10 | 1 | 12 | 18 | 9 | -195 | -23 | -358 | 6 | 14 | 31 | 223 | 355 | 168
233 | Connection of Aragon Pumping hydro | PINT | 63 | 81 | 43 | 12 | 16 | 7 | 47 | 63 | 31 | -413 | -244 | -555 | 13 | 30 | 66 | 900 | 1171 | 607
234 | DKE - PL-1 | PINT | 14 | 19 | 12 | 10 | 13 | 5 | 6 | 6 | 5 | -344 | -195 | -474 | 11 | 25 | 55 | 102 | 108 | 92
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Grafenrheinfeld | PINT | 554 | 679 | 357 | 5 | 13 | -8 | 198 | 258 | 106 | -165 | 287 | -462 | 5 | 12 | 27 | 4159 | 5498 | 2173
239 | Fenno-Skan 1 renewal | light PINT | 6 | 9 | 4 | 0 | 1 | 0 | 2 | 5 | 0 | -15 | 15 | -42 | 0 | 1 | 2 | 35 | 105 | 0
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines | PINT | 4 | 7 | 1 | 1 | 3 | -3 | 1 | 2 | 0 | -18 | 110 | -109 | 1 | 1 | 3 | 15 | 40 | 0
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 8 | 11 | 4 | 0 | 4 | -4 | 0 | 1 | 0 | 2 | 125 | -130 | 0 | 0 | 0 | 8 | 28 | 1
244 | Vigy - Uchtelfangen area | PINT | 59 | 67 | 51 | 20 | 25 | 12 | 23 | 24 | 22 | -707 | -445 | -898 | 23 | 51 | 114 | 436 | 470 | 416
245 | Upgrade Meeden - Diele
247 | AQUIND Interconnector | PINT | 61 | 75 | 47 | 17 | 23 | 12 | 1 | 2 | 0 | -615 | -426 | -839 | 20 | 44 | 99 | 21 | 44 | 2
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 3 | 5 | 0 | -1 | 0 | -3 | 1 | 6 | 0 | 46 | 101 | -13 | -1 | -3 | -7 | 22 | 117 | 0
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | light PINT | 1 | 1 | 1 | 5 | 5 | 5 | 1 | 1 | 1 | -175 | -175 | -175 | 6 | 13 | 28 | 20 | 20 | 20
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT - A2 | 22 | 29 | 16 | 10 | 17 | 6 | 0 | 0 | 0 | -355 | -219 | -601 | 11 | 26 | 57 | 2 | 5 | 0
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 204 | 267 | 178 | -32 | -25 | -50 | 5 | 5 | 5 | 1169 | 1799 | 904 | -37 | -84 | -188 | 101 | 104 | 100
258 | Westcoast line | No assessment
259 | HU-RO | PINT | 7 | 10 | 4 | -1 | 1 | -4 | 1 | 2 | 0 | 41 | 146 | -35 | -1 | -3 | -7 | 14 | 40 | 0
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 36 | 39 | 32 | 11 | 13 | 6 | 24 | 26 | 22 | -387 | -224 | -480 | 12 | 28 | 62 | 450 | 491 | 397
262 | Belgium-Netherlands: Zandvliet-Rilland | TOOT | 14 | 15 | 12 | 6 | 6 | 5 | 16 | 17 | 14 | -201 | -184 | -230 | 6 | 14 | 32 | 300 | 333 | 261
263 | Lake Constance East | light PINT | 32 | 37 | 28 | 11 | 18 | 4 | 20 | 26 | 16 | -396 | -152 | -626 | 13 | 29 | 64 | 364 | 518 | 294
264 | Swiss Roof I | light PINT | 43 | 51 | 37 | 12 | 16 | 7 | 23 | 31 | 20 | -430 | -253 | -567 | 14 | 31 | 69 | 434 | 620 | 351
265 | Tessin | light PINT
266 | Swiss Ellipse I | PINT | 24 | 30 | 20 | 7 | 11 | 1 | 13 | 14 | 13 | -251 | -51 | -404 | 8 | 18 | 40 | 242 | 279 | 214
267 | Hansa PowerBridge II | light PINT | 25 | 27 | 22 | 4 | 5 | 3 | 8 | 11 | 4 | -133 | -106 | -180 | 4 | 10 | 21 | 149 | 197 | 80
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 57 | 64 | 53 | 8 | 11 | 5 | 32 | 37 | 28 | -299 | -187 | -377 | 10 | 22 | 48 | 601 | 701 | 514
276 | FR-ES project -Navarra-Landes | PINT | 57 | 64 | 53 | 8 | 11 | 5 | 32 | 37 | 28 | -299 | -187 | -377 | 10 | 22 | 48 | 601 | 701 | 514
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 28 | 34 | 23 | 10 | 12 | 7 | 0 | 0 | 0 | -353 | -260 | -432 | 11 | 25 | 57 | 3 | 9 | 0
283 | TuNur | PINT | 614 | 615 | 613 | 122 | 137 | 110 | 644 | 708 | 593 | -4369 | -3924 | -4877 | 140 | 315 | 703 | 11567 | 11600 | 11547 | 4000
284 | LEG1 | PINT | 85 | 87 | 82 | -49 | -48 | -51 | 0 | 0 | 0 | 1765 | 1821 | 1708 | -56 | -127 | -284 | 0 | 0 | 0 | 2000
285 | GridLink | PINT | 47 | 54 | 42 | 13 | 17 | 9 | 1 | 1 | 0 | -465 | -315 | -607 | 15 | 33 | 75 | 12 | 28 | 2
286 | Greenlink | PINT | 36 | 38 | 34 | 5 | 6 | 3 | 32 | 34 | 30 | -172 | -108 | -232 | 6 | 12 | 28 | 583 | 619 | 549
293 | Southern Aegean Interconnector | PINT | 56 | 64 | 52 | 12 | 16 | 9 | 54 | 60 | 49 | -434 | -324 | -570 | 14 | 31 | 70 | 1012 | 1205 | 852 | 582
296 | Britib | PINT | 124 | 130 | 114 | 26 | 29 | 22 | 40 | 43 | 34 | -933 | -773 | -1044 | 30 | 67 | 150 | 750 | 812 | 626
297 | BRABO II + III | PINT | 9 | 10 | 7 | 2 | 3 | 1 | 14 | 14 | 12 | -75 | -22 | -120 | 2 | 5 | 12 | 257 | 280 | 222
299 | SACOI3 | TOOT | 28 | 35 | 24 | 5 | 7 | 4 | 0 | 0 | 0 | -170 | -132 | -234 | 5 | 12 | 27 | 2 | 6 | 0
309 | NeuConnect | TOOT | 43 | 52 | 39 | 11 | 15 | 7 | 24 | 26 | 21 | -406 | -250 | -519 | 13 | 29 | 65 | 435 | 492 | 386
312 | St. Peter (AT) - Tauern (AT) | TOOT | 63 | 71 | 57 | 17 | 28 | 9 | 36 | 38 | 32 | -594 | -332 | -995 | 19 | 43 | 96 | 655 | 735 | 607
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 63 | 71 | 57 | 17 | 28 | 9 | 36 | 38 | 32 | -594 | -332 | -995 | 19 | 43 | 96 | 655 | 735 | 607
320 | Slovenia-Hungary/Croatia interconnection | TOOT | 2 | 3 | 0 | -1 | 1 | -3 | 0 | 0 | 0 | 22 | 120 | -24 | -1 | -2 | -4 | 1 | 1 | 0
322 | Wullenstetten - Border Area (DE-AT) | PINT | -20 | -12 | -23 | -1 | 0 | -2 | -9 | -6 | -10 | 45 | 76 | 5 | N/A | N/A | N/A | -174 | -128 | -206
323 | Dekani (SI) - Zaule (IT) interconnection | PINT | 2 | 4 | 0 | 1 | 5 | -2 | 1 | 5 | 0 | -34 | 55 | -185 | 1 | 2 | 5 | 23 | 98 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | PINT | 2 | 4 | 0 | 0 | 5 | -2 | 1 | 3 | 0 | -9 | 75 | -175 | 0 | 1 | 1 | 15 | 63 | 1
325 | Obersielach (AT) - Podlog (SI) | PINT | 5 | 9 | 2 | 4 | 10 | 0 | 2 | 8 | 0 | -132 | 9 | -372 | 4 | 10 | 21 | 34 | 153 | 0
328 | Interconnector DE-LUX | PINT | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | -1 | 0 | 0 | 0 | 6 | 10 | 3
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 363 | 363 | 363 | 77 | 77 | 77 | 399 | 399 | 399 | -2759 | -2759 | -2759 | 88 | 199 | 444 | 7546 | 7546 | 7546
330 | 4th 400kV CZ-SK interconnector | light PINT | 3 | 4 | 2 | -2 | -2 | -3 | 2 | 5 | 0 | 85 | 94 | 75 | -3 | -6 | -14 | 31 | 92 | 0
333 | PST Foretaille | PINT - A1 | 44 | 53 | 35 | 19 | 23 | 14 | 0 | 0 | 0 | -687 | -511 | -814 | 22 | 49 | 111 | 1 | 3 | 0
335 | Project 335 - North Sea Wind Power Hub | light PINT | 2357 | 2367 | 2347 | 528 | 533 | 524 | 2705 | 2774 | 2636 | -18874 | -18724 | -19023 | 604 | 1359 | 3039 | 48141 | 48209 | 48073
336 | Prati (IT) – Steinach (AT) | No assessment
338 | Adriatic HVDC link | PINT | 10 | 13 | 7 | 4 | 8 | 0 | 1 | 5 | 0 | -138 | 0 | -286 | 4 | 10 | 22 | 28 | 104 | 1
339 | Italian HVDC tri-terminal link | PINT | 3 | 7 | 1 | 1 | 6 | -1 | 1 | 5 | 0 | -47 | 50 | -218 | 2 | 3 | 8 | 25 | 97 | 0
340 | Avelgem-Center: new corridor (Boucle du Hainaut) | TOOT | 242 | 242 | 242 | 51 | 51 | 51 | 266 | 266 | 266 | -1839 | -1839 | -1839 | 59 | 132 | 296 | 5031 | 5031 | 5031
341 | North CSE Corridor | PINT | 1 | 1 | 0 | 1 | 4 | 0 | 1 | 4 | 0 | -35 | 6 | -145 | 1 | 3 | 6 | 21 | 80 | 0
342 | Central Balkan Corridor | PINT | 1 | 2 | 1 | 0 | 0 | -1 | 1 | 5 | 0 | 16 | 33 | -3 | -1 | -1 | -3 | 27 | 106 | 0
343 | CSE1 New | PINT | 9 | 14 | 5 | -1 | 3 | -4 | 1 | 3 | 0 | 48 | 152 | -116 | -2 | -3 | -8 | 17 | 58 | 0
344 | Reinforcements Ring NL phase II | PINT
346 | ZuidWest380 NL Oost | PINT | 8 | 10 | 6 | 2 | 3 | 1 | 14 | 14 | 12 | -74 | -19 | -120 | 2 | 5 | 12 | 258 | 280 | 225
348 | NoordWest380 NL | PINT
349 | MaresConnect | PINT | 235 | 238 | 230 | 46 | 49 | 45 | 260 | 263 | 257 | -1640 | -1590 | -1735 | 52 | 118 | 264 | 4832 | 4964 | 4700 | 1800
350 | South Balkan Corridor
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 8 | 12 | 4 | -2 | 1 | -5 | 0 | 1 | 0 | 59 | 175 | -42 | -2 | -4 | -9 | 5 | 9 | 1
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 1 | 1 | 0 | 1 | 4 | -1 | 1 | 4 | 0 | -27 | 26 | -132 | 1 | 2 | 4 | 24 | 71 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 8 | 10 | 6 | 2 | 3 | 1 | 14 | 14 | 12 | -74 | -19 | -120 | 2 | 5 | 12 | 258 | 280 | 225
378 | Transformer Gatica | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
379 | Uprate Gatica lines | TOOT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 303 | 378 | 177 | 13 | 20 | 2 | 118 | 158 | 55 | -446 | -63 | -698 | 14 | 32 | 72 | 2481 | 3356 | 1130
1039 | SE North-south long-term reinforcements | light PINT | 5 | 9 | 2 | 0 | 1 | 0 | 2 | 6 | 0 | -17 | -1 | -37 | 1 | 1 | 3 | 45 | 129 | 0
1040 | LirIC | PINT | 46 | 49 | 44 | 6 | 9 | 5 | 41 | 43 | 39 | -222 | -168 | -310 | 7 | 16 | 36 | 767 | 816 | 727
1041 | GREGY Interconnector | PINT | 76 | 76 | 76 | -221 | -217 | -224 | 0 | 1 | 0 | 7881 | 8014 | 7749 | -252 | -567 | -1269 | 7 | 11 | 2
1042 | Offshore wind integration | PINT | 114 | 120 | 110 | 25 | 29 | 22 | 125 | 136 | 111 | -910 | -770 | -1027 | 29 | 66 | 147 | 2231 | 2352 | 2181 | 600
1043 | Wahle-Mecklar
1046 | N-S Finland P1 stage 3 | PINT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1047 | Emden-Eemshaven | light PINT | 2 | 3 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | -3 | 3 | -12 | 0 | 0 | 1 | 9 | 14 | 0
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | light PINT | 56 | 56 | 56 | -157 | -157 | -158 | 1 | 1 | 0 | 5618 | 5637 | 5599 | -180 | -404 | -904 | 10 | 21 | 0
1049 | Cronos Energy Ltd | PINT | 16 | 17 | 14 | 4 | 5 | 2 | 0 | 1 | 0 | -127 | -56 | -168 | 4 | 9 | 20 | 8 | 17 | 3
1050 | Tarchon Energy Ltd | PINT | 30 | 32 | 27 | 7 | 11 | 3 | 20 | 21 | 18 | -251 | -106 | -394 | 8 | 18 | 40 | 367 | 393 | 326
1051 | Aminth Energy Ltd | PINT | 27 | 30 | 24 | 8 | 10 | 6 | 18 | 19 | 16 | -300 | -209 | -375 | 10 | 22 | 48 | 338 | 358 | 298
1052 | Lienz (AT) - Obersielach (AT) | PINT | 6 | 9 | 3 | 4 | 10 | -2 | 2 | 8 | 0 | -144 | 74 | -372 | 5 | 10 | 23 | 42 | 153 | 0
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 14 | 17 | 13 | 4 | 7 | 2 | 9 | 10 | 8 | -136 | -55 | -246 | 4 | 10 | 22 | 165 | 194 | 140
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 321 | 321 | 320 | 19 | 23 | 15 | 0 | 1 | 0 | -667 | -538 | -818 | 21 | 48 | 107 | 5 | 13 | 1
1056 | Croatian south connection | light PINT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1057 | HVDC CentraLink | light PINT
1058 | HVDC Interconnector DE-CH | light PINT
1059 | Southern Italy | PINT | 1 | 1 | 0 | 1 | 5 | 0 | 1 | 4 | 0 | -49 | 4 | -166 | 2 | 4 | 8 | 17 | 81 | 0
1061 | Reactive compensation for project 197
1062 | Reactive compensation for project 1046
1063 | ZuidWest380 West
1066 | Bulgaria - Turkey | light PINT | 171 | 211 | 132 | 19 | 22 | 16 | 0 | 0 | 0 | -694 | -585 | -802 | 22 | 50 | 112 | 1 | 1 | 0
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 73 | 115 | 37 | 12 | 15 | 10 | 1 | 4 | 0 | -418 | -342 | -537 | 13 | 30 | 67 | 26 | 78 | 0
1068 | LaSGo Link | light PINT | 12 | 22 | 1 | 4 | 7 | 1 | 2 | 3 | 1 | -128 | 0 | -266 | 4 | 9 | 21 | 35 | 68 | 0
1074 | Pannonian Corridor | light PINT | 7 | 10 | 3 | -1 | 2 | -3 | 1 | 3 | 0 | 27 | 106 | -78 | -1 | -2 | -4 | 21 | 62 | 0
1077 | Crete-North Greece-North Macedonia-Bulgaria Interconnector | light PINT | 1 | 1 | 0 | 1 | 2 | -1 | 0 | 1 | 0 | -10 | 31 | -61 | 0 | 1 | 2 | 0 | 0 | 0
1081 | LAG Interconnector (LAG) | light PINT | 133 | 264 | 2 | -118 | 2 | -182 | 1 | 2 | 0 | 4231 | 6484 | 0 | -135 | -305 | -681 | 0 | 1 | 0
1082 | Sea-Socket | light PINT | 54 | 73 | 2 | 11 | 15 | 2 | 57 | 80 | 2 | -374 | 0 | -534 | 12 | 27 | 60 | 1070 | 1465 | 0 | 700

## Trans.ProjectLevelBenefits
Project ID | Project name | B7 System Flexibility – Balancing Energy Exchange | [5 empty] | B8 Focus on Frequency quality targets (energy aspect): for HVDC interconnectors between synchronous areas | [5 empty] | B8 Blackstart services – Application for synchronization with Continental Europe | [5 empty] | B9 Reduction of Necessary Reserve for Redispatch Power Plants
|  | NT2025 | NT2030 | DE2030 | GA2030 | 2025 | 2030 | NT2025 | NT2030 | DE2030 | GA2030 | 2025 | 2030 | NT2025 | NT2030 | DE2030 | GA2030 | 2025 | 2030 | NT2025 | NT2030 | DE2030 | GA2030 | 2025 | 2030
|  | Qualitative assessment by ENTSO-E | [5 empty] | MWh/year | [5 empty] | M€ / year | [11 empty] | Unit
1 | RES in north of Portugal
4 | Interconnection Portugal-Spain | + | +
16 | Biscay Gulf
23 | FR-BE: Avelin/Mastaing-Avelgem-Horta HTLS
26 | Reschenpass Interconnector Project |  |  |  |  | ++
28 | Italy-Montenegro
29 | Italy-Tunisia | [5 empty] | ++
33 | Central Northern Italy |  |  |  |  | + | +
35 | CZ Southwest-east corridor
36 | Kriegers Flak CGS
37 | Norway - Germany, NordLink
39 | DKW-DE, step 3
40 | Belgium-Luxembourg-Germany: long-term perspective
47 | Westtirol (AT) - Vöhringen (DE)
48 | New SK-HU intercon. - phase 1
62 | Estonia-Latvia 3rd IC
78 | South West Cluster
81 | North South Interconnector
82 | RIDP I
85 | Integration of RES in Alentejo
92 | ALEGrO
94 | GerPol Improvements
103 | Reinforcements Ring NL phase I
107 | Celtic Interconnector
110 | Norway-Great Britain, North Sea Link
111 | 3rd AC Finland-Sweden north
120 | MOG II: connection of up to 2 GW additional offshore wind Belgium
121 | Nautilus: multi-purpose interconnector Belgium - UK
123 | LitPol Link Stage 2
124 | NordBalt phase 2
126 | SE North-south short-term reinforcements
127 | Central Southern Italy |  |  |  |  | ++ | ++
130 | HVDC SuedOstLink Wolmirstedt to area Isar | [18 empty] | 22 1080 | 13 625 | 125 6249 | 25 1254 |  |  | Meuro/year MW
132 | HVDC Line A-North | [18 empty] | 35 1751 | 48 2388 | 145 7231 | 64 3185 |  |  | Meuro/year MW
138 | Black Sea Corridor
142 | CSE4
144 | Mid Continental East corridor
150 | Italy-Slovenia | [5 empty] | ++
153 | France-Alderney-Britain
167 | Viking DKW-GB
170 | Baltic States Synchronization with Continental Europe | [11 empty] | 42200 | [5 empty] | 5,8 |  |  |  |  | 840,5 900 | 840,5 900 | Meuro/year MW
172 | ElecLink
173 | FR-BE: PSTs Aubange-Moulaine
174 | Greenconnector
176 | Hansa PowerBridge I
179 | DKE - DE (Kontek2)
183 | DKW-DE, Westcoast
186 | East of Austria | [18 empty] | -10.1 | -1.3 |  |  |  |  | Meuro/year MW
187 | St. Peter (AT) - Pleinting (DE)
190 | NorthConnect |  |  |  |  | + | +
197 | N-S Finland P1 stage 2
200 | CZ Northwest-South corridor
207 | Reinforcement Northwestern DE
208 | N-S Western DE_section North_1
210 | Wurmlach (AT) - Somplago (IT) interconnection
219 | EuroAsia Interconnector
225 | 2nd interconnector Belgium - Germany
227 | Transbalkan Corridor
228 | Muhlbach - Eichstetten
229 | GerPol Power Bridge II
230 | GerPol Power Bridge I
231 | Beznau - Tiengen
233 | Connection of Aragon Pumping hydro
234 | DKE - PL-1
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Grafenrheinfeld | [18 empty] | 66 3292 | 97 4830 | 295 14746 | 94 4703 |  |  | Meuro/year MW
239 | Fenno-Skan 1 renewal
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines
243 | New 400 kV interconnection line between Serbia and Croatia
244 | Vigy - Uchtelfangen area
245 | Upgrade Meeden - Diele
247 | AQUIND Interconnector
250 | Merchant line Castasegna (CH) - Mese (IT)
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator
253 | Upstream reinforcement in France to increase FR-CH capacity
254 | HVDC Ultranet Osterath to Philippsburg | [18 empty] | 19 950 | 1 41 | 161 8038 | 0.5 13.5 |  |  | Meuro/year MW
258 | Westcoast line
259 | HU-RO
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands
262 | Belgium-Netherlands: Zandvliet-Rilland
263 | Lake Constance East
264 | Swiss Roof I
265 | Tessin
266 | Swiss Ellipse I
267 | Hansa PowerBridge II
270 | FR-ES project -Aragón-Atlantic Pyrenees
276 | FR-ES project -Navarra-Landes
280 | FR-BE: study Lonny-Achene-Gramme
283 | TuNur
284 | LEG1
285 | GridLink
286 | Greenlink
293 | Southern Aegean Interconnector
296 | Britib
297 | BRABO II + III
299 | SACOI3 |  |  |  |  | ++ | ++
309 | NeuConnect
312 | St. Peter (AT) - Tauern (AT) | [18 empty] | 15.4 | -4.1 |  |  |  |  | Meuro/year MW
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT)
320 | Slovenia-Hungary/Croatia interconnection |  |  |  |  | + | +
322 | Wullenstetten - Border Area (DE-AT) | [18 empty] | 1 58 | 4 186 | 8 391 | -1 -39 |  |  | Meuro/year MW
323 | Dekani (SI) - Zaule (IT) interconnection
324 | Redipuglia (IT) - Vrtojba (SI) interconnection
325 | Obersielach (AT) - Podlog (SI)
328 | Interconnector DE-LUX
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor
330 | 4th 400kV CZ-SK interconnector
333 | PST Foretaille
335 | Project 335 - North Sea Wind Power Hub
336 | Prati (IT) – Steinach (AT)
338 | Adriatic HVDC link | [5 empty] | ++
339 | Italian HVDC tri-terminal link |  |  |  |  | ++ | ++
340 | Avelgem-Center: new corridor (Boucle du Hainaut)
341 | North CSE Corridor
342 | Central Balkan Corridor
343 | CSE1 New
344 | Reinforcements Ring NL phase II
346 | ZuidWest380 NL Oost
348 | NoordWest380 NL
349 | MaresConnect
350 | South Balkan Corridor
375 | Lienz (AT) - Veneto region (IT) 220 kV | [5 empty] | ++
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht
378 | Transformer Gatica
379 | Uprate Gatica lines
1034 | HVDC corridor from Northern Germany to Western Germany | [18 empty] | 5 234 | 13 637 | 232 11623 | 34 1694 |  |  | Meuro/year MW
1039 | SE North-south long-term reinforcements
1040 | LirIC
1041 | GREGY Interconnector
1042 | Offshore wind integration
1043 | Wahle-Mecklar
1046 | N-S Finland P1 stage 3
1047 | Emden-Eemshaven
1048 | Greece - Africa Power Interconnector (GAP Interconnector)
1049 | Cronos Energy Ltd
1050 | Tarchon Energy Ltd
1051 | Aminth Energy Ltd
1052 | Lienz (AT) - Obersielach (AT) | [18 empty] | -1.2 | -3.5 |  |  |  |  | Meuro/year MW
1054 | Westtirol (AT) - Zell/Ziller (AT) | [18 empty] | -5.8 | -1.9 |  |  |  |  | Meuro/year MW
1055 | Interconnection of Crete to the Mainland System of Greece
1056 | Croatian south connection
1057 | HVDC CentraLink
1058 | HVDC Interconnector DE-CH
1059 | Southern Italy |  |  |  |  | ++ | ++
1061 | Reactive compensation for project 197
1062 | Reactive compensation for project 1046
1063 | ZuidWest380 West
1066 | Bulgaria - Turkey
1067 | New AC 400 kV interconnection line Greece - Turkey
1068 | LaSGo Link
1074 | Pannonian Corridor
1077 | Crete-North Greece-North Macedonia-Bulgaria Interconnector
1081 | LAG Interconnector (LAG)
1082 | Sea-Socket

## Stor.ProjectLevelBenefits
Project ID | Project name | B7 System Flexibility – Balancing Energy Exchange | [5 empty] | B8 Frequency stability | [5 empty] | B8 Blackstart Service | [5 empty] | B9 Reduction of Necessary Reserve for Redispatch Power Plants
|  | NT2025 | NT2030 | DE2030 | GA2030 | 2025 | 2030 | NT2025 | NT2030 | DE2030 | GA2030 | 2025 | 2030 | NT2025 | NT2030 | DE2030 | GA2030 | 2025 | 2030 | NT2025 | NT2030 | DE2030 | GA2030 | 2025 | 2030
|  | Qualitative assessment by ENTSO-E | [5 empty] | MWh/year | [5 empty] | M€ / year | [11 empty] | Unit