## Delta GTC Contributions
TYNDP 2016 Project Index | GTC_2020_1 | GTC_2020_2 | GTC_2030_1 | GTC_2030_2
1 | outside-inside: 2500 | inside-outside: 3100 | outside-inside: 2900 | inside-outside: 4200
2 | downstream-upstream: - | upstream-downstream: 1100 | downstream-upstream: - | upstream-downstream: 1700
4 | PT-ES: [700 ; 1000] | ES-PT: [1300 ; 1900] | PT-ES: [700 ; 1000] | ES-PT: [1300 ; 1900]
13 |  |  | ROW-Baza: [2200 ; 3100] | Baza-ROW: [1900 ; 2300]
16 | FR-ES: 2200 | ES-FR: 2600 | FR-ES: 2200 | ES-FR: 2600
21 | IT-FR : 1000 | FR - IT: 1200 | IT-FR : 1000 | FR - IT: 1200
22 | FR-CH: 500 | CH-FR: 0 | FR-CH: 550 | CH-FR: 100
23 | FR-BE: [800 ; 1200] | BE-FR: [800 ; 1200] | FR-BE: [600 ; 1000] | BE-FR: [600 ; 1000]
24 | BE-NL: 1000 | NL-BE: 1000 | BE-NL: [700 ; 1000] | NL-BE: [700 ; 1000]
25 | GB-FR: 1000 | FR-GB: 1000 | GB-FR: 1000 | FR-GB: 1000
26 |  |  | IT-AT: 1000 | AT-IT: 1100
28 | ME-IT : 1200 | IT - ME: 1200 | ME-IT : 1200 | IT - ME: 1200
29 | TU-IT: 600 | IT-TU: 600 | TU-IT: 600 | IT-TU: 600
31 | IT-CH: 600 | CH-IT: [1000 ; 1100] | IT-CH: 750 | CH-IT: 750
33 | IT North-IT Center : 600 | IT Center - IT North: 400 | IT North-IT Center : 600 | IT Center - IT North: 400
35 | DE-CZ: 500 | CZ-DE: 950 | DE-CZ: 500 | CZ-DE: 500
36 | DKE-DE: 400 | DE-DKE: 150 | DKE-DE: 150 | DE-DKE: 150
37 | DE-NO: 1400 | NO-DE: 1400 | DE-NO: 1400 | NO-DE: 1400
39 | DKW-DE: 720 | DE-DKW: 1000 | DKW-DE: 720 | DE-DKW: 1000
40 | BE-LU: 900 | LU-BE: 900 | BE-LU: 900 | LU-BE: 900
42 |  |  | -: 5750 | -: 5750
47 | DE-AT: 2900 | AT-DE: 2900 | DE-AT: 2900 | AT-DE: 2900
48 | HU-SK: 200 | SK-HU: 1550 | HU-SK: 950 | SK-HU: 2400
54 |  |  | HU-SK: 300 | SK-HU: 250
55 |  | outside: 650 | outside: 0 | outside: 100
62 | LV-EE: 500 | EE-LV: 500 | LV-EE: 600 | EE-LV: 600
69 |  |  | GB Internal: 1950 | GB Internal: 1950
71 | NL-DKW: 700 | DKW-NL: 700 | NL-DKW: 700 | DKW-NL: 700
74 | BE-GB: 1000 | GB-BE: 1000 | BE-GB: 1000 | GB-BE: 1000
75 | BE-BEcoast: 3000 | BEcoast-BE: 3000 | BE-BEcoast: 3000 | BEcoast-BE: 3000
77 |  |  | GB Internal: 2400 | GB Internal: 2400
78 |  |  | GB Internal: 4150 | GB Internal: 4150
79 |  |  | GB Internal: 2000 | GB Internal: 2000
81 | IE-NI: 800 | NI-IE: 800 | IE-NI: 800 | NI-IE: 800
82 |  |  | IE-NI: 550 | NI-IE: 600
85 |  |  | outide-inside: - | inside-outide: 1400
86 |  |  | GB Internal: n/a | GB Internal: n/a
92 | DE-BE: 1000 | BE-DE: 1000 | DE-BE: 1000 | BE-DE: 1000
94 | DE-PL: 2000 | PL-DE: 1000 | DE-PL: 500 | PL-DE: 1500
96 |  |  | -: 900 | -: 800
103 |  |  | NL-DE: n/a | DE-NL: 2900
107 |  |  | IE-FR: 700 | FR-IE: 700
110 | NO-GB: 1400 | GB-NO: 1400 | NO-GB: 1400 | GB-NO: 1400
111 | SE1-FI: 500 | FI-SE1: 800 | SE1-FI: 500 | FI-SE1: 800
113 | NL-DE: [1100 ; 1200] | DE-NL: [1100 ; 1500] | NL-DE: n/a | DE-NL: (1500 ; 1800]
120 |  |  | BE-BEcoast: 2000 | BEcoast-BE: 2000
121 |  |  | BE-GB: 1000 | GB-BE: 1000
123 | LT-PL: 500 | PL-LT: 1000 | LT-PL: 500 | PL-LT: 1000
124 | SE4-LT: 0 | LT-SE4: 0 | SE4-LT: 0 | LT-SE4: 0
126 | SE3-SE2: 500 | SE2-SE3: 500 | SE3-SE2: 500 | SE2-SE3: 500
127 | IT South-IT Center : 1200 | IT Center - IT South: 0 | IT South-IT Center : 1200 | IT Center - IT South: 0
129 |  |  | -: 4500 | -: 4500
130 | PL+CZ+AT-DE: 650 | DE-PL+CZ+AT: 650 | PL-DE: 650 | DE-PL: 650
132 | DE intern | DE intern | DE intern | DE intern
133 |  |  | -: - | -: -
134 | DE intern | DE intern | DE intern | DE intern
135 | DE intern: - | DE intern: - | DE intern: - | DE intern: -
136 | HR-BA: 950 | BA-HR: 650 | HR-BA: 200 | BA-HR: 500
138 | BG-RO: 1000 | RO-BG: 1200 | BG-RO: 800 | RO-BG: 1350
141 | SI-HU : 1650 | HU -SI: 650 | SI-HU : 800 | HU -SI: 1050
142 | GR-RO,BG: 0 | RO,BG-GR: 650 | GR-RO,BG: 400 | RO,BG-GR: 850
144 | HU,RS,HR,BA,ME-RO: 500 | RO-HU,RS,HR,BA,ME: 950 | HU,RS,HR,BA,ME-RO: 750 | RO-HU,RS,HR,BA,ME: 950
146 | IT-HR,BA,RO,RS,BG: 400 | HR,BA,RO,RS,BG-IT: 600 | IT-HR,BA,RO,RS,BG: 100 | HR,BA,RO,RS,BG-IT: 800
147 | AL,MK,GR-RO,RS,BG: 750 | RO,RS,BG-AL,MK,GR: 1250 | AL,MK,GR-RO,RS,BG: 200 | RO,RS,BG-AL,MK,GR: 750
150 | SI-IT: 1000 | IT-SI: 800 | SI-IT: 950 | IT-SI: 950
151 |  |  | ROW-central Asturias: [100 ; 1400] | central Asturias-ROW: [0 ; 300]
153 | GB-FR: 1400 | FR-GB: 1400 | GB-FR: 1400 | FR-GB: 1400
157 |  |  | east-west: [0 ; 2000] | west-east: [200 ; 1000]
158 |  |  | South-[FR] North : 3000 | [FR] North - South: 3000
164 | DE intern | DE intern | DE intern | DE intern
167 | GB-DKW: 1400 | DKW-GB: 1400 | GB-DKW: 1400 | DKW-GB: 1400
168 |  |  | NL-DE: 0 | DE-NL: 200
170 |  |  | LT-PL: 0 | PL-LT: 0
172 | GB-FR: 1000 | FR-GB: 1000 | GB-FR: 1000 | FR-GB: 1000
173 |  |  | FR-BE: [400 ; 500] | BE-FR: [400 ; 500]
174 | IT-CH: 800 | CH-IT: [800 ; 1200] | IT-CH: 850 | CH-IT: 850
175 |  |  | DKW-DKE: 600 | DKE-DKW: 600
176 | SE4-DE: 700 | DE-SE4: 700 | SE4-DE: 700 | DE-SE4: 700
177 | DE-CZ: 500 | CZ-DE: 0 | DE-CZ: 550 | CZ-DE: 150
179 |  |  | DE-DKE: 600 | DKE-DE: 600
183 | DKW-DE: 500 | DE-DKW: 500 | DKW-DE: 500 | DE-DKW: 500
184 | FR-ES: 100 | ES-FR: 500 | FR-ES: 100 | ES-FR: 500
186 | Outside: 1500 | Inside: 1500 | Outside: 1500 | Inside: 1500
187 |  |  | DE-AT: 1500 | AT-DE: 1500
189 |  |  | IE-GB: 1000 | GB-IE: 1000
190 | NO-GB: 1400 | GB-NO: 1400 | NO-GB: 1400 | GB-NO: 1400
191 |  |  | -: 2700 | -: 2700
192 |  |  | -: 3600 | -: 3600
193 |  |  | south-north: [1100 ; 2400] | north-south: [800 ; 2300]
194 |  |  | ROW-Cartuja: [450 ; 750] | Cartuja-ROW: [750 ; 850]
197 |  |  | -: 850 | -: 700
198 |  |  | DE-AT: 1000 | AT-DE: 1000
199 |  |  | FR-CH: 750 | CH-FR: 1300
200 | DE-CZ: 500 | CZ-DE: 300 | DE-CZ: 500 | CZ-DE: 500
203 | south-north: 1000 | north-south: 1400 | south-north: [400 ; 2000] | north-south: [400 ; 1600]
204 | DE intern | DE intern | DE intern | DE intern
205 | CZ-DE: 550 | DE-CZ: 550 | CZ-DE: 550 | DE-CZ: 550
206 | DE intern | DE intern | DE intern | DE intern
207 | DE intern | DE intern | DE intern | DE intern
208 | DE intern | DE intern | DE intern | DE intern
209 | DE intern | DE intern | DE intern | DE intern
210 | IT-AT: 150 | AT-IT: 150 | IT-AT: 150 | AT-IT: 150
214 |  |  | IS-GB: 1200 | GB-IS: 1200
216 |  |  | South-[FR] North : 3000 | [FR] North - South: 3000
219 | CY-GR: 2000 | GR-CY: 2000 | CY-GR: 2000 | GR-CY: 2000
225 |  |  | DE-BE: 1000 | BE-DE: 1000
227 | IT-HR,BA,RO,RS,BG: 350 | HR,BA,RO,RS,BG-IT: 1050 | IT-HR,BA,RO,RS,BG: 50 | HR,BA,RO,RS,BG-IT: 800
228 |  |  | FR-DE : 300 | DE - FR: 300
229 |  |  | DE-PL: 1500 | PL-DE: 0
230 | DE-PL: 1000 | PL-DE: 500 | DE-PL: 1500 | PL-DE: 500
231 |  |  | CH-DE: [700 ; 1000] | DE-CH: [700 ; 1000]
232 |  |  | DKE-DE: 600 | DE-DKE: 600
233 |  |  | -: 0 | -: 0
234 |  |  | PL-DKE: 600 | DKE-PL: 600
235 | NO&DKW -DE: 1800 | DE-NO&DKW : 1800 | NO&DKW -DE: 1800 | DE-NO&DKW : 1800
236 | BE: 1500 | BE: 1500 | BE: 1500 | BE: 1500
237 |  |  | NL-DKW: 700 | DKW-NL: 700
238 |  |  | SE3-DKW: 350 | DKW-SE3: 350
239 |  |  | SE3-FI: [500 ; 800] | FI-SE3: [500 ; 800]
240 | DE intern | DE intern | DE intern | DE intern
241 |  |  | BA-HR: 350 | HR-BA: 250
242 | DE: 1100 | DE: 1100 | DE: 1100 | DE: 1100
243 |  |  | HR-RS: 750 | RS-HR: 300
244 |  |  | FR-DE: 1500 | DE-FR: 1500
245 | NL-DE: 0 | DE-NL: 0 | NL-DE: n/a | DE-NL: 300
247 |  |  | GB-FR: 2000 | FR-GB: 2000
248 |  |  | Internal DE: 1100
249 |  |  | South West-[FR] North East : 3000 | [FR] North East - South West: 3000
250 | IT-CH: 100 | CH-IT: 100 | IT-CH: 100 | CH-IT: 100
251 | DKW -DE: 1000 | DE-DKW : 700 | DKW -DE: 1000 | DE-DKW : 700
252 | BE: 1400 | BE: 1400 | BE: 1400 | BE: 1400
253 |  |  | FR-CH: 650 | CH-FR: 100
254 | CH-DE & NL-DE: 600 | DE-CH & DE-NL: 600 | CH-DE & NL-DE: 600 | DE-CH & DE-NL: 600
255 | east-west: 1750 | west-east: 1000 | east-west: [400 ; 750] | west-east: [250 ; 3000]
256 |  |  | NL-DE: n/a | DE-NL: [1000 ; 2000]
257 |  |  | PT-ES: 700 | ES-PT: 300
258 | DKW -DE: 500 | DE-DKW : 500 | DKW -DE: 500 | DE-DKW : 500
259 |  |  | HU-RO: 200 | RO-HU: 800
260 |  |  | NL-GB: 1000 | GB-NL: 1000
261
262 |  |  | BE-NL: 1000 | NL-BE: 1000
263 |  |  | Swissroof-CH: 350 | CH-Swissroof: 800
264 | Swissroof-CH : 1600 | CH - Swissroof: 1100 | Swissroof-CH : 2000 | CH - Swissroof: 2000
265 |  |  | Export-CH: 1650 | CH-Export: 1650
266 | Export-CH: 1900 | CH-Export: 1900 | Export-CH: 2400 | CH-Export: 2400
267 |  |  | SE4-DE: 700 | DE-SE4: 700
268 |  |  | RS-RO: 500 | RO-RS: 550
269 | PT-ES: 500 | ES-PT: 0 | PT-ES: 500 | ES-PT: 0
270 |  |  | FR-ES: 1500 | ES-FR: 1500
271
272 |  |  | RS-BGMRO: 50 | BGMRO-RS: 200
273 |  |  | RS-RO: 0 | RO-RS: 100
274
275
276 |  |  | FR-ES: 1500 | ES-FR: 1500
277 |  |  | RS-BG: 400 | BG-RS: 1500
278 |  |  | FR-ES: 1500 | ES-FR: 1500
279 |  |  | GR-BG: 250 | BG-GR: 450
280 |  |  | FR-BE: [1000] | BE-FR: [1000]
281 |  |  | Boundary Iberia-central EU: 2000 MW both directions | Boundary GB-central EU: 1800 MW both directions
282 |  |  | Boundary Iberia-rest of EU: 700 MW IB-->rest of EU; 0 MW rest of EU-->IB | Boundary FR-IT: 1000 MW both directions
283 |  |  | TN-IT: 1000 | IT-TN: 1000
284 |  |  | -: - | -: -
285 |  |  | GB-FR: 1500 | FR-GB: 1500
286 |  |  | IE-GB: 700 | GB-IE: 700
287 |  |  | IE-GB: 1300 | GB-IE: 1300
289 |  |  | IE-GB: 1500 | GB-IE: 1500
290 |  |  | IE-GB: 1000 | GB-IE: 1000
291 |  |  | IE-GB: 700 | GB-IE: 700
292 |  |  | IE-GB: 700 | GB-IE: 700
293 |  |  | -: - | -: -
294 |  |  | NO-GB: 600 | GB-NO: 600
295 |  |  | IE-GB: 500 | GB-IE: 500
296 |  |  | Boundary Iberia-central EU: 0 MW IB-->central EU; 1400 MW centralEU-->IB | Boundary GB-central EU: 1800 MW both directions
297 | BE-NL: 1000 | NL-BE: 1000 | BE-NL: [700 ; 1000] | NL-BE: [700 ; 1000]
298 | GB Internal: - | GB Internal: - | GB Internal: 2000 | GB Internal: 2000
299 |  |  | Italy Sardinia – Italy Central North 400 MW Italy Central North – Italy Sardinia 400 MW | Italy – France (Corsica) 100 MW France (Corsica) – Italy 100 MW

## Storage Projects
TYNDP 2016 Project Index | TYNDP 2016:Project candidate name | Promoter(s) | Saving in generation capacity, (Meuro/y) | Country | Maximum active power [MW] | Total storage capacity [GWh] - and defined as total energy delivered to the grid when reservoir is totally emptied, starting at reservoir full condition | TYNDP 2016 expected commissioning date
1000 | Hydro Pump Storage Power Plant Pfaffenboden in Molln | Wien Energie GmbH | 10 | Austria | 300 | 1.8 | 2019
1001 | Kaunertal Extension Project | TIWAG | 34 | Austria | 1076 | 152 | 2028
1002 | iLand | THV iLand | 18 | Belgium | 550 | 2 | 2021
1003 | PCI hydro-pumped storage in Bulgaria - Yadenitsa | NATSIONALNA ELEKTRICHESKA KOMPANIA EAD | 28 | Bulgaria | 864 | 5.2 | 2021
1004 | Muuga HPSPP | Energiasalv OÜ | 16 | Estonia | 500 | 6 | 2023
1005 | CAES Cheshire, UK | Gaelectric Energy Storage Ltd | 9 | Great Britain | 268 | 1.608 | 2022
1006 | Pumped Storage Complex with two independent upper reservoirs: Agios Georgios & Pyrgos | TERNA ENERGY S.A | 19 | Greece | 594 | 3436 | 2021
1007 | MAREX storage | Organic Power Ltd. | 22 | Ireland | 680 | 3.974 | 2020
1008 | Battery storage in South Italy | Terna | 8 | Italy | 250 | 1.7 | 2022
1009 | Kruonis pumped storage power plant extension | Lietuvos energijos gamyba | 7 | Lithuania | 225 | 10.8 | 2020
1010 | CAES Larne, Northern Ireland | Gaelectric Energy Storage Ltd | 11 | Northern Ireland | 330 | 2 | 2020
1011 | Reversible pumped-storage hydro-electric exploitation "MONT-NEGRE" power 3300 MW Zaragoza, Spain | Ingenieria Pontificia S.L. | 106 | Spain | 3300 | 75.11 | 2020
1012 | Purifying -Pumped Hydroelectric Energy Storage (P-PHES Navaleo) | CDR TREMOR S.L. | 17 | Spain | 541 | 3.5 | 2018
1013 | CAES Zuidwending, NL | Gaelectric Energy Storage Ltd | 11 | The Netherlands | 330 | 2.64 | 2021
1014 | Coire Glas | SSE | 19 | UK | 600 | 30 | 2023
1015 | Cruachan II | Scottish Power | 19 | UK - Scotland | 600 | 7.2 | 2025
1016 | ANGS: Abengoa Northern Germany Storage | Abengoa | 9 | Germany | 140 | 1680 | 2019
1017 | ASSS: Abengoa Southern Spain Storage | Abengoa | 14 | Spain | 225 | 0.675 | 2019
1018 | ANSS: Abengoa Northern Spain Storage | Abengoa | 14 | Spain | 225 | 0.675 | 2019
1019 | TWO REVERSIBLE HIDROELECTRIC PLANTS: GIRONES & RAIMATS IN SPAIN | Grupo Romero Polo | 218 | Spain | 3400 | 24.5 | 2024
1020 | GIBREX STORAGE | Organic Power Ltd. | 96 | Spain | 1500 | 10 | 2022
1021 | Donegal Storage Project | Pump Storage Energy Ltd. | 96 | Ireland and Northern Ireland | 1500 | 120 | 2022
1022 | CARES (Compressed Air Renewable Energy Storage) | Storelectric Ltd | 32 | Great Britain | 500 | 2.5 | 2017

## Investments
TYNDP 2016 Project Index | TYNDP 2016 Project Index:Project candidate name | PCI Label | TYNDP 2016 Investment Index | Investment Name | Promoters | Co- Promoter TSO | Co Promoter | Co- Promoter | Cross-Border | Project Classification | Description | Voltage Level | AC or DC | EC regional initiative | Element type | TYNDP 2016 status name | From Substation name | To Substation name | GTC contribution [MW] | Investment type | Line circuit type | Line length [km] | Estimated cost [MEuro] | TYNDP 2012 status name | Estimated cost confidence [MEuro] | TYNDP 2014 expected commissioning date | TYNDP 2014 status name | TYNDP 2016 expected commissioning date | Evolution driver description | Evolution since last TYNDP
1 | RES in north of Portugal | PCI 2.16.1 and 2.16.3 |  |  | REN |  |  |  | Internal boundary in Portugal (north) | Mid-term Project | [12 empty] | 200 |  | 14.5 |  |  | 2022
1 | RES in north of Portugal |  | 474 | Rib. Pena |  | REN | - | - | Internal |  | New 400/60kV substation in Rib. Pena. | 400 |  | North-South (WEST) | Substation | Permitting | Ribeira de Pena (PT) |  | 890 | New |  |  |  | design & permitting |  | 01/01/2017 | Design & Permitting | 31/ 12/ 2020 | Due to the expected delay of the connection of new hydro power plants, the commissioning date of this investment item was rescheduled. | Rescheduled
1 | RES in north of Portugal |  | 476 | V.P.Aguiar-Carrap.-Estarreja |  | REN | - | - | Internal |  | New 400+220kV double circuit OHL (initially only used at 220kV) Vila Pouca Aguiar - (Rib. Pena) - Carrapatelo - Estarreja . Total length of line 121,7 km. | 220 | AC | North-South (WEST) | Overhead Line | Permitting | V. P. Aguiar (by Carrapatelo) | Estarreja (by Carrapatelo) | 600 | New | Double Circuit | 121.7 |  | design & permitting |  | 01/01/2017 | Design & Permitting | 31/ 12/ 2020 | Due to the expected delay of the connection of new RES generation in Portugal, the commissioning date of this investment item was rescheduled | Rescheduled
1 | RES in north of Portugal |  | 941 | Fridão |  | REN | - | - | Internal |  | New substation to connect a new hydro power plant. | 400 |  | North-South (WEST) | Substation | Permitting | Fridão |  | 890 | New | [5 empty] | 01/01/2017 | Planning | 31/ 12/ 2022 | Due to the expected delay of the connection of new hydro power plants, the commissioning date of this investment item was rescheduled | Rescheduled
1 | RES in north of Portugal |  | 1 | V.Minho-Pedralva 1&2 |  | REN | - | - | Internal |  | Connection of the new 400kV substation V.Minho to Pedralva substation by means of two new 400kV lines(33.5+33)km. The realization of this two connections can take advantage of some already existing 150kV single lines, which will be reconstructed as double circuit lines 400+150kV line and partially sharing towers with those 400kV circuits. | 400 | AC | North-South (WEST) | Overhead Line | Commissioned | V.Minho (PT) | Pedralva (PT) | 1650 | Upgrade | Double Circuit | 66.5 |  | design & permitting |  | 01/01/2015 | Under Construction | 29/ 12/ 2015 | The first circuit was commissioned in 2014, the second in 2015. | Investment on time
1 | RES in north of Portugal |  | 2 | Pedralva-Sobrado |  | REN | - | - | Internal |  | New 67km double circuit Pedralva (PT) - Sobrado (PT) 400kV OHL, (only one circuit installed in a first step). | 400 | AC | North-South (WEST) | Overhead Line | Permitting | Pedralva (PT) | Sobrado (PT) | 830 | New | Double Circuit | 66.5 |  | planned |  | 01/01/2020 | Planning | 31/ 12/ 2022 | Due to the expected delay of the connection of new RES generation in North of Portugal, the commissioning date of this investment item was rescheduled | Rescheduled
1 | RES in north of Portugal |  | 3 | Pedralva - Ponte de Lima |  | REN | - | - | Internal |  | New 37,6 km double circuit Pedralva - Ponte de Lima 400kV OHL (one circuit installed). | 400 | AC | North-South (WEST) | Overhead Line | Under Construction | Pedralva (PT) | Ponte de Lima (PT) | 680 | New | Double Circuit | 37.6 |  | design & permitting |  | 01/01/2015 | Design & Permitting | 31/ 12/ 2016 | In the first stage the line will be conected between Pedralva and Vila Nova de Famalicão (previously Vila do Conde). New substation of Ponte de Lima (previously Viana do Castelo) will be commissioned in 2018 | Delayed
1 | RES in north of Portugal |  | 4 | V.Minho -R.Pena-Fridão-Feira |  | REN | - | - | Internal |  | New 132km double-circuit 400kV OHL V.Minho (PT) - Ribeira de Pena (PT) - Fridão (PT) - Feira (PT) (one circuit operated at 220kV between V.P. Aguiar and Estarreja) with a new 400/60kV substation in Rib. Pena. In a first step, only the 69km section Rib. de Pena (PT) - Feira (PT) will be constructed and operated at 220kV as Vila Pouca Aguiar (PT) - Carrapatelo (PT) - Estarreja (PT). In a second step, one circuit of this line will be operated at 400kV. | 400 | AC | North-South (WEST) | Overhead Line | Permitting | V.Minho (by Ribeira de Pena and Fridão) | Feira (by Ribeira de Pena and Fridão) | 890 | New | Double Circuit | 132 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 31/ 12/ 2021 | Due to the expected delay of the connection of new hydro power plants, the commissioning date of this investment item was rescheduled. | Rescheduled
2 | RES in center of Portugal |  |  |  | REN |  |  |  | Internal boundary in Portugal (center) | Mid-term Project | [12 empty] | 106 |  | 6.9 |  |  | 2020
2 | RES in center of Portugal |  | 478 | Penela-Paraimo/Batalha |  | REN | - | - | Internal |  | New double circuit 400kV OHL (15km) to connect Penela substation to Paraimo-Batalha line. | 400 | AC | No EC Regional Group linked | Overhead Line | Permitting | Penela (PT) | Paraimo / Batalha (PT) | 1780 | New | Double Circuit | 15 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 31/ 12/ 2019 | Due to the expected delay of the connection of new hydro power plant, the commissioning date of this investment item was rescheduled | Rescheduled
2 | RES in center of Portugal |  | 481 | Penela 400kV |  | REN | - | - | Internal |  | Expansion of the existing Penela substation to include 400kV facilities. | 400 |  | No EC Regional Group linked | Substation | Permitting | Penela (PT) |  | 1780 | Upgrade |  |  |  | design & permitting |  | 01/01/2016 | Design & Permitting | 31/ 12/ 2019 | Due to the expected delay of the connection of new hydro power plant, the commissioning date of this investment item was rescheduled | Rescheduled
2 | RES in center of Portugal |  | 484 | Fundão |  | REN | - | - | Internal |  | New 400/220kV substation in Fundão. | 400 |  | No EC Regional Group linked | Substation | Design | Fundão (PT) |  | 450 | New |  |  |  | design & permitting |  | 01/01/2017 | Design & Permitting | 31/ 12/ 2017 | Project on time | Investment on time
2 | RES in center of Portugal |  | 8 | Seia-Penela |  | REN | - | - | Internal |  | New single circuit 400kV OHL Seia-Penela (108km). | 400 | AC | No EC Regional Group linked | Overhead Line | Permitting | Seia | Penela | 1780 | New | Single Circuit | 108 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 31/ 12/ 2020 | Due to the expected delay of the connection of new hydro power plant, the commissioning date of this investment item was rescheduled | Rescheduled
2 | RES in center of Portugal |  | 9 | Fundão-Falagueira |  | REN | - | - | Internal |  | New 400kV double circuit OHL Fundão (PT) -'Castelo Branco zone'-Falagueira (PT) | 400 | AC | No EC Regional Group linked | Overhead Line | Design | Fundão (PT) | Falagueira (PT) | 450 | New | Double Circuit | 99 |  | design & permitting |  | 01/01/2017 | Design & Permitting | 31/ 12/ 2017 | Project on time | Investment on time
4 | Interconnection Portugal-Spain | 2.17 |  |  | REE;REN |  |  |  | Portugal - Spain | Mid-term Project | [12 empty] | 128 |  | 12.8 |  |  | 2018
4 | Interconnection Portugal-Spain |  | 496 | Fontefría (ES) - Vila Nova de Famalicão (PT) |  | REN | - | - | Cross-border |  | New northern interconnection. New 400kV OHL Fontefría (ES) - Ponte de Lima (PT) - Vila Nova de Famalicão (PT). | 400 | AC | North-South (WEST) | Overhead Line | Permitting | Fontefría (ES) | Vila Nova de Famalicão (PT) (By Ponte de Lima) | 1000 | New | Double Circuit | 135 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 31/ 12/ 2018 | Due to local opposition in the border area REN had to withdraw the Portuguese section of the interconnection of the ongoing EIA process to maintain the schedule of other investments included in the EIA needed for connecting new hydro in Cávado | Delayed
4 | Interconnection Portugal-Spain |  | 497 | Vila Nova de Famalicão-Recarei/Vermoim |  | REN | - | - | Internal |  | New double circuit 400kV OHL between Vila Nova de Famalicão (PT) - Recarei/Vermoim (PT). | 400 | AC | North-South (WEST) | Overhead Line | Commissioned | Vila Nova de Famalicão (PT) | Recarei/Vermoim (PT) | 1000 | New | Double Circuit | 26 |  | design & permitting |  | 01/01/2015 | Design & Permitting | 17/ 12/ 2015 | Line commissioned | Investment on time
4 | Interconnection Portugal-Spain |  | 498 | SE Fontefria 400/220kV |  | REE | - | - | Internal |  | New northern interconnection. New 400kV substation Fontefria (ES), previously O Covelo. | 400 |  | North-South (WEST) | Substation | Permitting | Fontefria (ES) |  | 1000 | New |  |  |  | design & permitting |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2017 | The delay of this investment is affected by the explanation in the investment 496. Also, environmental problems lead to re-routing | Delayed
4 | Interconnection Portugal-Spain |  | 499 | Beariz 400kV (ES) |  | REE | - | - | Internal |  | New northern interconnection. New 400kV substation Beariz (ES), previously Boboras | 400 |  | North-South (WEST) | Substation | Permitting | Beariz (ES) |  | 1000 | New |  |  |  | design & permitting |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2017 | The delay of this investment is affected by the explanation in the investment 496. Also, environmental problems lead to re-routing | Delayed
4 | Interconnection Portugal-Spain |  | 500 | Ponte de Lima (PT) |  | REN | - | - | Internal |  | New 400/150kV substation Ponte de Lima (PT), previously V. Castelo. | 400 |  | North-South (WEST) | Substation | Permitting | Ponte de Lima (PT) |  | 1000 | New |  |  |  | design & permitting |  | 01/01/2016 | Design & Permitting | 31/ 12/ 2018 | Substation renamed to Ponte de Lima. See Investment 496. | Delayed
4 | Interconnection Portugal-Spain |  | 501 | Vila Nova de Famalicão (PT) |  | REN | - | - | Internal |  | New 400kV substation Vila Nova de Famalicão (PT), previously Vila do Conde. | 400 |  | North-South (WEST) | Substation | Commissioned | Vila Nova de Famalicão (PT) |  | 1000 | New |  |  |  | design & permitting |  | 01/01/2015 | Design & Permitting | 17/ 12/ 2015 | Substation commissioned. | Investment on time
4 | Interconnection Portugal-Spain |  | 18 | Beariz (ES) - Fontefria (ES) |  | REE | - | - | Internal |  | New northern interconnection. New double circuit 400kV OHL between Beariz (ES) - Fontefria (ES). | 400 | AC | North-South (WEST) | Overhead Line | Permitting | Beariz (ES) | Fontefria (ES) | 1000 | New | Double Circuit | 32 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2017 | The delay of this investment is affected by the explanation in the investment 496. Also, environmental problems lead to re-routing. | Delayed
13 | Baza project |  |  |  | REE |  |  |  | Internal boundary in the south of Spain | Future Project | [12 empty] | 113 |  | 11.3 |  |  | 2025
13 | Baza project |  | 569 | New substation Baza |  | REE | - | - | Internal |  | New 400kV substation in Baza | 400 |  | No EC Regional Group linked | Substation | Under Consideration | Baza (ES) |  | 2060 | New |  |  |  | design & permitting |  | 01/01/2025 | Under Consideration | 1/ 1/ 2025 | Investment rescheduled due to, and in accordance with, delayed development of new power plant, as considered in the Master Plan 2020 in progress | Investment on time
13 | Baza project |  | 570 | New substation La Ribina |  | REE | - | - | Internal |  | New 400kV substation in La Ribina (will be connected as an input/output in Carril-Litoral 400kV line ). | 400 |  | No EC Regional Group linked | Substation | Under Consideration | La Ribina (ES) |  | 2060 | New |  |  |  | design & permitting |  | 01/01/2025 | Under Consideration | 1/ 1/ 2025 | Investment rescheduled due to, and in accordance with, delayed development of new power plant, as considered in the Master Plan 2020 in progress | Investment on time
13 | Baza project |  | 31 | Axis Caparacena-Baza-La Ribina |  | REE | - | - | Internal |  | New double circuit Caparacena-Baza-La Ribina 400kV OHL. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Caparacena (ES) | La Ribina (ES) | 2060 | New | Double Circuit | 177 |  | design & permitting |  | 01/01/2025 | Under Consideration | 1/ 1/ 2025 | Investment rescheduled due to, and in accordance with, delayed development of new power plant, as considered in the Master Plan 2020 in progress | Investment on time
16 | Biscay Gulf | 2.7 |  |  | REE;RTE |  |  |  | Spain - France | Mid-term Project | [12 empty] | 1750 |  | 150 |  |  | 2022
16 | Biscay Gulf |  | 38 | HVDC Gatica-Cubnezais |  | REE | RTE | - | Cross-border |  | New HVDC interconnection in the western part of the border via DC subsea cable in the Biscay Gulf. | 320 | DC | North-South (WEST) | Subsea Cable | Planning | Gatica (ES) | Cubnezais (FR) | 2300 | New | Double Circuit | 400 |  | under consideration |  | 01/01/2023 | Planning | 01/ 01/ 2025 | There is a common political will to speed up the project, but more detailed technical studies showed the need to reschedule the project till 2025 due to manufacturing and installation needs adjustment. Specifically there will be a partial operation of the link before 2025 as the first bipole will be in service in 2024. | Rescheduled
21 | Italy-France | 2.5.1 |  |  | RTE;TERNA |  |  |  | France - Italy | Mid-term Project | [12 empty] | 1300 |  | 65 |  |  | 2019
21 | Italy-France |  | 55 | Savoie - Piémont |  | RTE | TERNA | - | Cross-border |  | "Savoie - Piémont" Project; New 190km HVDC (VSC) interconnection FR-IT via underground cable and converter stations at both ends (two poles, each of them with 600MW capacity). The cables will be laid in the security gallery of the Frejus motorway tunnel and also along the existing motorways' right-of-way. | 320 | DC | North-South (WEST) | Underground Cable | Under Construction | Grande Ile (FR) | Piossasco (IT) | 1200 | New | Double Circuit | 190 |  | design & permitting |  | 01/01/2019 | Under Construction | 1/ 1/ 2019 | Works in progress. | Investment on time
21 | Italy-France |  | 922 | Rondissone (IT) -Trino (IT) |  | TERNA | - | - | Internal |  | Removing limitations on the existing 380 kV Rondissone-Trino | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Rondissone (IT) | Trino (IT) | 300 | Upgrade | Single Circuit | 22 |  |  |  | 01/01/2019 | Planning | 2019 | - | Investment on time
21 | Italy-France |  | 923 | Lacchiarella-Chignolo Po |  | TERNA | - | - | Internal |  | Removing limitations on the existing 380 kV Lacchiarella-Chignolo Po | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Lacchiarella(IT) | Chignolo Po(IT) | 300 | Upgrade | Single Circuit | 39 |  |  |  | 01/01/2019 | Planning | 2019 | - | Investment on time
21 | Italy-France |  | 1283 | Vado-Vignole |  | TERNA | - | - | Internal |  | Removing limitations on the existing 380 kV Vado-Vignole | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Vado(IT) | Vignole(IT) | 300 | Upgrade | Single Circuit | 67 | [5 empty] | 2019 |  | Investment on time
22 | Lake Geneva West |  |  |  | RTE;SWISSGRID |  |  |  | France - Switzerland | Mid-term Project | [12 empty] | 60 |  | 12 |  |  | 2020
22 | Lake Geneva West |  | 57 | Geneva's lake (West) |  | RTE | SWISSGRID | - | Cross-border |  | Upgrading of the existing 225kV double circuit line Genissiat-Verbois to increase its capacity. | 220 | AC | No EC Regional Group linked | Overhead Line | Planning | Genissiat (FR) | Verbois (CH) | 500 | Upgrade | Double Circuit | 20 |  | under consideration |  | 01/01/2020 | Planning | 1/ 1/ 2018 | Feasibility studies showed the works are lighter and could be achieved earlier than initially thought. | Rescheduled
22 | Lake Geneva West |  | 1291 | Foretaille - Verbois |  | SWISSGRID | - | - | Internal |  | reinforcement of the existing 220 kV double line | 220 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Foretaille (CH) | Verbois (CH) |  |  | Double Circuit | [6 empty] | 01/01/2023 | Investment Foretaille - Verbois 1. Improves the security of supply in the area of Geneva 2. Ensures that the CH-FR GTC can be further increased once the investment Génissiat-Verbois has been realised | New Investment
23 | France-Belgium Phase 1 |  |  |  | ELIA;RTE |  |  |  | France - Belgium | Mid-term Project | [12 empty] | 140 |  | 20 |  |  | 2022
23 | France-Belgium Phase 1 |  | 60 | France -Belgium |  | RTE | ELIA | - | Cross-border |  | Replacement of the current conductors on the axis Avelin/Mastaing - Avelgem - Horta with high performance conductors (HTLS = High Temperature Low Sag) | 400 | AC | No EC Regional Group linked | Overhead Line | Design | Avelin/Mastaing (FR) | Horta (BE) | 1000 | Upgrade | Double Circuit | 80 |  | under consideration |  | 01/01/2023 | Planning | 1/ 1/ 2022 | Detailed feasibility studies showed the works could be achieved by 2022, earlier than initially planned, assuming acquisition of all necessary permits as planned. | Rescheduled
24 | Belgian North Border: BRABO I |  |  |  | ELIA |  |  |  | Belgium (Antwerp area) - Netherlands | Mid-term Project | [12 empty] | 30 |  | 5 |  |  | 2016
24 | Belgian North Border: BRABO I |  | 609 | BRABO I: PST 4 + Doel-Zandvliet |  | ELIA | - | - | Cross-border |  | New PST in Zandvliet substation making it the 4th PST on the Belgian North Border. Enabling this PST to increase import capacity from NL to BE implies that the current single 150 kV overhead line Zandvliet-Doel is upgraded to 380 kV, including i) adaptations to the Zandvliet & Doel substations ii) the installation of a 380/150 kV transformer in Doel iii) the installation of a 150kV cable Kallo-Ketenisse-Lillo with 150kV substation at Ketenisse The integration of this PST at Zandvliet implies that a "langskoppeling" is put at Zandvliet as temporary interface between Zandvliet and the NL network until the post "Rilland" is constructed in NL (investment item 439 as part of project # 103 "Reinforcements Ring NL"). Note that the realization of investment item 439 is needed as well to allow a capacity increase direction BE to NL. | 380 |  | North-South (WEST) | Phase Shift Transformer | Under Construction | Zandvliet (BE) |  | 1000 | Upgrade |  |  |  | planned |  | 01/01/2016 | Design & Permitting | 31/10/ 2016 | Progressed as planned. | Investment on time
25 | IFA2 | 1.7.2 |  |  | NGIHL;RTE |  |  |  | France - Great Britain | Mid-term Project | [12 empty] | 685 |  | 145 |  |  | 2020
25 | IFA2 |  | 62 | IFA2 |  | RTE | NGT | - | Cross-border |  | New subsea HVDC VSC link between the UK and France with a capacity around 1000 MW. PCI 1.7.2 (NSCOG corridor) | 320 | DC | North Seas Countries Offshore Grid Initiative | Subsea Cable | Permitting | Tourbe (FR) | Chilling (GB) | 1000 | New | Single Circuit | 250 |  | under consideration |  | 01/01/2020 | Design & Permitting | 1/ 1/ 2020 | On the French side, the Ministry of Energy aknowledged the notification of the investment on 08/04/14. | Investment on time
26 | Austria - Italy | 3.2.1 (Lienz - Veneto region) and 3.2.2 (Lienz - Obersielach) |  |  | APG;TERNA |  |  |  | Austria - Italy | Long-term Project | [12 empty] | 715 |  | 100 |  |  | 2023
26 | Austria - Italy |  | 63 | 63 |  | APG | TERNA | - | Cross-border |  | The project foresees the reconstruction of the existing 220kV-interconnection line as 380kV-line on an optimized route to minimize the environmental impact. Total length should be in the range of approx. 140km. | 400 | AC | North-South (WEST) | Overhead Line | Planning | Lienz (AT) | Veneto region (IT) | 800 | New | Single Circuit | 140 |  | planned |  | 01/01/2023 | Planning | 1/ 1/ 2024 | Planning in progress coordinatedly between TERNA and APG | Rescheduled
26 | Austria - Italy |  | 218 | 218 |  | APG | - | - | Internal |  | New 380kV OHL connecting the substations Lienz (AT) and Obersielach (AT) to close the Austrian 380kV-Security Ring in the southern grid area. Line length&#58; 190km. | 400 | AC | North-South (WEST) | Overhead Line | Planning | Obersielach (AT) | Lienz (AT) | 320 | New | Double Circuit | 190 |  | under consideration |  | 01/01/2023 | Under Consideration | 1/ 1/ 2024 | Tests and gaining of experience for novel technical solution in progress. | Rescheduled
26 | Austria - Italy |  | 614 | 614 |  | APG | TERNA | - | Cross-border |  | interconnector IT-AT | 220 | AC | North-South (WEST) | Overhead Line | Design | Nauders (AT) | Glorenza (IT) | 300 | New | Single Circuit | 15 |  | under consideration |  | 01/01/2018 | Design & Permitting | 1/ 1/ 2020 | Common planning progress between Terna an APG ongoing. | Delayed
26 | Austria - Italy |  | 1039 | Volpago substation |  | TERNA | - | - | Internal |  | New 380/220/132 kV substation with related connections to 380 kV Sandrigo Cordignano and 220 KV Soverzene Scorzè where removing limitations are planned | 380 |  | No EC Regional Group linked | Substation | Planning | Volpago (IT) |  | 800 | New | [5 empty] | 01/01/2020 | Planning | 1/ 1/ 2022 | - | Investment on time
28 | Italy-Montenegro | 3.19.1 |  |  | CGES;TERNA |  |  |  | Italy - Montenegro | Mid-term Project | [12 empty] | 1246 |  | 65 |  |  | 2019
28 | Italy-Montenegro |  | 70 | 70 |  | TERNA | CGES | - | Cross-border |  | New 1200MW HVDC interconnection line between Italy and Montenegro via 475 km 500kV DC subsea cable and converter stations at both ending points. | 500 | DC | North-South (EAST) | Subsea Cable | Under Construction | Villanova (IT) | Lastva (ME) | 1200 | New | Double Circuit | 475 |  | under construction |  | 01/01/2017 | Under Construction | 31/ 12/ 2019 | Works in progress. | Investment on time
28 | Italy-Montenegro |  | 624 | SS 400/110 kV Lastva |  | CGES | - | - | Internal |  | New 400 kV substation Lastva in Montenegro will be connected to the existing line 400kV Podgorica 2(ME)-Trebinje(BA), with two transformers 2X300MVA 400/110kV. This substation will enable secure supply of the Montenegrin coastal network, and connection of the convertor station for the HVDC cable between Montenegro and Italy. | 400 |  | No EC Regional Group linked | Substation | Under Construction | Lastva (ME) |  | 1000 | New |  |  |  | design & permitting |  | 01/01/2015 | Design & Permitting | 1/ 1/ 2016 | The commissioning date has been updated to be coherent with the new schedule of the activities also considering that the construction phase of the substation started in mid 2014 | Rescheduled
29 | Italy-Tunisia |  |  |  | TERNA |  |  |  | Italy - Tunisia | Mid-term Project | [12 empty] | 600 |  | 90 |  |  | 2022
29 | Italy-Tunisia |  | 635 | ITA-7 |  | TERNA | - | - | Cross-border |  | New interconnection between Italy and Tunisia -new DC submarine cable | 500 | DC | No EC Regional Group linked | Subsea Cable | Planning | Sicily Area (IT) | Tunisia node | 600 | New | Double Circuit | 200 |  | under consideration |  | 01/01/2030 | Under Consideration | 31/ 12/ 2022 | - | Investment on time
31 | Italy-Switzerland | PCI 2.15.1 |  |  | SWISSGRID;TERNA |  |  |  | Switzerland - Italy | Mid-term Project | [12 empty] | 995 |  | 100 |  |  | 2022
31 | Italy-Switzerland |  | 642 | ITA-4 |  | TERNA | - | - | Cross-border |  | New interconnection project beetween Italy and Switzerland | 380 | AC | North-South (WEST) | Overhead Line | Design & Permitting | Airolo (CH) | Pallanzeno(IT)-Baggio(IT) | 1000 | New | Double Circuit | 100 |  | under consideration |  | 01/01/2022 | Design & Permitting | 1/ 1/ 2022 | progressed as planned | Investment on time
31 | Italy-Switzerland |  | 914 | 380 kV btw Milano and Brescia |  | TERNA | - | - | Internal |  | Upgrade to 380 kV of part of existing 220 kV Cassano Ric.Ovest | 380 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Cassano (IT) | Chiari (IT) | 500 | New | Single Circuit | 35 |  |  |  | 01/01/2022 | Design & Permitting | 1/ 1/ 2022 | progressed as planned | Investment on time
31 | Italy-Switzerland |  | 932 | Magenta substation |  | TERNA | - | - | Internal |  | new 400 kV section in Magenta substation | 400 |  | North-South (WEST) | Substation | Design & Permitting | Magenta(IT) |  | 1000 | Upgrade | [5 empty] | 01/01/2020 | Design & Permitting | 1/ 1/ 2020 | progressed as planned | Investment on time
33 | Central Northern Italy |  |  |  | TERNA |  |  |  | Italy Center- Italy South | Mid-term Project | [12 empty] | 300 |  | 30 |  |  | 2020
33 | Central Northern Italy |  | 90 | 90 |  | TERNA | - | - | Internal |  | Voltage upgrade of the existing 80km Calenzano-Colunga 220kV OHL to 400kV, providing in and out connection to the existing 220/150kV substation of S. Benedetto del Querceto (which already complies with 400kV standards). | 400 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Calenzano (IT) | Colunga (IT) | 400 | New | Single Circuit | 80 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 1/ 1/ 2022 | delay in the permitting process (EIA) | Delayed
33 | Central Northern Italy |  | 1041 | Rem. lim. in Central Italy |  | TERNA | - | - | Internal |  | Removing limitations on existing 220 kV grid between Villanova e S.Barbara | 220 | AC | No EC Regional Group linked | Overhead Line | Planning | Villanova (IT) | S. Barbara (IT) | 600 | Upgrade | Single Circuit | 350 |  |  |  | 01/01/2020 | Planning | 1/ 1/ 2022 | Additional technical studies on-going. | Delayed
35 | CZ Southwest-east corridor | 3.11.3; 3.11.4; 3.11.5 |  |  | CEPS |  |  |  | Czech - Germany | Long-term Project | [12 empty] | 518 |  | 104 |  |  | 2028
35 | CZ Southwest-east corridor |  | 311 | R Kocin |  | CEPS | - | - | Internal |  | Upgrade of the existing substation 400/110kV; upgrade transformers 2x350MVA. | 400 |  | North-South (EAST) | Substation | Design & Permitting | Kocin (CZ) |  | 500 | New |  |  |  | design & permitting |  | 01/01/2024 | Design & Permitting | 1/ 1/ 2024 | Investment evolution as indicated in previous TYNDP. | Investment on time
35 | CZ Southwest-east corridor |  | 313 | Kocin-Mirovka |  | CEPS | - | - | Internal |  | Connection of 2 existing 400kV substations with double circuit OHL having 120.5km length and a capacity of 2X1700 MVA. | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Kocin (CZ) | Mirovka (CZ) | 500 | New | Double Circuit | 121 |  | planned |  | 01/01/2024 | Design & Permitting | 1/ 1/ 2024 | Investment evolution as indicated in previous TYNDP | Investment on time
35 | CZ Southwest-east corridor |  | 315 | Kocin-Prestice |  | CEPS | - | - | Internal |  | Adding second circuit to existing single circuit line OHL upgrade in length of 115.8km. Target capacity 2x1700 MVA. | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Kocin (CZ) | Prestice (CZ) | 500 | New | Single Circuit | 116 |  | planned |  | 01/01/2028 | Design & Permitting | 1/ 1/ 2028 | Investment evolution as indicated in previous TYNDP. | Investment on time
35 | CZ Southwest-east corridor |  | 316 | Mirovka-Cebin |  | CEPS | - | - | Internal |  | Adding second circuit to existing single circuit line (88.5km, 2x1700 MVA). | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Mirovka (CZ) | Cebin (CZ) | 100 | New | Single Circuit | 89 |  | under consideration |  | 01/01/2028 | Design & Permitting | 1/ 1/ 2029 | Changes on the generation side (in relation to other types of generation) | Rescheduled
36 | Kriegers Flak CGS | PCI 4.1 |  |  | 50HERTZ;Energinet.dk |  |  |  | Denmark-East - Germany | Mid-term Project | [12 empty] | 350 |  | 50 |  |  | 2018
36 | Kriegers Flak CGS |  | 141 | 141 |  | ENERGINET | 50HERTZ | - | Cross-border |  | Three offshore windfarms connected to shore combined with 400 MW interconnection between both countries.New technical solution 220/150 kV; HVDC VSC Converter moved from offshore to shore | 220 | AC | Baltic Energy Market Interconnection Plan | Subsea Cable | Under Construction | Ishøj / Bjæverskov (DK) | Bentwisch (DE) | 400 | New | Single Circuit | 210 |  | planned |  | 01/01/2018 | Design & Permitting | 1/ 1/ 2018 | New design due to result of first tendering process, where the offers exceeded expected prices by far. Second tendering process and construction is ongoing | Investment on time
37 | Norway - Germany, NordLink | 1.8 |  |  | STATNETT;TENNET-DE |  |  |  | Germany - Norway | Mid-term Project | [12 empty] | 1850 |  |  |  |  | 2020
37 | Norway - Germany, NordLink |  | 142 | Norway - Germany HVDC |  | STATNETT | - | - | Cross-border |  | A 514 km 500 kV HVDC subsea interconnector between southern Norway and northern Germany. | 500 | DC | North Seas Countries Offshore Grid Initiative | Subsea Cable | Under Construction | Tonstad (NO) | Wilster (DE) | 1400 | New | Double Circuit | 520 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 01/ 01/ 2020 | Agreement between the two TSOs on commissioning date. | Investment on time
37 | Norway - Germany, NordLink |  | 406 | Western corridor |  | STATNETT | - | - | Internal |  | Voltage uprating of existing 300 kV line Sauda/Saurdal - Lyse - Ertsmyra - Feda - 1&2, Feda - Kristiansand; Sauda-Samnanger in long term. Voltage upgrading of existing single circuit 400kV OHL Tonstad-Solhom-Arendal. Reactive power devices in 400kV substations. | 400 | AC | North Seas Countries Offshore Grid Initiative | Overhead Line | Under Construction | (Southern part of Norway) (NO) | (Southern part of Norway)(NO) | 1000 | Upgrade | Single Circuit | 400 |  | design & permitting |  | 01/01/2020 | Design & Permitting | 2020 | Revised progress due to less flexible system operations in a running system (voltage upgrade of existing lines). Commissioning date expected 2019-2021. | Delayed
39 | DKW-DE, step 3 | 1.4.1 |  |  | Energinet.dk;TENNET-DE |  |  |  | Denmark-West - Germany | Mid-term Project | [12 empty] | 500 |  | 100 |  |  | 2020
39 | DKW-DE, step 3 |  | 144 | Audorf - Kassoe |  | ENERGINET | TENNET-DE | - | Cross-border |  | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity. It consists of a new 400kV route in Denmark and In Germany new 400kV line mainly in the trace of a existing 220kV line. | 400 | AC | North Seas Countries Offshore Grid Initiative | Overhead Line | Permitting | Audorf (DE) | Kassö (DK) | 720 | Upgrade | Double Circuit | 124 |  | under consideration |  | 01/01/2019 | Planning | 31/ 12/ 2020 | step forward from planning to permitting | Investment on time
40 | Luxembourg-Belgium Interco | 2.3.2 |  |  | CREOS; ELIA; AMPRION |  |  |  | Luxembourg - Belgium | Mid-term project | [12 empty] | 140 |  | 35 |  |  | 2022
40 | Luxembourg-Belgium Interco |  | 447 | LUXEMBOURG RING |  | CREOS | - | - | Internal |  | Erection of a new 20km 225kV double-circuit mixed (cable+OHL)line with 1000 MVA capacity in order to create a loop around Luxembourg city including substations for in feed in lower voltage levels. | 220 | AC | North-South (WEST) | Overhead Line | Under Construction | Heisdorf (LU) | Berchem (LU) | 700 | New | Double Circuit | 20 |  | design & permitting |  | 01/01/2017 | Design & Permitting | 1/ 1/ 2017 | Substation Blooren is under construction, line section Heisdorf Blooren is under construction | Investment on time
40 | Luxembourg-Belgium Interco |  | 650 | BELUX Long-Term |  | ELIA | CREOS | AMPRION | Cross-border |  | A 220 kV interconnection between substation Bascharage (CREOS-LU) and substation Aubange (ELIA-BE) is envisioned via a 16km double circuit underground cable with a total capacity of ~1000 MVA. The technical solution, with potential need to add PSTs to the cables, is subject to complementary studies. | 220 | AC | North-South (WEST) | Underground Cable | Under Consideration | Bascharage (LU) | Aubange (BE) | 300 | New | Double Circuit | 16 |  | under consideration |  | 01/01/2020 | Under Consideration | 1/ 1/ 2022 | Robustness of the envisioned reference solution towards the long-term perspective of the energy transition is subject of ongoing studies. | Rescheduled
42 | OWP TenneT Northsea part 1 |  |  |  | TENNET-DE |  |  |  | North-South | Mid-term Project | [12 empty] | 7000 |  | 1000 |  |  | 2017
42 | OWP TenneT Northsea part 1 |  | 160 | Nordergründe |  | TENNET-DE | - | - | Internal |  | New AC-cable connection with a total length of 32km. | 154 | AC | No EC Regional Group linked | Subsea Cable | Under Construction | Offshore- Wind park Nordergründe (DE) | Inhausen (DE) | 111 | New | Single Circuit | 32 |  | design & permitting |  | 01/01/2016 | Under Construction | 1/ 1/ 2016 | on time relative to TYNDP14 | Investment on time
42 | OWP TenneT Northsea part 1 |  | 163 | HelWin1 |  | TENNET-DE | - | - | Internal |  | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 133km. Line capacity&#58; aprox. 576 MW. | 400 | DC | No EC Regional Group linked | Subsea Cable | Commissioned | Cluster HelWin1 (DE) | Büttel (DE) | 576 | New | Single Circuit | 133 |  | under construction |  | 01/01/2014 | Under Construction | 1/ 1/ 2014 | in operation | Investment on time
42 | OWP TenneT Northsea part 1 |  | 164 | SylWin1 |  | TENNET-DE | - | - | Internal |  | New line consisting of underground +subsea cable with a total length of 206 km. Line capacity&#58; aprox.864MW. | 400 | DC | No EC Regional Group linked | Subsea Cable | Commissioned | Cluster SylWin1 (DE) | Büttel (DE) | 864 | New | Single Circuit | 206 |  | under construction |  | 01/01/2015 | Under Construction | 1/ 1/ 2015 | in operation | Investment on time
42 | OWP TenneT Northsea part 1 |  | 165 | DolWin1 |  | TENNET-DE | - | - | Internal |  | New line consisting of underground +subsea cable with a total length of 167 km. Line capacity&#58; 800MW. | 400 | DC | No EC Regional Group linked | Subsea Cable | Commissioned | Cluster DolWin1 (DE) | Dörpen/West (DE) | 800 | New | Single Circuit | 167 |  | under construction |  | 01/01/2014 | Under Construction | 1/ 1/ 2015 | due to the project | Delayed
42 | OWP TenneT Northsea part 1 |  | 166 | Riffgat |  | TENNET-DE | - | - | Internal |  | New AC-cable connection with a total length of 77 km. | 154 | AC | No EC Regional Group linked | Subsea Cable | Commissioned | Offshore Wind park Riffgat (DE) | Emden /Borßum(DE) | 108 | New | Single Circuit | 77 |  | under construction |  | 01/01/2014 | Commissioned | 1/ 1/ 2014 | in operation | Investment on time
42 | OWP TenneT Northsea part 1 |  | 167 | BorWin2 |  | TENNET-DE | - | - | Internal |  | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 205km. Line capacity&#58; 800MW. | 400 | DC | No EC Regional Group linked | Subsea Cable | Commissioned | Cluster BorWin2 (DE) | Diele (DE) | 800 | New | Single Circuit | 205 |  | under construction |  | 01/01/2015 | Under Construction | 1/ 1/ 2015 | in operation | Investment on time
42 | OWP TenneT Northsea part 1 |  | 654 | DolWin2 |  | TENNET-DE | - | - | Internal |  | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 138 km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Construction | Cluster DolWin2 (DE) | Dörpen/West (DE) | 900 | New | Single Circuit | 138 |  | under construction |  | 01/01/2015 | Under Construction | 1/ 1/ 2016 | due to the project | Delayed
42 | OWP TenneT Northsea part 1 |  | 655 | DolWin3 |  | TENNET-DE | - | - | Internal |  | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 162 km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Construction | Cluster DolWin3 (DE) | Dörpen/West (DE) | 900 | New | Single Circuit | 162 |  | design & permitting |  | 01/01/2017 | Under Construction | 1/ 1/ 2017 | on time | Investment on time
42 | OWP TenneT Northsea part 1 |  | 657 | HelWin2 |  | TENNET-DE | - | - | Internal |  | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 133 km. Line capacity&#58; 690 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Commissioned | Cluster HelWin2 | Büttel (DE) | 690 | New | Single Circuit | 133 |  | under construction |  | 01/01/2015 | Under Construction | 1/ 1/ 2015 | on time | Investment on time
47 | Austria - Germany | 3.1.1(Investment 212), 3.1.2(Inv.216) and 2.1(Inv. 219) |  |  | AMPRION;APG;TENNET-DE |  |  |  | Germany - Austria | Mid-term Project | [12 empty] | 1250 |  | 250 |  |  | 2021
47 | Austria - Germany |  | 212 | 212 Isar/Altheim/Ottenhofen - St. Peter |  | TENNET-DE | APG | - | Cross-border |  | New 380kV double circuit OHL Isar/Altheim - St. Peter including new 380kV switchgears Altheim, Pirach, Simbach and St. Peter. | 400 | AC | North-South (EAST) | Overhead Line | Permitting | Isar (DE) | St. Peter (AT) | 2320 | New | Double Circuit | 90 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 1/ 1/ 2020 | Delayed due to long permitting process | Delayed
47 | Austria - Germany |  | 216 | 216 |  | APG | - | - | Internal |  | Completion of the 380kV-line St. Peter - Tauern. This contains an upgrade of the existing 380kV-line St. Peter - Salzburg from 220kV-operation to 380kV-operation and the erection of a new internal double circuit 380kV-line connecting the substations Salzburg and Tauern (replacement of existing 220kV-lines on optimized routes). Moreover the erection of the new substations Wagenham and Pongau and the integration of the substations Salzburg and Kaprun is planned. | 400 | AC | North-South (EAST) | Overhead Line | Permitting | St. Peter (AT) | Tauern (AT) | 1740 | New | Double Circuit | 128 |  | design & permitting |  | 01/01/2020 | Design & Permitting | 1/ 1/ 2021 | Significant delays in the authorisation process (EIA). | Delayed
47 | Austria - Germany |  | 219 | 219 |  | APG | - | - | Internal |  | Upgrade of the existing 220kV-line Westtirol - Zell-Ziller and erection of an additional 220/380kV-Transformer. Line length 105km. | 400 | AC | North-South (WEST) | Overhead Line | Planning | Westtirol (AT) | Zell-Ziller (AT) | 470 | New | Double Circuit | 105 |  | partly under construction |  | 01/01/2021 | Planning | 1/ 1/ 2022 | Tests and gaining of experience for novel technical solution in progress | Rescheduled
47 | Austria - Germany |  | 689 | Vöhringen (DE) - Westtirol (AT) |  | AMPRION | APG | - | Cross-border |  | Upgrade of an existing over head line to 380 kV, extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. Transmission route Vöhringen (DE) -Westtirol (AT). This project will increase the current power exchange capacity between the DE, AT. | 400 | AC | No EC Regional Group linked | Overhead Line | Planning | Vöhringen (DE) | Westtirol (AT) | 585 | Upgrade | Double Circuit | 114 |  | planned |  | 01/01/2020 | Planning | 1/ 1/ 2020 |  | Investment on time
48 | New SK-HU intercon. - phase 1 | 3.16 and 3.17 |  |  | MAVIR;SEPS |  |  |  | Slovakia - Hungary | Mid-term Project | [12 empty] | 82 |  | 8.2 |  |  | 2019
48 | New SK-HU intercon. - phase 1 |  | 214 | 1. SK-HU interconnection |  | SEPS | MAVIR | - | Cross-border |  | New interconnection (new 2x400 kV tie-line) between SK and HU starting from Gabčíkovo substation (SK) to the Gőnyü substation (HU), with one circuit connected to Veľký Ďur substation (SK). Project does not include the erection of new switching station Gabčíkovo next to the existing one. It includes extension of the new Gabčíkovo substation by the two 400 kV bays where the new double line will be connected. | 400 | AC | North-South (EAST) | Overhead Line | Planning | Gabčíkovo (SK) | Gőnyü (HU) | 1000 | New | Double Circuit | 110 |  | under consideration |  | 01/01/2018 | Planning | 31/12/2019 | The approval of the Contract of Construction for each PCI in the project between the two promoters has been in delay compared to the original schedule. The project promoters agreed jointly in November 2015 to set a new feasible commissioning date, which will also figure in the Contract. | Delayed
48 | New SK-HU intercon. - phase 1 |  | 695 | 2. SK-HU interconnection |  | SEPS | MAVIR | - | Cross-border |  | Connection of the two existing substations (R.Sobota (SK) - Sajoóivánka (HU)) by the new 2x400 kV line (preliminary armed only with one circuit on the Hungarian side). | 400 | AC | North-South (EAST) | Overhead Line | Planning | Rimavská Sobota (SK) | Sajóivánka (HU) | 800 | New | Double Circuit | 48 |  | under consideration |  | 01/01/2018 | Planning | 31/12/2019 | The approval of the Contract of Construction for each PCI in the project between the two promoters has been in delay compared to the original schedule. The project promoters agreed jointly in November 2015 to set a new feasible commissioning date, which will also figure in the Contract. | Delayed
48 | New SK-HU intercon. - phase 1 |  | 696 | Hunew 1 |  | MAVIR | - | - | Internal |  | 2x70 Mvar shunt reactors in station Sajóivánka (HU) | 400 |  | North-South (EAST) | Compensation | Planning | Sajóivánka (HU) |  | 800 | New |  |  |  | under consideration |  | 01/01/2018 | Planning | 12/31/2019 | The approval of the Contract of Construction for each PCI in the project between the two promoters has been in delay compared to the original schedule. The project promoters agreed jointly in November 2015 to set a new feasible commissioning date, which will also figure in the Contract. | Delayed
48 | New SK-HU intercon. - phase 1 |  | 697 | Hunew 1 |  | MAVIR | - | - | Internal |  | Second 400/120 kV transformer in station Sajóivánka (HU) | 400 |  | North-South (EAST) | Substation | Planning | Sajóivánka (HU) |  | 800 | Upgrade |  |  |  | under consideration |  | 01/01/2018 | Planning | 12/31/2019 | The approval of the Contract of Construction for each PCI in the project between the two promoters has been in delay compared to the original schedule. The project promoters agreed jointly in November 2015 to set a new feasible commissioning date, which will also figure in the Contract. | Delayed
54 | New SK-HU intercon. - phase 2 | 3.18 |  |  | MAVIR;SEPS |  |  |  | Slovakia - Hungary | Future Project | [12 empty] | 63 |  | 6.3 |  |  | 2029
54 | New SK-HU intercon. - phase 2 |  | 720 | 3. SK-HU interconnection |  | SEPS | MAVIR | - | Cross-border |  | Erection of new 2x400 line between SK and Hungary (substation on Hungarian side still to be defined). The Investment is under consideration. | 400 | AC | North-South (EAST) | Overhead Line | Under Consideration | Veľké Kapušany (SK) | Kisvárda area (HU) | 500 | New | Double Circuit | 40 |  | under consideration |  | 01/01/2021 | Under Consideration | 1/1/2029 | Investment is dependant on the future operation of the SK-UA existing cross-border line, which has been prolongued till around 2030 based on the diagnostics. | Rescheduled
55 | CZ West-East corridor | N/A - the project is not in the PCI list |  |  | CEPS |  |  |  | West-East | Mid-term Project | [12 empty] | 265 |  | 53 |  |  | 2019
55 | CZ West-East corridor |  | 302 | Vyskov-Cechy Stred |  | CEPS | - | - | Internal |  | New second circuit 400kV OHL; Target capacity 2x1730 MVA. | 400 | AC | North-South (EAST) | Overhead Line | Under Construction | Vyskov (CZ) | Cechy Stred (CZ) | 1000 | New | Double Circuit | 98 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2016 | Progress as indicated in TYNDP 2014 | Investment on time
55 | CZ West-East corridor |  | 303 | Babylon-Bezdecin |  | CEPS | - | - | Internal |  | New second circuit 400kV OHL; 1700 MVA. | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Babylon (CZ) | Bezdecin (CZ) | 350 | New | Double Circuit | 54 |  | planned |  | 01/01/2018 | Design & Permitting | 1/ 1/ 2018 | Progress as indicated in TYNDP 2014 | Investment on time
55 | CZ West-East corridor |  | 304 | Babylon-Vyskov |  | CEPS | - | - | Internal |  | New second circuit 400kV OHL; 1700 MVA. | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Babylon (CZ) | Vyskov (CZ) | 750 | New | Double Circuit | 73 |  | planned |  | 01/01/2021 | Design & Permitting | 1/ 1/ 2019 | Rescheduling due to construction phases harmonization of several investments | Ahead of time
62 | Estonia-Latvia 3rd IC | The second PCI list No. 4.2 |  |  | AST;ELERING |  |  |  | Estonia - Latvia | Mid-term Project | [12 empty] | 176 |  | 28 |  |  | 2020
62 | Estonia-Latvia 3rd IC |  | 386 | 3rd EE-LV |  | AST | ELERING | - | Cross-border |  | 330 kV AC OHL between Kilingi-Nõmme substation in Estonia and R-TEC2 substation in Latvia. New 330 kV power transmission line is planned to take route along already existing 110 kV power transmission lines, by constructing both 110 kV and 330 kV lines on the same towers. Under the framework of the project it is planned to reconstruct the open-air switchyard of the 330/110 kV substation „TEC-2” by constructing new open-air connection point for the 330 kV line „Kilingi Nomme-TEC-2”. | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Design & Permitting | Kilingi-Nomme (EE) | R-TEC2 (LV) | 500 | New | Single Circuit | 205 |  | planned |  | 01/01/2020 | Planning | 2020 | Electricty market integration, Security of Supply, RES connection to the transmission network. | Investment on time
62 | Estonia-Latvia 3rd IC |  | 735 | Harku-Sindi 330kV OHL |  | ELERING | - | - | Internal |  | New double circuit OHL with 2 different voltages 330 kV and 110 kV and with capacity 1143 MVA/240 MVA and a length 175 km. Major part of new internal connection will be established on existing right of way on the western part of Estonian mainland.The investment helps together with 3rd EE-LV interconnector to increase interarea capacity up to 600 MW. | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Design & Permitting | Harku (EE) | Sindi (EE) | 600 | New | Double Circuit | 175 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 31/ 12/ 2020 | Planning phase finsished in 2016 | Investment on time
62 | Estonia-Latvia 3rd IC |  | 1062 | RigaCHP2-RigaHPP |  | AST | - | - | Internal |  | Internal reinforcement for 3rd EE-LV interconnectors and significant investment for Baltic Synchronization projetc (ID 170) | 330 | AC | Baltic Energy Market Interconnection Plan | Underground Cable | Under Consideration | RigaCHP2 | RigaHPP | 600 | New | Single Circuit | 10 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2020 | -Security of Supply, Capacity increase through Baltic States by 600 MW | New Investment
69 | East Anglia Cluster |  |  |  | NGT |  |  |  | inside-downstream | Future Project | [12 empty] | 360 |  | 10 |  |  | 2023
69 | East Anglia Cluster |  | 747 | Bramford - Twinstead |  | NGT | - | - | Internal |  | Construction of a new transmission route from Bramford to the Twinstead Tee Point creating Bramford - Pelham and Bramford - Braintree - Rayleigh Main double circuits; the rebuild of Bramford substation and the installation of an MSC at Barking. | 400 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Bramford (GB) | Twinstead (GB) | 1950 | New | Double Circuit | 35 |  | Design & Permitting |  | 01/01/2022 | Design & Permitting | 1/ 1/ 2023 | Delay in project requirement due to generation going back. | Delayed
71 | COBRA cable | 1.5 |  |  | Energinet.dk;TENNET-NL |  |  |  | Denmark-West - Netherlands | Mid-term Project | [12 empty] | 620 |  | 60 |  |  | 2019
71 | COBRA cable |  | 427 | COBRA Cable |  | ENERGINET | TENNET-NL | - | Cross-border |  | COBRA; New single circuit HVDC connection between Jutland and the Netherlands via 350km subsea cable; the DC voltage will be 320kV and the capacity 700MW. | 320 | DC | North Seas Countries Offshore Grid Initiative | Subsea Cable | Under Construction | Endrup (DK) | Eemshaven (NL) | 700 | New | Single Circuit | 350 |  | design & permitting |  | 01/01/2019 | Design & Permitting | 31/03/ 2019 | Permits in place, main contracts signed, construction started. | Investment on time
74 | Thames Estuary Cluster (NEMO) | 1.1 |  |  | ELIA; NGIHL; NGET |  |  |  | Belgium - Great Britain | Mid-term Project | [12 empty] | 800 |  | 100 |  |  | 2019
74 | Thames Estuary Cluster (NEMO) |  | 443 | NEMO |  | ELIA | - | - | Cross-border |  | New DC sea link of 1000 MW over a distance of around 140 km between Richborough (GB) and Gezelle (BE) | 400 | DC | North Seas Countries Offshore Grid Initiative | Subsea Cable | Under Construction | Richborough (GB) | Gezelle (BE) | 1000 | New | Single Circuit | 140 |  | Planned |  | 01/01/2018 | Design & Permitting | 1/ 1/ 2019 | Final Investment Decision has been taken and confirms the target date of technical commissioning end 2018 with commercial operation in 2019. | Investment on time
74 | Thames Estuary Cluster (NEMO) |  | 449 | Richborough - Canterbury |  | NGT | - | - | Internal |  | New 400kV double circuit and new 400kV substation in Richborough connecting the new Belgium interconnector providing greater market coupling between the UK and the European mainland. | 400 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Richborough (GB) | Canterbury (GB) | 1000 | New | Double Circuit | 20 |  | Planned |  | 01/01/2018 | Planning | 1/ 1/ 2018 | Investment on time | Investment on time
74 | Thames Estuary Cluster (NEMO) |  | 450 | SELL - DUNG Reconductoring |  | NGT | - | - | Internal |  | Reconductor the existing circuit which runs from Sellindge - Dungeness with a higher rated conductor. This will facilitate the connection of more interconnectors on the South coast and prevent thermal overloading of this area. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Construction | Sellindge (GB) | Dungeness (GB) | 400 | Upgrade | Double Circuit | 26 |  | Planned |  | 01/01/2015 | Design & Permitting | 1/ 1/ 2016 | Delayed by one year due to interconnector progresion. | Delayed
75 | STEVIN & Modular Offshore Grid |  |  |  | ELIA |  |  |  | Belgium (offshore - inland) | Mid-term Project | [12 empty] | 670 |  | 100 |  |  | 2017
75 | STEVIN & Modular Offshore Grid |  | 444 | STEVIN |  | ELIA | - | - | Internal |  | The STEVIN project extends the 380 kV backbone from the substation Horta (Zomergem) to a new substation Stevin at Zeebrugge. The substation Stevin will be integrated via two 380/150 kV transformers to the existing 150 kV grid at Zeebrugge and will also contain a 220 kV part o facilitate the integration of offshore wind. This new 380 kV corridor will be constructed as a double-circuit (3000 MVA capacity per circuit) overhead line, except for the section of 10 km between two new substations "Van Maerland" & "Gezelle which will be realized as an underground solution via four 380 kV cables. As part of the STEVIN project, the existing 150 kV line between Eeklo Pokmoer and Brugge Waggelwater will be decomissioned and the existing 150kV line between Eeokle Noord and Brugge Waggelwater will be undergrounded. | 380 | AC | North Seas Countries Offshore Grid Initiative | Overhead Line | Under Construction | Horta (BE - Zomergem) | Stevin (BE - Zeebrugge) | 3000 | New | Double Circuit | 50 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 31/12/2017 | State Council procedures no longer pending due to agreements reached with involved stakeholders. Construction phase initiated. | Investment on time
75 | STEVIN & Modular Offshore Grid |  | 752 | Modular Offshore Grid |  | ELIA | - | - | Internal |  | The Modular Offshore Grid envisions the modular creation of the offshore infrastructure for the integration of the wind farms of four offshore wind farms in the Belgian part of the North Sea. The offshore infrastructure would then consist of an offshore hub to centralize the production from these offshore wind farms, and then transport it via 220 kV subsea AC cables to the onshore substation Stevin at Zeebrugge. | 220 | AC | North Seas Countries Offshore Grid Initiative | Subsea Cable | Permitting | Offshore platform(s) | Stevin (Zeebrugge) | 1835 | New | Triple Circuit | 50 |  | planned |  | 01/01/2016 | Design & Permitting | 01/01/2019 | 2019 refers to 1st step in modular construction of an offshore hub. Subject of ongoing alignment with wind farm developers and competent authorities. MOG is presented here into the extent that it would be considered as regulated infrastructure. | Rescheduled
77 | Anglo-Scottish -1 |  |  |  | NGT;SHETL |  |  |  | North-South | Future Project | [12 empty] | 1220 |  |  |  |  | 2017
77 | Anglo-Scottish -1 |  | 452 | Western HVDC Link |  | NGT | - | - | Internal |  | A new 2.4GW (short term rating) submarine HVDC cable route from Hunterston to Deeside with associated AC network reinforcement works at both ends. | 500 | DC | No EC Regional Group linked | Subsea Cable | Under Construction | Hunterston (GB) | Deeside (GB) | 2400 | New | Quadruple Circuit | 360 |  | Design & Permitting |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2017 | Delayed due to complexity in construction and issues with the | Delayed
78 | South West Cluster |  |  |  | NGT |  |  |  | West-East | Future Project | [12 empty] | 814 |  |  |  |  | 2022
78 | South West Cluster |  | 458 | HINP-SEAB New Double Circuit |  | NGT | - | - | Internal |  | New 400kV substation at Hinkley Point. New 400kV transmission route from Hinkley Point to Seabank. Reconstruction of Bridgewater substation for 400kV operation. Uprate Bridgewater - Melksham to 400kV. | 400 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Hinkley Point (GB) | Seabank (GB) | 3200 | New | Double Circuit | 60 |  | design & permitting |  | 01/01/2019 | Design & Permitting | 1/ 1/ 2022 | Based on current the generation connection dates the investment has been rescheduled. | Rescheduled
79 | Wales Cluster |  |  |  | NGT |  |  |  | West-East | Future Project | [12 empty] | 1180 |  | 5 |  |  | 2024
79 | Wales Cluster |  | 769 | WYLF-PEMB HVDC Link |  | NGT | - | - | Internal |  | A new ~2GW submarine HVDC cable route from Wylfa/Irish Sea to Pembroke with associated AC network reinforcement works at both ends. | 500 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Wylfa (GB) | Pembroke (GB) | 2000 | New | Double Circuit | 260 |  | Planned |  | 01/01/2025 | Planning | 1/ 1/ 2024 | Delayed due to anticipated changes in the local generation background. | Investment on time
81 | North South Interconnector | 2.13.1 |  |  | EIRGRID;SONI |  |  |  | Ireland - Northern Ireland | Mid-term Project | [12 empty] | 286 |  |  |  |  | 2019
81 | North South Interconnector |  | 462 | 462 |  | EIRGRID | - | - | Cross-border |  | A new 140 km single circuit 400 kV 1500 MVA OHL from Turleenan 400/275 kV in Northern Ireland to Woodland 400/220 kV in Ireland. This is a new interconnector project between Ireland and Northern Ireland. | 400 | AC | North-South (WEST) | Overhead Line |  | Woodland (IE) | Turleenan (NI) | 0 | New | Single Circuit | 140 |  | design & permitting |  | 01/01/2017 | Design & Permitting |  | Further studies required before re-submission for planning consents | Delayed
82 | RIDP I | 2.13.2 |  |  | EIRGRID;SONI |  |  |  | Ireland - Northern Ireland | Future Project | [12 empty] | 412 |  |  |  |  | 2030
82 | RIDP I |  | 463 | Srananagh - South Donegal |  | EIRGRID | - | - | Internal |  | A new EHV overhead line from Srananagh in Co. Sligo to a new substation in south Co. Donegal | 220 | AC | North-South (WEST) | Overhead Line |  | Srananagh (IE) | New substation in South Donegal (IE) | 500 | New | Single Circuit | 76 |  | under consideration |  | 01/01/2020 | Planning |  | The preferred scheme has been selected since the last TYNDP; this is one of the elements of the preferred scheme. | Investment on time
82 | RIDP I |  | 896 | Omagh South to South Donegal |  | EIRGRID | - | - | Cross-border |  | A new 275 kV cross border link between a new substation in South Donegal in Ireland and a new substation established south of Omagh in Northern Ireland | 275 | AC | North-South (WEST) | Overhead Line |  | South Donegal (IE) | Omagh South (NI) | 500 | New | Single Circuit | 58 |  |  |  | 01/01/2024 | Planning |  | Investment 82.463 of the previous TYNDP described the as then undefined scheme that was the subject of a joint study between NIE and EirGrid. That study has since been completed. This investment is one of a number emerging from the study. | New Investment
82 | RIDP I |  | 897 | Omagh South to Turleenan |  | SONI | - | - | Internal |  | A new 275 kV overhead line from a new substation established south of Omagh to a new 400/275 kV substation, established at Turleenan by the North South Interconnection Development | 275 | AC | North-South (WEST) | Underground Cable |  | Omagh South | Turleenan | 500 | New | Single Circuit | 63 |  |  |  | 01/01/2020 | Planning |  | Investment 82.463 of the previous TYNDP described the as then undefined scheme that was the subject of a joint study between NIE and EirGrid. That study has since been completed. This investment is one of a number emerging from the study. | New Investment
85 | Integration of RES in Alentejo |  |  |  | REN |  |  |  | Internal boundary in Portugal (Alentejo) | Long-term Project | [12 empty] | 70.3 |  | 7 |  |  | 2025
85 | Integration of RES in Alentejo |  | 779 | F.Alentejo-Ourique-Tavira |  | REN | - | - | Internal |  | New 107 km double-circuit 400+150 kV OHL F. Alentejo-Ourique-Tavira. The realization of this connection can take advantage of some already existing 150kV single lines, which can be reconstructed as double circuit line 400+150kV, investments needs the investment which consist of the extension of existing Ourique substation to include 400 kV facilities. | 400 | AC | No EC Regional Group linked | Overhead Line | Planning | F. Alentejo (by Ourique) | Tavira (by Ourique) | 1400 | Upgrade | Double Circuit | 107 |  | planned |  | 01/01/2025 | Planning | 31/ 12/ 2025 | Project on time | Investment on time
85 | Integration of RES in Alentejo |  | 780 | Extension of Ourique |  | REN | - | - | Internal |  | Extension of existing Ourique substation to include 400 kV facilities. | 400 |  | No EC Regional Group linked | Substation | Planning | Ourique (PT) |  | 1400 | Upgrade |  |  |  | planned |  | 01/01/2025 | Planning | 31/ 12/ 2024 | Project on time | Investment on time
86 | East Coast Cluster |  |  |  | NGT |  |  |  | East-West | Future Project | [12 empty] | 3500 |  | 100 |  |  | 2026
86 | East Coast Cluster |  | 781 | East Coast Offshore |  | NGT | - | - | Internal |  | A very high level indication of the works required for GB East Coast. In detail the projects will consist of multiple offshore HVDC and AC circuits and connecting platforms joining to multiple onshore connection points with their own reinforcement requirements. It enables significant connection of offshore windfarms and provides alternative to onshore reinforcment at a cheaper overall cost. | 400 | AC | No EC Regional Group linked | Subsea Cable | Under Consideration | Under Consideration (GB) | Under Consideration (GB) | 3000 | New | Double Circuit | 500 |  | under consideration |  | 01/01/2023 | Under Consideration | 1/ 1/ 2026 | Investment on time | Rescheduled
86 | East Coast Cluster |  | 782 | East Coast Offshore |  | NGT | - | - | Internal |  | Connection of Triton Knoll, Doggerbank & Hornsea GB Wind Farms and all associated works. This is in the region of 11GW of offshore generation. | 400 | AC | No EC Regional Group linked | Subsea Cable | Under Consideration | Under Consideration (GB) | Under Consideration (GB) | 3000 | New | Double Circuit | 500 |  | under consideration |  | 01/01/2020 | Under Consideration | 1/ 1/ 2026 | Rescheduled due to changes in the generation timescales. | Rescheduled
92 | ALEGrO | 2.2 |  |  | AMPRION;ELIA |  |  |  | Belgium - Germany | Mid-term Project | [12 empty] | 560 |  | 35 |  |  | 2020
92 | ALEGrO |  | 146 | ALEGrO |  | ELIA | AMPRION | - | Cross-border |  | Connection between the Oberzier substation in Germany and the Lixhe substation in Belgium via a +-100 km HVDC underground cable, including 2 DC/AC convertor stations to integrate the DC cable with the AC substations at Lixhe & Oberzier. | 320 | DC | North-South (WEST) | Underground Cable | Permitting | Area of Oberzier - Aachen/Düren (DE) | Area of Lixhe - Liège (BE) | 1000 | New | Single Circuit | 94 |  | design & permitting |  | 01/01/2019 | Design & Permitting | 01/ 01/ 2020 | The expected commissioning date of 2020 is based on the hypothesis of acquiring all necessary permits as planned. | Delayed
92 | ALEGrO |  | 1045 | ALEGrO - AC reinforcements in Belgium |  | ELIA | - | - | Internal |  | Internal reinforcements in AC network in BE are needed to integrate Alegro, whilst at the same time contributing to security of supply of Liege and Limburg area by securing infeed from 380kV network. The reinforcements consist of i) installation of a second 380 kV circuit on the existing 380 kV overhead line Lixhe-Herderen (2017). This second circuit will be realized with high performance conductors (HTLS) ii) construction of a 380 kV substation in Lixhe including two 380/220 kV transformers (2017) and one 380/150 kV transformer (2019) | 380 | AC | North-South (WEST) | Overhead Line | Under Construction | Lixhe | Herderen | 1000 | Upgrade | Single Circuit | 10 |  |  |  | 01/01/2017 | Design & Permitting | 01/01/2017 | Progressed as planned. | Investment on time
94 | GerPol Improvements | 3.15 |  |  | 50Hertz; PSE |  |  |  | Poland - Germany | Mid-term Project | [12 empty] | 85 |  |  |  |  | 2018
94 | GerPol Improvements |  | 139 | Krajnik-Vierraden |  | PSE | - | - | Cross-border |  | Upgrade of existing 220 kV line Vierraden-Krajnik to double circuit 400 kV OHL. | 400 | AC | North-South (EAST) | Overhead Line | Under Construction | Vierraden (DE) | Krajnik (PL) | 1200 | New | Double Circuit | 26 |  | design & permitting |  | 01/01/2017 | Design & Permitting | 31/ 12/ 2018 | Finalization of the investment in due date (2017) was not possible because of permit granting reasons (regarding building of the “Uckermark” line) on 50Hertz side. Therefore the schedule for switching off of the existing 220 kV line to 400 kV has been changed. The interconnector will be temporally disconnected until 2018 in order to perform necessary works in the substations Krajnik and Vierraden. In 2018 first two PST in Vierraden will be installed and the line will be connected on 400 kV through a 220/400 kV transformer. The project is planned to operate in final shape (4 PSTs in SS Vierraden and the 2x400 kV interconnector) by 2020, depending on the permit granting process for the “Uckermark” line. | Delayed
94 | GerPol Improvements |  | 796 | Krajnik |  | PSE | - | - | Internal |  | Upgrade of 400/220 kV switchgear in substation Krajnik (new 400/220 kV switchyard). | 400 |  | No EC Regional Group linked | Substation | Design & Permitting | Krajnik (PL) |  | 1200 | New |  |  |  | design & permitting |  | 01/01/2017 | Design & Permitting | 31/12/ 2020 | The commissioning date was adjusted to optimize the planning and development of transmission system. | Rescheduled
94 | GerPol Improvements |  | 799 | PST in Mikułowa |  | PSE | - | - | Cross-border |  | Installation of new Phase Shift Transformer in substation Mikułowa and the upgrade of substation Mikułowa for the purpose of PST installation. | 400 |  | North-South (EAST) | Phase Shift Transformer | Commissioned | Mikułowa (PL) |  | 300 | New |  |  |  | design & permitting |  | 01/01/2015 | Design & Permitting | 30/06/2016 | The PSTs in Mikułowa substation have been constructed in 2015. In first half of 2016 test and trials have been performed. The delay accured due to technical difficulties during starting phase. | Delayed
94 | GerPol Improvements |  | 992 | PST Vierraden |  | 50HERTZ | - | - | Internal |  | Installation of new PSTs in Vierraden | 380 |  | North-South (EAST) | Phase Shift Transformer | Design & Permitting | Vierraden |  | 1200 | New | [5 empty] | 01/01/2016 | Planning | 31/12/2018 | The 380 kV commissioning will be possible after finalization of the new connecting OHL from Vierraden to Neuenhagen (near Berlin) to replace the current 220 kV network and form a new 380 kV grid. | Delayed
96 | Keminmaa-Pyhänselkä |  |  |  | FINGRID |  |  |  | Finland North-South | Long-term Project | [12 empty] | 50 |  | 5 |  |  | 2024
96 | Keminmaa-Pyhänselkä |  | 801 | FI5 KI-PS |  | FINGRID | - | - | Internal |  | Integration of new generation + increased transmission capacity demand. | 400 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Planning | Keminmaa (FI) | Pyhänselkä (FI) | 1000 | New | Single Circuit | 156 |  | under consideration |  | 01/01/2024 | Under Consideration | 1/ 1/ 2024 | Investment progresses as planned, rescheduled slightly since last TYNDP due to expected development on the drivers behind the investment. | Investment on time
103 | Reinforcements Ring NL |  |  |  | TENNET-NL |  |  |  | Netherlands - Germany; Netherlands - Belgium | Long-term Project | [12 empty] | 2500 |  | 500 |  |  | 2027
103 | Reinforcements Ring NL |  | 438 | Noord-West 380 kV |  | TENNET-NL | - | - | Internal |  | New 175-200km AC overhead line with capacity of 2x2650 MVA of 380kV. In the first phase a connection between Eemshaven Oude Schip and Vierverlaten will be built as well as an upgrade of the existing line Diemen - Lelystad - Ens. Last phase of the project expected after 2025. | 380 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Eemshaven (NL) | Diemen (NL) | 125 | New | Double Circuit | 175 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 1/ 1/ 2020 | Changes in plans of thermal plants at Eemshaven offers the opportunity to phase the grid expansions. The a first phase consists of a new 380 kV connection between Eemshaven-Oudeschip and Vierverlaten and the upgrade the circuits form Diemen-Lelystad-Ens. The second phase is a future project and consists of a new 380 kV connection between Vierverlaten and Ens. The second phase of the project expected after 2030. | Investment on time
103 | Reinforcements Ring NL |  | 439 | Zuid-West 380 kV |  | TENNET-NL | - | - | Internal |  | New 100-130km double-circuit 380kV OHL with 2x2650 MVA capacity. Phase 1&#58;2019; phase 2 2025. | 380 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Borssele (NL) | Tilburg (NL) | 125 | New | Double Circuit | 100 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2025 | With a 380 kV substation at Rilland, the Zuid-West 380 kV project can be taken into service in two parts. The first part consists of the Borssele - Rilland line including substation Rilland (2020) and the second part consist of the Rilland – Tilburg line (2025). | Delayed
103 | Reinforcements Ring NL |  | 440 | Randstad380 |  | TENNET-NL | - | - | Internal |  | New 380 kV double-circuit mixed project (OHL+ underground cable) including approximately 20km of underground cable for 2650 MVA. The cable sections are a pilot project. The total length of cable at 380kV is frozen until more experience is gained. | 380 | AC | No EC Regional Group linked | Overhead Line | Under Construction | Maasvlakte (NL) | Beverwijk (NL) | 125 | New | Double Circuit | 65 |  | under construction |  | 01/01/2017 | Under Construction | 1/ 1/ 2019 | The part from Maasvlakte to Bleiswijk has been commisssioned. Phase 2 between Bleiswijk and Beverwijk wll be commissioned in 2019. | Investment on time
103 | Reinforcements Ring NL |  | 441 | Upgrade Dutch Ring |  | TENNET-NL | - | - | Internal |  | Upgrade of the capacity of the existing 300km double circuit 380kV OHL to reach a capacity of 2x2650 MVA along the Dutch Central ring (Hengelo-Zwolle-Ens Diemen-Krimpen-Geertruidenberg-Eindhoven-Maasbracht); First phase 2019; last phase 2025 | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Zwolle (NL) | Maasbracht (NL) | 125 | Upgrade | Double Circuit | 300 |  | under consideration |  | 01/01/2019 | Under Consideration | 1/ 1/ 2030 | Upgrade of the capacity of the existing 300km double circuit 380kV OHL to reach a capacity of 2x2650 MVA along the Dutch Central ring (Hengelo-Zwolle-Ens Diemen-Krimpen-Geertruidenberg-Eindhoven-Maasbracht); First phase (Ens-Zwolle) 2025; last phase 2030 | Investment on time
103 | Reinforcements Ring NL |  | 442 | Upgrade Krimpen - Maasbracht |  | TENNET-NL | - | - | Internal |  |  | 400 | AC | No EC Regional Group linked | Overhead Line | Design | Krimpen aan de IJssel (NL) | Maasbracht (NL) | 100 | Upgrade | Double Circuit | 150 |  | under consideration |  | 01/01/2018 | to be deleted | 01-01-2027 | Upgrade of Krimpen-Geertruidenberg is expected in 2023, Geertruidenberg-Maasbracht completed in 2027. | Investment on time
107 | Celtic Interconnector | PCI label 1.6 |  |  | EIRGRID;RTE |  |  |  | France - Ireland | Long-term Project | [12 empty] | 920 |  | 150 |  |  | 2025
107 | Celtic Interconnector |  | 810 | France Ireland Interconnector |  | EIRGRID | RTE | - | Cross-border |  | A new HVDC subsea connection between Ireland and France | 320 | DC | North Seas Countries Offshore Grid Initiative | Subsea Cable | Under Consideration | West Wexford or East Cork (IE) | La Martyre (FR) | 700 | New | Single Circuit | 500 |  | under consideration |  | 01/01/2025 | Under Consideration | 2026 | The project is now starting the Initial Design and Pre-consultation Phase Feasibility Study resulted in minor commissioning postponement. | Rescheduled
110 | Norway-Great Britain North Sea Link | 1.10 |  |  | NGIHL;STATNETT |  |  |  | Great Britain Norway | Mid-term Project | [12 empty] | 1850 |  |  |  |  | 2021
110 | Norway-Great Britain North Sea Link |  | 424 | Norway - Great Britain |  | STATNETT | - | - | Cross-border |  | A 720 km long 500 kV 1400 MW HVDC subsea interconnector between western Norway and eastern England. | 500 | DC | North Seas Countries Offshore Grid Initiative | Subsea Cable | Under Construction | Kvilldal (NO) | Blythe (GB) | 0 | New | Double Circuit | 720 |  | design & permitting |  | 01/01/2020 | Design & Permitting | 2021 | On time | Investment on time
111 | 3rd AC Finland-Sweden north |  |  |  | FINGRID;SVK |  |  |  | Finland - Sweden | Long-term Project | [12 empty] | 130 |  | 15 |  |  | 2025
111 | 3rd AC Finland-Sweden north |  | 396 | 3rd AC Finland-Sweden north |  | SVK | FINGRID | - | Cross-border |  | Third AC 400 kV overhead line interconnector between Finland north and Sweden SE1. Strengthening the AC connection between Finland and Sweden is necessary due to new wind power generation, larger conventional units and decomissioning of the existing 220 kV interconnector. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Finland North (FI) | Sweden bidding area SE1/SE2 | 800 | New | Single Circuit | 200 |  | under consideration |  | 01/01/2025 | Under Consideration | 2025 |  | Investment on time
113 | Doetinchem - Niederrhein | 2.12 |  |  | AMPRION;TENNET-NL |  |  |  | Netherlands - Germany | Mid-term Project | [12 empty] | 220 |  | 30 |  |  | 2017
113 | Doetinchem - Niederrhein |  | 145 | Doetinchem-Niederrhein |  | TENNET-NL | AMPRION | - | Cross-border |  | New 400kV line double circuit DE-NL interconnection line. | 400 | AC | North-South (WEST) | Overhead Line | Under Construction | Niederrhein (DE) | Doetinchem (NL) | 1500 | New | Double Circuit | 57 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2017 | New 400kV line double circuit DE-NL interconnection line, to facilitate the market. | Investment on time
120 | 2nd Offshore-Onshore Corridor (Belgium) |  |  |  | ELIA |  |  |  | Belgium (offshore - inland) | Future Project | [12 empty] | 1100 |  | 300 |  |  | 2025
120 | 2nd Offshore-Onshore Corridor (Belgium) |  | 933 | Complementary connection |  | ELIA | - | - | Internal |  | To integrate the full potential of 4 GW, additional solutions are needed on top op the 1 GW connection to the Antwerp area. This could take the form of a complementary connection towards Izegem or Brussels, as well as a larger dimensioning of the connection to the Antwerp area.Subject to further studies. | 380 | AC | North Seas Countries Offshore Grid Initiative | Underground Cable | Under Consideration | Offshore Hub OR Stevin - TBD | Antwerp Area OR Izegem - TBD | 1800 | New | Double Circuit | 100 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2025 | Long-term potential of energy transition&#58; additional offshore-onshore corridor needed in order to evacuate up to 4GW of offshore wind in the Belgian part of the North Sea. | Investment on time
120 | 2nd Offshore-Onshore Corridor (Belgium) |  | 1053 | 1 GW to Antwerp area |  | ELIA | - | - | Internal |  | To evacuate up to 3.3 GW wind, thus 1 GW more than currenlty planned, preliminary studies indicated that this corridor could consists of a 1 GW DC connection from an offshore platform or nearby Stevin substation in Zeebrugge towards the Antwerp Area (substation Doel could be a possible location). Subject to further studies. | 320 | DC | North Seas Countries Offshore Grid Initiative | Underground Cable | Under Consideration | Offshore Hub OR Stevin - TBD | Doel (BE) - TBD | 1000 | New | Single Circuit | 100 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2025 | Long-term potential of energy transition&#58; additional offshore-onshore corridor needed in order to evacuate up to 4GW of offshore wind in the Belgian part of the North Sea. | Investment on time
121 | 2nd interconnector Belgium - UK |  |  |  | ELIA |  |  |  | Belgium - Great Britain | Future Project | [12 empty] | 700 |  | 150 |  |  | 2025
121 | 2nd interconnector Belgium - UK |  | 934 | 2nd interco UK - BE |  | ELIA | - | - | Cross-border |  | This investment item envisions the possibility of a second 1GW HVDC connection, between UK (Kemsley) and a Belgian 380kV substation further inland in the Antwerp area (Doel, Zandvliet are indicative locations). Subject to further studies. | 400 | DC | North Seas Countries Offshore Grid Initiative | Subsea Cable | Under Consideration | Kemsley (UK) for example - TBD | Doel/Zandvliet (BE) for example - TBD | 1000 | New | Single Circuit | 250 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2025 | Preliminary studies have indicated potential for further regional welfare & RES integration increase by further increasing the interconnection capacity between Belgium & UK. | Investment on time
123 | LitPol Link Stage 2 | 4.5 |  |  | Litgrid; PSE |  |  |  | Poland - Lithuania | Mid-term Project | [12 empty] | 335 |  |  |  |  | 2021
123 | LitPol Link Stage 2 |  | 335 | Ostrołęka-Olsztyn Mątki |  | PSE | - | - | Internal |  | Existing 220 kV single circuit line of 139 km between Ostrołęka and Olsztyn Mątki will be upgraded to 400 kV AC double circuit OHL with capacity of 2x1870 MVA. After dismantling of 220 kV line Ostrołęka - Olsztyn the one circuit Ostrołęka - Olsztyn Mątki will be temporarily switched on 220kV and connected to Olsztyn substation. | 400 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Design & Permitting | Ostrołęka (PL) | Olsztyn Mątki (PL) | 500 | New | Double Circuit | 138 |  | design & permitting |  | 01/01/2017 | Design & Permitting | 1/ 1/ 2018 | Delay due to lingering permit granting process and other formal aspects. | Delayed
123 | LitPol Link Stage 2 |  | 373 | Ostrołęka-Stanisławów |  | PSE | - | - | Internal |  | Construction of new 400 kV AC double-circuit OHL line with a length of 108 km and capacity of 2x1870 MVA between Ostrołęka and Stanisławów will partly use route existing 220 kV single-circuit line between Ostrołęka and Miłosna. In one circuit of 400 kV line will be enabled substation Wyszków. After the construction of 400 kV line, the 220 kV line will be dismantled. Expansion of 400 kV Ostrołęka substation and construction of a new 400 kV substation Stanisławów, which will be connected by splitting and extending of 400 kV lines Miłosna - Narew and Miłosna - Siedlce. | 400 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Design & Permitting | Ostrołęka (PL) | Stanisławów (PL) | 500 | New | Double Circuit | 106 |  | design & permitting |  | 01/01/2020 | Design & Permitting | 31/ 12/ 2021 | The investment is in tendering procedure, the contract (design and build scheme) will by signed by Q4 2015. | Investment on time
123 | LitPol Link Stage 2 |  | 374 | Kozienice-Siedlce Ujrzanów |  | PSE | - | - | Internal |  | Existing 220 kV single circuit OHL between Kozienice and Siedlce Ujrzanów will be upgraded to AC 400 kV double circuit line (OHL) with a length of 90 km and a capacity of 2x1870 MVA (onshore). The Kozienice substation will be upgraded to connect the new lines. | 400 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Design & Permitting | Kozienice (PL) | Siedlce Ujrzanów (PL) | 300 | New | Double Circuit | 90 |  | design & permitting |  | 01/01/2019 | Design & Permitting | 1/ 1/ 2019 | Investment on time. | Investment on time
123 | LitPol Link Stage 2 |  | 1038 | Back-to-back in Alytus |  | LITGRID | - | - | Internal |  | Construction of the second 500 MW Back-to-Back converter station in Alytus (LT). | 400 |  | Baltic Energy Market Interconnection Plan | LCC converter station | Planning | Alytus |  | 500 | New | [5 empty] | 01/01/2020 | Planning | 31/12/2020 | No change of status. | Investment on time
124 | NordBalt phase 2 | 4.4.2 |  |  | AST;LITGRID;SVK |  |  |  | Lithuania - Sweden | Long-term Project | [12 empty] | 294 |  | 30 |  |  | 2023
124 | NordBalt phase 2 |  | 378 | 330 kV Panevezys-Musa |  | LITGRID | - | - | Internal |  | New single circuit 330kV OHL (1080 MVA, 80km). | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Planning | Panevezys (LT) | Musa (LT) | 150 | New | Single Circuit | 80 |  | planned |  | 01/01/2022 | Planning | 31/12/ 2023 | Project implementation depends on decisions about new nuclear power plant in Lithuania and project 170."Baltic synchronisation". | Delayed
124 | NordBalt phase 2 |  | 385 | Grobina (LV) - Imanta (LV) |  | AST | - | - | Internal |  | The reinforcement for Latvian grid project with the new 330kV OHL construction and connection to the Riga node. New 330kV OHL construction mainly instead of the existing 110kV double circuit line route, 110kV line will be renovated at the same time and both will be assembled on the same towers. Length 380km, Capacity 800MW | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Under Construction | Grobina (LV) | Imanta (LV) | 150 | New | Double Circuit | 380 |  | design & permitting |  | 01/01/2018 | Under Construction | 2019 | The last part of reinforcement for Kurzemes ring project | Delayed
124 | NordBalt phase 2 |  | 733 | Ekhyddan-Nybro-Hemsjö |  | SVK | - | - | Internal |  | Second phase includes the internal network reinforcements in Sweden to be able to fully utilize the interconnector between Lithuania and Sweden. | 400 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Design & Permitting | Ekhyddan (SE) | Nybro/Hemsjö (SE) | 700 | New | Single Circuit | 160 |  | under consideration |  | 01/01/2023 | Planning | 2023 | Commissioning date is current estimation | Rescheduled
126 | SE North-south reinforcements |  |  |  | SVK |  |  |  | North-South | Long-term Project | [12 empty] | 400 |  | 80 |  |  | 2025
126 | SE North-south reinforcements |  | 403 | Reinforcements SE2-3 in Sweden |  | SVK | - | - | Internal |  | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. The need for capacity is driven by RES integration in northern Sweden and nuclear decommission in southern Sweden. | 400 |  | No EC Regional Group linked | Compensation | Under Consideration | Sweden bidding area SE2 | Sweden bidding area SE3 | 1500 | New | Single Circuit | 900 |  | under consideration |  | 01/01/2025 | Under Consideration | 2025 | The investment now combine new investments in various reactive compensation components and other reinforcements not yet specified. | Investment on time
127 | Central Southern Italy |  |  |  | TERNA |  |  |  | Italy South - Italy Center | Mid-term Project | [12 empty] | 530 |  | 53 |  |  | 2019
127 | Central Southern Italy |  | 86 | 86 |  | TERNA | - | - | Internal |  | New 178km double circuit 400kV OHL between existing Foggia and Villanova 400kV substations, also connected in and out to the Larino and Gissi substations. | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Foggia (IT) | Villanova (IT) | 600 | New | Double Circuit | 178 |  | design & permitting |  | 01/01/2019 | Design & Permitting | 1/ 1/ 2022 | the part Foggia-Gissi still under authorization; the part Villanova Gissi has been commissioned in 2016. | Delayed
127 | Central Southern Italy |  | 91 | 91 |  | TERNA | - | - | Internal |  | Upgrade of the existing 85km Foggia-Benevento II 400kV OHL. | 400 | AC | No EC Regional Group linked | Overhead Line | Commissioned | Foggia (IT) | Benevento II (IT) | 250 | New | Single Circuit | 85 |  | under construction |  | 01/01/2014 | Under Construction | 30/ 06/ 2014 | - | Investment on time
127 | Central Southern Italy |  | 96 | 96 |  | TERNA | - | - | Internal |  | New 30km single circuit 400kV OHL between the future substations of Deliceto and Bisaccia, in the Candela area. | 400 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Deliceto (IT) | Bisaccia (IT) | 400 | New | Single Circuit | 30 |  | design & permitting |  | 01/01/2017 | Design & Permitting | 31/ 12/ 2022 | delay in the permitting process (EIA) | Delayed
127 | Central Southern Italy |  | 645 | ITA-3 |  | TERNA | - | - | Internal |  | New 400kV OHL between the existing substations of Laino and Altomonte in Calabria. | 400 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Laino (IT) | Altomonte (IT) | 250 | New | Quadruple Circuit | 50 |  | partly under construction, design & permitting |  | 01/01/2017 | Design & Permitting | 1/ 1/ 2022 | delay in the permitting process (EIA) | Delayed
129 | OWP Northsea TenneT Part 4 |  |  |  | TENNET-DE |  |  |  | inside-DE | Future Project | [12 empty] | 7000 |  | 1000 |  |  | 2031
129 | OWP Northsea TenneT Part 4 |  | 658 | BorWin4 |  | TENNET-DE | - | - | Internal |  | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 180 km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Cluster BorWin4 (DE) | area of Cloppenburg/East | 900 | New | Single Circuit | 180 |  | under consideration |  | 01/01/2019 | Design & Permitting | 1/ 1/ 2029 |  | Investment on time
129 | OWP Northsea TenneT Part 4 |  | 943 | NOR-9-1 |  | TENNET-DE | - | - | Internal |  | Connection of new offshore wind park. New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 255 km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | NOR-9-1 | area of Unterweser | 900 | New | Single Circuit | 255 |  |  |  | 01/01/2028 | Under Consideration | 1/ 1/ 2035 | due to new planning | Rescheduled
129 | OWP Northsea TenneT Part 4 |  | 946 | NOR-11-1 |  | TENNET-DE | - | - | Internal |  | Connection of new offshore wind parks. New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 230km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | NOR-11-1 | area of Wilhelmshaven | 900 | New | Single Circuit | 230 |  |  |  | 01/01/2026 | Under Consideration | 1/ 1/ 2032 |  | Rescheduled
129 | OWP Northsea TenneT Part 4 |  | 948 | NOR-12-1 |  | TENNET-DE | - | - | Internal |  | Connection of new offshore wind parks. New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 240km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | NOR-12-1 | area of Wilhelmshafen | 900 | New | Single Circuit | 240 |  |  |  | 01/01/2027 | Under Consideration | 1/ 1/ 2034 |  | Rescheduled
129 | OWP Northsea TenneT Part 4 |  | 950 | NOR-13-1 |  | TENNET-DE | - | - | Internal |  | Connection of new offshore wind parks. New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 330km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | NOR-13-1 | Kreis Segeberg | 900 | New | Single Circuit | 330 |  |  |  | 01/01/2025 | Under Consideration | 1/ 1/ 2031 |  | Rescheduled
130 | HVDC Wolmirstedt to area Isar | 3.12 |  |  | 50HERTZ;TENNET-DE |  |  |  | Internal Project | Mid-term Project | [12 empty] | 2800 |  | 400
130 | HVDC Wolmirstedt to area Isar |  | 665 | Wolmirstedt-Isar |  | TENNET-DE | 50HERTZ | - | Internal |  | New DC- lines to integrate new wind generation from control area 50Hertz especially Mecklenburg-Vorpommern, Brandenburg and Sachsen-Anhalt towards Central/south Europe for consumption and storage. Due to ongoing political discussions a change of the connection point Gundremmingen is under consideration. | 500 | DC | North-South (EAST) | Overhead Line | Planning | Wolmistedt (DE) | Isar (DE) | 3583 | New | Double Circuit | 450 |  | under consideration |  | 01/01/2022 | Planning | 1/ 1/ 2025 | The commissioning date of the investment is delayed due to new preference of underground cable instead of overhead lines by german legal requirement. | Delayed
132 | RES-Integration in North-West Germany 2 |  |  |  | AMPRION;TENNET-DE |  |  |  | Internal Project | Long-term Project | [12 empty] | 1680 |  | 200 |  |  | 2025
132 | RES-Integration in North-West Germany 2 |  | 661 | HVDC Line A-North |  | AMPRION | - | - | Internal |  | New HVDC-lines from Emden to Osterath to integrate new wind generation especially from North Sea towards Central Germany for consumption. | 400 | DC | No EC Regional Group linked | Overhead Line | Planning | Emden East (DE) | Osterath (DE) | 3049 | New | Single Circuit | 320 |  | under consideration |  | 01/01/2022 | Planning | 1/ 1/ 2025 | The commissioning date of the investment has been rescheduled due to the postponement of the development of offshore windfarms in the North Sea. | Rescheduled
132 | RES-Integration in North-West Germany 2 |  | 663 | Cloppenburg East - Merzen |  | AMPRION | TENNET-DE | - | Internal |  | New 380-kV double circuit over-head-line Cloppenburg East - Merzen with a total length of ca. 55 km. New errection of a 380-kV substation Merzen. | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Cloppenburg East (DE) | Merzen (DE) | 3386 | New | Double Circuit | 55 |  | under consideration |  | 01/01/2022 | Planning | 1/ 1/ 2022 |  | Investment on time
132 | RES-Integration in North-West Germany 2 |  | 666 | Conneforde - Cloppenburg East |  | TENNET-DE | - | - | Internal |  | New 380-kV-line in existing OHL corridor for integration of on- and offshore Wind generation. Incl. new 380-kV-switchgear in Cloppenburg and new transformers in Cloppenburg | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Conneforde (DE) | Cloppenburg (DE) | 3386 | New | Double Circuit | 60 |  | under consideration |  | 01/01/2022 | Planning | 1/ 1/ 2022 |  | Investment on time
133 | Longterm RES-Integration in Germany |  |  |  | 50HERTZ;AMPRION;TENNET-DE;TRANSNET-BW |  |  |  | Internal Project | Future Project | [12 empty] | 20000 |  | 5000 |  |  | >2030
133 | Longterm RES-Integration in Germany |  | 662 | HVDC Line B |  | AMPRION | - | - | Internal |  | New lines in HVDC technology from Wehrendorf to Urberach to integrate new wind generation especially from North Sea towards Central-South Europe for consumption and storage. | 400 | DC | No EC Regional Group linked | Overhead Line | Under Consideration | Wehrendorf (DE) | Urberach (DE) | 2000 | New | Single Circuit | 380 |  | under consideration |  | 01/01/2022 | Under Consideration | >2030 | The need for this long-term investment was not confirmed by the regulatory authority within the national grid development plan 2014. Therefore the project has been rescheduled and further studies on this project are ongoing. | Rescheduled
133 | Longterm RES-Integration in Germany |  | 956 | further HCDC connections C |  | TENNET-DE | - | - | Internal |  | new DC- line in HVDC technology to integrate new wind generation from northern Germany toward soutern Germany and southern Europe for consumption and storage. Connections points north&#58; Brunsbüttel, Wilster, Kreis Segeberg, Stade, Alfsted. South&#58; Großgartach, Goldshöfe, Raitersaich, Vöhringen | 500 | DC | No EC Regional Group linked | Overhead Line | Under Consideration | Schleswig-Hostein | Baden-Würtemberg / Bavaria | 8000 | New | Double Circuit | 770 |  |  |  | 01/01/2030 | Under Consideration | >2030 |  | Investment on time
133 | Longterm RES-Integration in Germany |  | 958 | DC Güstrow - Area Isar |  | 50HERTZ | TENNET-DE | - | Internal |  | New DC- lines to integrate new wind generation from Baltic Sea and control area 50Hertz especially Mecklenburg-Vorpommern towards Central/south Europe for consumption and storage. | 500 | DC | North-South (EAST) | Overhead Line | Under Consideration | Güstrow (DE) | Area of Isar (DE) | 2000 | New | Single Circuit | 770 |  |  |  | 01/01/2034 | Under Consideration | >2030 |  | Investment on time
133 | Longterm RES-Integration in Germany |  | 969 | further HVDC connections A |  | AMPRION | - | - | Internal |  | New HVDC line to integrate new wind gerneration especially from North Sea towards Central Germany for consumption and storage. connections points north&#58; Emden, Conneforde. South&#58; Oberzier, Rommerskirchen | 500 | DC | No EC Regional Group linked | Overhead Line | Under Consideration | Lower Saxony | North Rhine-Westphalia | 4000 | New | Double Circuit | 360 |  |  |  | 01/01/2030 | Under Consideration | >2030 |  | Investment on time
133 | Longterm RES-Integration in Germany |  | 970 | further HVDC connections B |  | AMPRION | TENNET-DE | - | Internal |  | New HVDC line to integrate new wind gerneration especially from North Sea towards South Germany for consumption and storage. Connectionspoints north: Cloppenburg, Elsfelth/West. South: Bürstadt, Philipsburg | 500 | DC | No EC Regional Group linked | Overhead Line | Under Consideration | Lower Saxony | Hesse/Baden-Würtemberg | 4000 | New | Double Circuit | 500 |  |  |  | 01/01/2030 | Under Consideration | >2030 |  | Investment on time
134 | Grid Reinforcements in South-West Germany |  |  |  | AMPRION;TRANSNET-BW |  |  |  | Internal Project | Mid-term Project | [12 empty] | 890 |  | 130 |  |  | 2021
134 | Grid Reinforcements in South-West Germany |  | 176 | Daxlanden-Eichstetten |  | TRANSNET-BW | - | - | Internal |  | This AC project is necessary in order to evacuate the energy arriving from HVDC corridors towards southern Germany and reinforce the interconnection capacity with Switzerland | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Daxlanden (DE) | Eichstetten (DE) | 754 | Upgrade | Double Circuit | 120 |  | under consideration |  | 01/01/2020 | Under Consideration | 1/ 1/ 2021 | No significant change | Rescheduled
134 | Grid Reinforcements in South-West Germany |  | 680 | Urberach - Daxlanden |  | AMPRION | TRANSNET-BW | - | Internal |  | New line and extension of existing line to 380 kV double circuit overhead line Urberach - Weinheim - Daxlanden. Extension of existing substations are included. | 400 | AC | No EC Regional Group linked | Overhead Line | Planning | Urberach (DE) | Daxlanden (DE) | 1833 | New | Double Circuit | 219 |  | under consideration |  | 01/01/2021 | Planning | 1/ 1/ 2022 | Commissioning is planned for the end of 2021 / beginning of 2022. Therefore, the commissioning date is set to 2022. | Investment on time
135 | Grid Reinforcements in Western Germany |  |  |  | AMPRION |  |  |  | Internal Project | Mid-term Project | [12 empty] | 900 |  | 135 |  |  | 2022
135 | Grid Reinforcements in Western Germany |  | 179 | Rommerskirchen - Weißenthurm |  | AMPRION | - | - | Internal |  | New380 kV overhead line in existing route. Extension and erection of substations incl. erection of 380/110kV-transformers. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Construction | Rommerskirchen (DE) | Weißenthurm (DE) | 900 | New | Double Circuit | 94 |  | under construction/design & permitting |  | 01/01/2017 | Under Construction | 1/ 1/ 2019 | The section Rommerskrichen to Sechtem is delayed because the permitting procedures take longer than planned. The 36 km section from Sechtem to Weißenturm is already commissioned. | Delayed
135 | Grid Reinforcements in Western Germany |  | 188 | Kruckel - Dauersberg |  | AMPRION | - | - | Internal |  | New 380 kV over head lines in existing rout. Extension of existing and erection of several 380/110kV-substations. | 380 | AC | No EC Regional Group linked | Overhead Line | Permitting | Kruckel (DE) | Dauersberg (DE) | 774 | New | Double Circuit | 110 |  | planned |  | 01/01/2020 | Design & Permitting | 1/ 1/ 2021 | Delay due to long permitting process | Delayed
136 | CSE1 |  |  |  | HOPS;NOS-BIH |  |  |  | Croatia – Bosnia and Herzegovina | Mid-term Project | [12 empty] | 173 |  | 20 |  |  | 2022
136 | CSE1 |  | 227 | OHL 400 kV Banja Luka - Lika |  | HOPS | NOS-BIH | - | Cross-border |  | New 400kV interconnection line between BA and HR | 400 | AC | North-South (EAST) | Overhead Line | Under Consideration | Banja Luka (BA) | Lika (HR) | 504 | New | Single Circuit | 155 |  | under consideration |  | 01/01/2021 | Under Consideration | 1/ 1/ 2030 | Feasibility study is expected to be launched. | Rescheduled
136 | CSE1 |  | 617 | OHL 400 kV Lika - Brinje |  | HOPS | - | - | Internal |  | New 55 km single circuit 400 kV OHL replacing aging 220 kV overhead line | 400 | AC | North-South (EAST) | Overhead Line | Under Consideration | Lika(HR) | Brinje(HR) | 215 | Upgrade | Single Circuit | 55 |  | planned |  | 01/01/2020 | Planning | 1/ 1/ 2025 | Feasibility study is expected to be launched. | Rescheduled
136 | CSE1 |  | 618 | OHL 400 kV Lika - Velebit |  | HOPS | - | - | Internal |  | New 60 km single circuit 400 kV OHL replacing aging 220 kV overhead line | 400 | AC | North-South (EAST) | Overhead Line | Under Consideration | Lika(HR) | Velebit(HR) | 215 | Upgrade | Single Circuit | 60 |  | planned |  | 01/01/2020 | Planning | 1/ 1/ 2025 | Feasibility study is expected to be launched. | Rescheduled
136 | CSE1 |  | 619 | Substation 400/110 kV Lika |  | HOPS | - | - | Internal |  | New 400/110 kV substation, 2x300 MVA | 400 |  | North-South (EAST) | Substation | Under Consideration | Lika (HR) |  | 215 | New |  |  |  | planned |  | 01/01/2018 | Planning | 1/ 1/ 2027 | Feasibility study is expected to be launched. | Rescheduled
136 | CSE1 |  | 620 | Substation 400/220 kV Brinje |  | HOPS | - | - | Internal |  | New 400/220 kV substation, 1x400 MVA | 400 |  | North-South (EAST) | Substation | Under Consideration | Brinje (HR) |  | 215 | New |  |  |  | planned |  | 01/01/2020 | Planning | 1/ 1/ 2025 | Feasibility study is expected to be launched. | Rescheduled
136 | CSE1 |  | 633 | OHL 400 kV Konjsko - Velebit |  | HOPS | - | - | Internal |  | New 100km single circuit 400 kV OHL replacing ageing 220 kV overhead line | 400 | AC | North-South (EAST) | Overhead Line | Under Consideration | Konjsko(HR) | Velebit(HR) | 215 | Upgrade | Single Circuit | 100 |  | planned |  | 01/01/2020 | Planning | 1/ 1/ 2025 | Feasibility study is expected to be launched. | Rescheduled
138 | Black Sea Corridor | 3.8 |  |  | TRANSELECTRICA, ESO-EAD |  |  |  | North-South | Mid-term Project | [12 empty] | 298 |  | 40 |  |  | 2023
138 | Black Sea Corridor |  | 273 | 400kV OHL Cernavoda-Stalpu |  | TRANSELECTRICA | - | - | Internal |  | Reinforcement of the cross-section between the Western coast of the Black Sea (Eastern Romania) and the rest of the system. New 400kV double circuit OHL between existing substations Cernavoda and Stalpu, with 1 circuit derivation in/out in 400 kV substation Gura Ialomitei,situated in the vicinity of the new line. Line length 159km,2x1380 MVA. | 400 | AC | North-South (EAST) | Overhead Line | Permitting | Cernavoda (RO) | Stalpu (RO) | 808 | New | Double Circuit | 159 |  | planned |  | 01/01/2019 | Design & Permitting | 31/ 12/ 2020 | Longer than expected delay regarding clarification of legal framework for right of land acquirement and regarding environmental permitting procedure. | Delayed
138 | Black Sea Corridor |  | 275 | 400 kV OHL Smardan-Gutinas |  | TRANSELECTRICA | - | - | Internal |  | Reinforcement of the cross-section between the Western coast of the Black Sea (Dobrogea area) and the rest of the system. New 400kV double circuit OHL (one circuit wired) between existing substations. Line length 140km; 1380 MVA. | 400 | AC | North-South (EAST) | Overhead Line | Permitting | Smardan (RO) | Gutinas (RO) | 560 | New | Double Circuit | 140 |  | planned |  | 01/01/2020 | Design & Permitting | 28/ 02/ 2020 | Rapid increase of wind generation connected in the area. Efforts to be made to speed construction. | Investment on time
138 | Black Sea Corridor |  | 276 | 400 kV OHL Gadalin - Suceava |  | TRANSELECTRICA | - | - | Internal |  | Reinforcement of the cross-section between developing wind generation hub in Eastern Romania and the rest of the system. New 400kV simple circuit OHL between existing substations. Line length 260km, 1204 MVA. | 400 | AC | North-South (EAST) | Overhead Line | Permitting | Gadalin (RO) | Suceava (RO) | 165 | New | Single Circuit | 260 |  | planned |  | 01/01/2021 | Design & Permitting | 31/ 12/ 2023 | Longer than expected delay regarding clarification of legal framework for right of land acquirement and regarding environmental permitting procedure. | Delayed
138 | Black Sea Corridor |  | 715 | 220kV Stalpu substation upgrade to 400 kV |  | TRANSELECTRICA | - | - | Internal |  | To reinforce the cross-section between the Black Sea coast wind generation in Romania and Bulgaria and the consumption and storage centers to the West, the 220 kV OHL Stalpu-Teleajen-Brazi is upgraded to 400 kV, as a continuation of the 400 kV d.c. OHL Cernavoda-Stalpu. The 220/110 kV substation Stalpu is upgraded to 400/110kV (1x250MVA). | 400 |  | North-South (EAST) | Substation | Permitting | Stalpu (RO) | Stalpu (RO) | 808 | Upgrade |  |  |  | planned |  | 01/01/2019 | Planning | 31/ 12/ 2020 | This project is complementing with project 273. | Delayed
138 | Black Sea Corridor |  | 800 | 400 kV OHL Varna-Burgas |  | ESO | - | - | Internal |  | New 140km single circuit 400kV OHL in parallel to the existing one. | 400 | AC | North-South (EAST) | Overhead Line | Planning | Varna(BG) | Burgas(BG) | 165 | New | Single Circuit | 140 |  | planned |  | 01/01/2018 | Planning | 1/ 1/ 2020 | Delayed due to lack of funding. | Delayed
141 | Slovenia-Hungary corridor | 3.9 |  |  | ELES;MAVIR |  |  |  | Hungary - Slovenia | Mid-term Project | [12 empty] | 345
141 | Slovenia-Hungary corridor |  | 223 | 223 |  | ELES | - | - | Cross-border |  | A new 400 kV substation of Cirkovce(SI) will be connected to one circuit of the existing Heviz(HU) -Zerjavinec(HR) double circuit 400kV OHL by erecting a new 80km double circuit 400kV OHL in Slovenia. The project will result in two new cross-border circuits&#58; Heviz(HU)-Cirkovce(SI) and Cirkovce (SI)-Žerjavenec (HR). | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Cirkovce (SI) | Heviz (HU) Zerjavenec (HR) | 1085 | New | Double Circuit | 80 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2019 | ELES is currently in the process of gaining easment from the land owners. | Delayed
141 | Slovenia-Hungary corridor |  | 225 | 225 |  | ELES | - | - | Internal |  | Upgrading 220kV lines to 400kV in corridor Divaca-Klece-Bericevo-Podlog-Cirkovce. | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Divaca (SI) | Cirkovce (SI) | 800 | Upgrade | Double Circuit | 193 |  | planned |  | 01/01/2020 | Design & Permitting | 1/ 1/ 2025 | The project is splitted in three phases: - 1st phase corridor Divača-Kleče-Beričevo (2020 - in permitting) - 2nd phase corridor Beričevo-Podlog (2025 - under consideration) - 3rd phase corridor Podlog-Cirkovce (2025 - under consideration). | Investment on time
142 | CSE 4 (2nd BG-GR interconnector and South BG corridor) | 3.7.11 |  |  | ESO;IPTO-SA |  |  |  | North-South | Mid-term Project | [12 empty] | 188.2 |  | 10 |  |  | 2021
142 | CSE 4 (2nd BG-GR interconnector and South BG corridor) |  | 256 | 256 |  | ESO | IPTO-SA | - | Cross-border |  | New interconnection line BG-GR by a 130km single circuit 400kV OHL. | 400 | AC | North-South (EAST) | Overhead Line | Permitting | Maritsa East 1 (BG) | N.Santa (GR) | 648 | New | Single Circuit | 130 |  | design & permitting |  | 01/01/2021 | Design & Permitting | 30/06/ 2021 | Delayed due to lack of funding. | Delayed
142 | CSE 4 (2nd BG-GR interconnector and South BG corridor) |  | 257 | 257 |  | ESO | - | - | Internal |  | New 100km single circuit 400kV OHL in parallel to the existing one. | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Maritsa East 1 (BG) | Plovdiv (BG) | 648 | New | Single Circuit | 100 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2019 | Delayed due to difficulties with the acquisition of the land | Delayed
142 | CSE 4 (2nd BG-GR interconnector and South BG corridor) |  | 258 | 258 |  | ESO | - | - | Internal |  | New 13km single circuit 400kV OHL in parallel to the existing one. | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Maritsa East 1 (BG) | Maritsa East 3 (BG) | 648 | New | Single Circuit | 13 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2017 | Delayed due to difficulties with the acquisition of the land | Delayed
142 | CSE 4 (2nd BG-GR interconnector and South BG corridor) |  | 262 | 262 |  | ESO | - | - | Internal |  | New 400kV OHL. Line length&#58; 150km. | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Maritsa East 1 (BG) | Burgas (BG) | 648 | New | Single Circuit | 150 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2021 | Delayed due to difficulties with the acquisition of the land | Delayed
144 | Mid Continental East corridor | 3.22 |  |  | TRANSELECTRICA; EMS |  |  |  | East-West | Mid-term Project | [12 empty] | 176 |  | 25 |  |  | 2022
144 | Mid Continental East corridor |  | 238 | New_400 kV OHL RO-RS |  | TRANSELECTRICA | EMS | - | Cross-border |  | New 131 km double circuit 400kV OHL between existing substation in Romania and Serbia (63 km on Romanian side and 68 km on Serbian side) 2x1380 MVA. | 400 | AC | North-South (EAST) | Overhead Line | Under Construction | Resita (RO) | Pancevo (RS) | 350 | New | Double Circuit | 131 |  | design & permitting |  | 01/01/2017 | Design & Permitting | 31/03/ 2017 | On Romanian side the line is under construction and the status on Serbian territory is also under construction | Investment on time
144 | Mid Continental East corridor |  | 269 | 400 kV OHL Portile de Fier-Resita |  | TRANSELECTRICA | - | - | Internal |  | New 116 km 400kV OHL single circuit between existing substation 400 kV Portile de Fier and new 400 kV substation Resita; 1380 MVA. | 400 | AC | North-South (EAST) | Overhead Line | Under Construction | Portile de Fier (RO) | Resita (RO) | 287 | New | Single Circuit | 116 |  | design & permitting |  | 01/01/2017 | Design & Permitting | 01/03/ 2018 | The investment was coordinated with investment no 238. The main problems are right of land along the line path and permitting. | Delayed
144 | Mid Continental East corridor |  | 270 | Upgrade of the existing 220kV double circuit OHL Resita –Timisoara – Sacalaz – Arad to 400kV double circuit line |  | TRANSELECTRICA | - | - | Internal |  | Upgrade of an existing 220 kV AC double circuit line (OHL) between Resita – Timisoara (RO) to 400 kV double circuit line Resita-Timisoara/Sacalaz of which: 74 km from Resita to Timisoara with a capacity of 1380 MVA and 92 km from Resita to Sacalaz with a capacity of 1380 MVA, both overhead lines will be built on common towers up to Icloda on 58 km. Upgrade of the existing 220 kV AC double circuit line (OHL) Timisoara/Sacalaz-Arad to 400 kV on 67 km of which: 14 km of line will be build single circuit between Sacalaz-C.Aradului-“connection point”, 11 km single circuit from Timisoara to “connection point” and the rest 42 km of the line will be double circuit from “connection point” to Arad. Current status of the project is devided as follows: Permitting for OHL 400 kV Resita- Timisoara/Sacalaz and Design for OHL 400 kV Timisoara/Sacalaz - Arad. | 400 | AC | North-South (EAST) | Overhead Line | Permitting | Resita (RO) | Arad (RO) | 180 | Upgrade | Double Circuit | 175 |  | design & permitting |  | 01/01/2022 | Design & Permitting | 31/12/ 2023 | Planned to start after investment 269 is finalized. | Delayed
144 | Mid Continental East corridor |  | 701 | 400 kV Substation Resita |  | TRANSELECTRICA | - | - | Internal |  | New 400 kV substation Resita (T400/220 kV 400 MVA + T 400/110 kV 250 MVA), as development of the existing 220/110 kV substation. | 400 |  | North-South (EAST) | Substation | Permitting | Resita (RO) | Resita (RO) | 350 | New |  |  |  | design & permitting |  | 01/01/2017 | Design & Permitting | 01/ 03/ 2018 | This investment is in correlation with investment no 269. | Delayed
144 | Mid Continental East corridor |  | 705 | 400 kV Substation Timisoara |  | TRANSELECTRICA | - | - | Internal |  | Replacement of 220 kV substation Timisoara with 400 kV substation (2x250 MVA 400/110 kV) | 400 |  | North-South (EAST) | Substation | Design | Timisoara (RO) | Timisoara (RO) | 180 | Upgrade |  |  |  | design & permitting |  | 01/01/2022 | Design & Permitting | 31/ 12/ 2023 | Investments 269 and 701 have to be finalized first. | Delayed
146 | CSE8 Transbalkan Corridor |  |  |  | CGES;EMS;NOS-BIH |  |  |  | East-West | Mid-term Project | [12 empty] | 95.6
146 | CSE8 Transbalkan Corridor |  | 625 | 400 kV OHL Lastva - Pljevlja |  | CGES | - | - | Internal |  | Reinforcement of the Montenegrin internal 400 kV transmission network with new 160 km double circuit 400kV AC OHL between existing substation Pljevlja and new substation Lastva. The investment will enable secure supply of Montenegrin power system and power transits directed to new HVDC link towards Italy. Also, this investment will enable connection of Renewable energy sources along its route. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Construction | Lastva (ME) | Pljevlja (ME) | 1095 | New | Single Circuit | 160 |  | design & permitting |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2016 | on time | Investment on time
146 | CSE8 Transbalkan Corridor |  | 1075 | 400 kV OHL Kragujevac-Kraljevo |  | EMS | - | - | Internal |  | New internal 400 kV OHL will connect existing SS Kragujevac with SS Kraljevo which is planned for upgrade to 400 kV voltage level. This investment will enhance the possibility of energy transits in direction north-east to south-west and east to west. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Construction | Kragujevac | Kraljevo | 1095 | New | Single Circuit | 55 |  |  |  | 01/01/2018 | Under Construction | 2019 | Due to insufficient financial support from EU this project is postponed. | Delayed
146 | CSE8 Transbalkan Corridor |  | 1076 | Upgrade of SS Kraljevo |  | EMS | - | - | Internal |  | Upgrade of the existing 220/110kV substation Kraljevo 3 by constructing the 400 kV level. | 400 |  | No EC Regional Group linked | Substation | Under Construction | Kraljevo |  | 1095 | Upgrade | [5 empty] | 01/01/2017 | Under Construction | 2019 | Due to insufficient financial support from EU this project is postponed. | Delayed
147 | South Balkan (CSE9) |  |  |  | EMS;IPTO-SA;MEPSO |  |  |  | North-South | Mid-term Project | [12 empty] | 270 |  | 30
147 | South Balkan (CSE9) |  | 235 | New_400kVinterconnection_RS_AL |  | IPTO-SA | - | - | Cross-border |  | New 242km 400kV OHL; on 78km the circuit will be installed on the same towers as the Tirana-Podgorica OHL currently in construction ; the rest will be built as single circuit line. | 400 | AC | No EC Regional Group linked | Overhead Line | Commissioned | Tirana(AL) | Pristina (RS) | 160 | New | Single Circuit | 242 |  | design & permitting |  | 01/01/2016 | Under Construction | 1/ 1/ 2016 | The project has been commissioned | Commissioned
147 | South Balkan (CSE9) |  | 236 | 236 |  | MEPSO | - | - | Cross-border |  | New 170km 400kV single circuit overhead interconnection between Serbia and FYR of Macedonia. | 400 | AC | No EC Regional Group linked | Overhead Line | Commissioned | Leskovac(RS) | Shtip (MK) | 620 | New | Single Circuit | 170 |  | under construction |  | 01/01/2014 | Under Construction | 1/ 1/ 2015 | Project has been commissioned | Commissioned
147 | South Balkan (CSE9) |  | 239 | 239 |  | MEPSO | - | - | Internal |  | New 150km cross-border single circuit 400kV OHL between existing substation Bitola and Elbasan | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Bitola (MK) | Elbasan (AL) | 160 | New | Single Circuit | 151 |  | planned |  | 01/01/2017 | Design & Permitting | 1/ 1/ 2020 | additional investigation of feasibility | Rescheduled
147 | South Balkan (CSE9) |  | 244 | 244 |  | IPTO-SA | - | - | Internal |  | Connection of the new 400kV substation in Lagadas in Thessaloniki area to the existing substation of Filippi via a new 110km double circuit 400kV OHL. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Construction | Filippi(GR) | Lagadas (GR) | 301 | New | Double Circuit | 110 |  | under construction |  | 01/01/2016 | Design & Permitting | 1/ 6/ 2017 | Delayd due to dificulties with the acquisition of the land. This issue has been resolved. | Delayed
147 | South Balkan (CSE9) |  | 707 | 239 |  | MEPSO Tyndp_project_promoter | - | - | Internal |  | New 400/110 kV substation in Ohrid area connected in/out to the new 400 kV line Bitola-Elbasan. | 400 |  | North-South (EAST) | Substation | Design & Permitting | Ohrid area (MK) |  | 0 | New |  |  |  | planned |  | 01/01/2017 | Design & Permitting | 1/ 1/ 2020 | additional investigation of feasibility | Rescheduled
147 | South Balkan (CSE9) |  | 708 | 708 |  | IPTO-SA | - | - | Internal |  | New 400kV substation in Lagadas in Thessaloniki area. | 400 |  | No EC Regional Group linked | Substation | Commissioned | Lagadas (GR) |  | 301 | New |  |  |  | under construction |  | 01/01/2014 | Under Construction | 1/ 1/ 2016 |  | Investment on time
147 | South Balkan (CSE9) |  | 912 | SS Kumanovo |  | MEPSO Tyndp_project_promoter | - | - | Internal |  | New 400/110 kV substation in North East part of FYRO Macedonia area connected in/out to the new 400 kV line Leskovac-Shtip. | 400 |  | No EC Regional Group linked | Substation | Under Consideration | Kumanovo |  | 0 | New | [5 empty] | 01/01/2030 | Under Consideration | 1/ 1/ 2020 | it is a new investment | New Investment
147 | South Balkan (CSE9) |  | 1002 | Tirana 3 (AL) - Prizren (RS) |  | MEPSO Tyndp_project_promoter | - | - | Cross-border |  | New 400 kV OHL between SS Tirana 3 – SS Skavica with around 100 km length. New 400 kV OHL between SS Skavica (Albania) and SS Prizren (Kosovo) with around 45 km (30 km Albanian Part). SS Skavica is a new SS and all this investment is dependent of construction of 300 MW HPP Skavica which is plant to be connected in SS Skavica. | 400 | AC | North-South (EAST) | Overhead Line | Planning | SS Skavica | SS Prizren | 0 | New | Single Circuit | 45 |  |  |  | 01/01/2028 | Planning | 1/ 1/ 2028 | New investment | New Investment
150 | Italy-Slovenia | 3.21 |  |  | TERNA;ELES |  |  |  | Slovenia - Italy | Mid-term Project | [12 empty] | 870 |  |  |  |  | 2022
150 | Italy-Slovenia |  | 616 | ITA-6 |  | ELES | - | - | Cross-border |  | New HVDC link between Italy and Slovenia. | 500 | DC | North-South (EAST) | Underground Cable | Design & Permitting | Slovenia (SI) | Salgareda (IT) | 800 | New | Single Circuit | 240 |  | under consideration |  | 01/01/2022 | Under Consideration | 1/ 1/ 2022 | On Slovenian side: Project in the study phase. On Italian side: Permitting procedure is still in progress. | Investment on time
151 | Asturian Ring |  |  |  | REE |  |  |  | Internal boundary in the north of Spain | Future Project | [12 empty] | 25.2 |  | 2.5 |  |  | 2025
151 | Asturian Ring |  | 522 | New substation Sama |  | REE | - | - | Internal |  | New 400kV substation Sama in the new Asturias Ring with connection to Lada and a new reactance. | 400 |  | No EC Regional Group linked | Substation | Planning | Sama (ES) |  | 1220 | New |  |  |  | partly commissioned, design & permitting |  | 01/01/2026 | Under Consideration | 1/ 1/ 2020 | Changes in the Spanish Master Plan, approved after the released of the project candidate list. This project is considered in the assessment as a future project instead a midterm one. | Ahead of time
151 | Asturian Ring |  | 523 | New substation Reboria |  | REE | - | - | Internal |  | New 400kV substation Reboria in the Asturian ring with 1 transformer 400/220 kV | 400 |  | No EC Regional Group linked | Substation | Planning | Reboria (ES) |  | 1220 | New |  |  |  | partly commissioned, design & permitting |  | 01/01/2026 | Under Consideration | 1/ 1/ 2020 | Changes in the Spanish Master Plan, approved after the released of the project candidate list. This project is considered in the assessment as a future project instead a midterm one. | Ahead of time
151 | Asturian Ring |  | 928 | Double circuit Gozon-Sama |  | REE | - | - | Internal |  | Asturian Ring. New double circuit Gozon-Reboria-Sama 400 kV (in a phase I only one circuit will be installed). Subestation Costa Verde is under consideration yet and wont be part of phase I | 400 | AC | No EC Regional Group linked | Overhead Line | Planning | GOZON (ES) | SAMA (ES) | 1220 | New | Double Circuit | 184 |  |  |  | 01/01/2026 | Under Consideration | 1/ 1/ 2020 | Changes in the Spanish Master Plan, approved after the released of the project candidate list. This project is considered in the assessment as a future project instead a midterm one. In a first step only 1 circuit will be installed. Costa Verde wont be part of phase I | Ahead of time
153 | France-Alderney-Britain | 1.7.1 |  |  | RTE and FAB LINK limited |  |  |  | France - Great Britain | Mid-term Project | [12 empty] | 850 |  | 230 |  |  | 2022
153 | France-Alderney-Britain |  | 987 | France-Alderney-Britain |  | RTE | - | - | Cross-border |  | France-Alderney-Britain (FAB) is a new 220km-long HVDC subsea interconnection between Exeter (UK) and Menuel (France) with VSC converter station at both ends. Expected rated capacity is 2*700 MW. | 320 | DC | North Seas Countries Offshore Grid Initiative | Subsea Cable | Design & Permitting | Menuel (FR) | Exeter (GB) | 1400 | New | Double Circuit | 220 |  |  |  | 01/01/2022 | Planning | 1/ 1/ 2022 | The notifications of the project were approved by the French and British authorities in July 2014. Feasibility studies have been finalised and a final route identified. Consent applications will be made in 2016. | Investment on time
157 | Aragón-Catalonia south |  |  |  | REE |  |  |  | Internal boundary in the east of Spain | Future Project | [12 empty] | 117 |  | 11.7 |  |  | 2027
157 | Aragón-Catalonia south |  | 545 | Escatrón-La Secuita |  | REE | - | - | Internal |  | New single circuit Escatrón-Els Aubals-La Secuita 400kV OHL. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Escatron (ES) | La Secuita (ES) | 200 | New | Single Circuit | 125 |  | design & permitting |  | 01/01/2027 | Under Consideration | 1/ 1/ 2027 | The investment progressed as previously planned | Investment on time
157 | Aragón-Catalonia south |  | 546 | New substation Els Aubals |  | REE | - | - | Internal |  | New 400kV substation in Els Aubals. | 400 |  | No EC Regional Group linked | Substation | Under Consideration | Els Aubals (ES) |  | 200 | New |  |  |  | design & permitting |  | 01/01/2027 | Under Consideration | 1/ 1/ 2027 | The investment progressed as previously planned | Investment on time
157 | Aragón-Catalonia south |  | 547 | New substation La Secuita |  | REE | - | - | Internal |  | New 400kV substation in La Secuita with 400/220kV transformer. | 400 |  | No EC Regional Group linked | Substation | Under Consideration | La Secuita (ES) |  | 200 | New |  |  |  | design & permitting |  | 01/01/2027 | Under Consideration | 1/ 1/ 2027 | The investment progressed as previously planned | Investment on time
158 | Massif Central South |  |  |  | RTE |  |  |  | Internal boundary in France North-South | Long-term Project | [12 empty] | 310 |  | 60 |  |  | 2025
158 | Massif Central South |  | 597 | Southern Massif Central |  | RTE | - | - | Internal |  | New 175-km 400kV double circuit OHL Gaudière-Rueyres substituting to the existing single circuit 400kV OHL | 400 | AC | No EC Regional Group linked | Overhead Line | Planning | La Gaudière (FR) | Rueyres (FR) | 3500 | New | Double Circuit | 175 |  | under consideration |  | 01/01/2023 | Under Consideration | 1/ 1/ 2025 | Further studies performed after TYNDP2014 confirmed the feasibility of the project. The commisionning date follows the amount of generation installation in the area (Hydro, Solar and Wind). | Rescheduled
164 | N-S Eastern DE_central section |  |  |  | TENNET-DE |  |  |  | inside-inside | Mid-term Project | [12 empty] | 1110 |  | 170 |  |  | 2022
164 | N-S Eastern DE_central section |  | 149 | Dollern - Stade |  | TENNET-DE | - | - | Internal |  | New 380kV double circuit OHL Dollern - Stade including new 380kV switchgear in Stade. Length 14km. | 380 | AC | No EC Regional Group linked | Overhead Line | Permitting | Dollern (DE) | Stade (DE) | 3749 | New | Double Circuit | 14 |  | design & permitting |  | 01/01/2022 | Design & Permitting | 1/ 1/ 2023 | Delay due to long permitting process | Delayed
164 | N-S Eastern DE_central section |  | 157 | Wahle - Mecklar |  | TENNET-DE | - | - | Internal |  | New 380kV double circuit OHL Wahle - Mecklar including two new substations. Length: 210km. | 380 | AC | No EC Regional Group linked | Overhead Line | Permitting | Wahle (DE) | Mecklar (DE) | 2264 | New | Double Circuit | 210 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 1/ 1/ 2021 | Delay due to long permitting process | Delayed
164 | N-S Eastern DE_central section |  | 677 | Dollern - Landesbergen |  | TENNET-DE | - | - | Internal |  | New 380 kV line in existing OHL corridor Dollern-Sottrum-Wechold-Landesbergen (130 km) | 380 | AC | No EC Regional Group linked | Overhead Line | Permitting | Dollern (DE) | Landesbergen (DE) | 3749 | New | Double Circuit | 130 |  | under consideration |  | 01/01/2022 | Planning | 1/ 1/ 2023 | Delay due to long permitting process | Delayed
164 | N-S Eastern DE_central section |  | 685 | Mecklar - Grafenrheinfeld |  | TENNET-DE | - | - | Internal |  | New double circuit OHL 380-kV-line (130 km). Due to ongoing political discussions a change of the connection point Grafenrheinfeld is under consideration. | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Mecklar (DE) | Grafenrheinfeld (DE) | 2387 | New | Double Circuit | 130 |  | under consideration |  | 01/01/2022 | Planning | 1/ 1/ 2022 |  | Investment on time
167 | Viking DKW-GB | 1.14 |  |  | Energinet.dk;NGIHL |  |  |  | Denmark- West - Great Britain | Mid-term Project | [12 empty] | 1970 |  | 395 |  |  | 2020
167 | Viking DKW-GB |  | 436 | Endrup - Idomlund |  | ENERGINET | - | - | Internal |  | New 95 km single circuit 400 kV line | 400 | AC | No EC Regional Group linked | Underground Cable | Planning | Idomlund (DK) | Endrup (DK) | 1360 | New | Single Circuit | 74 |  | under consideration |  | 01/01/2030 | Under Consideration | 1/ 1/ 2022 | The connection to GB requires this upgrade of the internal Danish grid in order to harvest the full benefits of the Viking link. As this investment serves multi-purposes, only part of it is allocated to the Viking project | Investment on time
167 | Viking DKW-GB |  | 998 | DKW-GB link |  | ENERGINET | - | - | Cross-border |  | 2x700 MW HVDC subsea link across the North Seas. New substations on both sides; GB; Bicker Fenn; DK- Revsing | 500 | DC | No EC Regional Group linked | Subsea Cable | Permitting | Revsing (DKW) | Bicker Fen (GB) | 1400 | New | Double Circuit | 760 |  |  |  | 01/01/2030 | Under Consideration | 31/12/ 2022 | Feasibility study finalized, UK cap and floor regulation awarded, public consultation ongoing, permit procedure ongoing, pre-application procedure started. supplier engagement ongoing, preparation of tender package for cables and converter ongoing. | Investment on time
168 | Spaak NL |  |  |  | TENNET-NL |  |  |  | Netherlands - Germany | Future Project | [17 empty] | 2025
168 | Spaak NL |  | 894 | Spaak NL |  | TENNET-NL | - | - | Internal |  | New Overhead line from Sliedrecht to Dodewaard of 2x2633 MVA in Wintrack, 65 km. Update&#58; AC solution is unlikely at the moment; other solutions are being considered. Until a new solution is found, this project is kept as it is in TYNDP. | 380 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Krimpen aan de Ijssel | Dodewaard | 0 | New | Double Circuit | 65 |  |  |  | 01/01/2025 | Under Consideration | >>2030 | This conceptual future project could become relevant when large amounts wind power need to be transported from west to east. Internal studies have shown that an AC solution as in the project list is not very likely. This project is investigated as one of the options together with other projects (e.g. 256) and has no formal status within TenneT. | Investment on time
170 | Baltic synchronization |  |  |  | AST;ELERING;LITGRID |  |  |  | Baltics - Nordic - Continental Europe | Future Project | [12 empty] | 1069 |  | 200 |  |  | >2030
170 | Baltic synchronization |  | 380 | 330 kV line VAE-Kruonis |  | LITGRID | - | - | Internal |  | New single circuit 330kV OHL VAE-Kruonis for the internal grid reinforcement, to complement new Visaginas NPP and project 170. “Baltic synchronization” | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Under Consideration | Visaginas (LT) | Kruonis (LT) | 150 | New | Single Circuit | 200 |  | planned |  | 01/01/2022 | Under Consideration | 01/01/ 2024 | Investment implementation time depends from decisions about new Visaginas NPP and project 170. Baltic synchronization”. | Delayed
170 | Baltic synchronization |  | 382 | 330 kV line Vilnius-Neris |  | LITGRID | - | - | Internal |  | New single circuit 330kV OHL (943 MVA, 50km). | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Planning | Vilnius (LT) | Neris (LT) | 150 | New | Single Circuit | 50 |  | planned |  | 01/01/2022 | Planning | 1/ 1/ 2024 | Investment implementation time depends from decisions about new Visaginas NPP and project 170. Baltic synchronization” | Delayed
170 | Baltic synchronization |  | 1004 | 330kV OHL Paide-Sindi (L346) |  | ELERING | - | - | Internal |  | Reinforcement of existing 330 kV OHL between Paide and Sindi 330 kV substations in Estonia. Old line will be replaced with new towers and wires of 3x400 mm2 in phase. The thermal capacity of the line is planned 1143 MVA. The investment is also a backbone for Baltics Synchronization with CE (project nr 170). | 330 | AC | No EC Regional Group linked | Overhead Line | Cancelled | Sindi | Paide | 200 | New | Single Circuit | 76 |  |  |  | 01/01/2030 | Planning | 01/01/2025 | we have developed an operational procedure to overcome the overloading issues, therefore the investment can be postponed | Cancelled
170 | Baltic synchronization |  | 1010 | 330 kV OHL Tartu-Valmiera |  | ELERING | AST | - | Cross-border |  | Reinforcement of existing 330 kV OHL with new towers and wires of 3x300 mm2 in phase. The thermal capacity of the line is planned 1000 MVA. The investment is also a backbone for Baltics Synchronization with CE (project nr 170). | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Under Consideration | Tartu | Valmiera | 500 | Upgrade | Single Circuit | 133 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2025 | Baltic States desinchronisation | Rescheduled
170 | Baltic synchronization |  | 1011 | Valmiera -Tsirguliina 330 kV |  | ELERING | AST | - | Cross-border |  | Reinforcement of existing 330 kV OHL with new towers and wires of 3x300 mm2 in phase. The thermal capacity of the line is planned 1000 MVA.The investment is also a backbone for Baltics Synchronization with CE (project nr 170). | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Under Consideration | Tsirguliina | Valmiera | 500 | Upgrade | Single Circuit | 60 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2025 | - | Rescheduled
170 | Baltic synchronization |  | 1012 | 330 kV OHL Tartu-Balti (L300) |  | ELERING | - | - | Internal |  | Reinforcement of existing 330 kV OHL between Balti and Tartu 330 kV substations in Estonia. Old line will be replaced with new towers and wires of 3x400 mm2 in phase. The thermal capacity of the line is planned 1143 MVA. The investment is also a backbone for Baltics Synchronization with CE (project nr 170). | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Planning | Balti | Tartu | 500 | Upgrade | Single Circuit | 168 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2024 | - | Rescheduled
170 | Baltic synchronization |  | 1013 | Eesti-Tsirguliina 330kV OHL |  | ELERING | - | - | Internal |  | Reinforcement of existing 330 kV OHL between Eesti and Tsirguliina 330 kV substations in Estonia. Old line will be replaced with new towers and wires of 3x400 mm2 in phase. The thermal capacity of the line is planned 1143 MVA. The investment is also a backbone for Baltics Synchronization with CE (project nr 170). | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Planning | Eesti | Tsirguliina | 500 | New | Single Circuit | 243 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2025 | - | Rescheduled
170 | Baltic synchronization |  | 1034 | New 400 kV interconnection line |  | LITGRID | - | - | Internal |  | New 400 kV interconnection line necessary for synchronous interconnection of Baltics with CE. | 400 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Under Consideration | New planned 400 kV Marijampole substation or exicting 400 kV Aytus substation. | State border | 600 | New | Double Circuit | 60 |  |  |  | 01/01/2023 | Under Consideration | 01/01/2031 | New line routing and implementation time depends from decisions for project 170. “Baltic synchronization”. | New Investment
170 | Baltic synchronization |  | 1063 | TEC1-TEC2 |  | AST | - | - | Internal |  | Investment is necessary to strenghtening internal grid in Latvia due to get transmission capacity of 600 MW via Latvia | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Under Consideration | TEC1 | TEC2 | 600 | Upgrade | Single Circuit | 12 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2025 | - | Rescheduled
170 | Baltic synchronization |  | 1064 | Viskali (LV) - Musa (LT) |  | AST | LITGRID | - | Cross-border |  | To increase transmission capacity by 600 MW via Baltic States. | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Under Consideration | Viskali (LV) | Musa (LT) | 600 | Upgrade | Single Circuit | 88 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2025 | Comissioning date changed from 2030 to 2025, to avoid splitting project 170."Baltic synchronisation" in two stages. | Rescheduled
170 | Baltic synchronization |  | 1065 | Aizkraukle(LV)-Panevėžys(LT) |  | AST | LITGRID | - | Cross-border |  | To increase transmission capacity by 600 MW via Baltic States. | 330 | AC | Baltic Energy Market Interconnection Plan | Overhead Line | Under Consideration | Aizkraukle (LV) | Panevežys (LT) | 600 | Upgrade | Single Circuit | 127 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2025 | Comissioning date changed from 2030 to 2025, to avoid splitting project 170."Baltic synchronisation" in two stages. | Rescheduled
170 | Baltic synchronization |  | 1117 | B2B at Narva |  | ELERING | - | - | Internal |  | B2B construction with 500 MW capacity on existing Estonia-Russia 330 kV AC lines on Estonian side, in Narva area. | 330 |  | Baltic Energy Market Interconnection Plan | Substation | Planning | Eesti |  | 500 | New | [7 empty] | 1/ 1/ 2024 | The investment is related to Baltic synchronisation cluster. | New Investment
170 | Baltic synchronization |  | 1118 | SVC and control upgrades |  | ELERING | - | - | Internal |  | SVC implementation in weak grid parts due to decrease of SC capacity; upgrade of PSS in power stations. AGC impementation and commissioning in SCADA systems and power plants; WAMS and WAMPAC systems | 330 |  | Baltic Energy Market Interconnection Plan | Compensation | Planning | Eesti 330 kV |  | 0 | New | [7 empty] | 1/ 1/ 2024 | New investment | New Investment
172 | ElecLink | PCI number 1.7.3 |  |  | ElecLink |  |  |  | France - Great Britain | Mid-term project | [12 empty] | 350 |  | 90 |  |  | 2018
172 | ElecLink |  | 1388 | ElecLink | [6 empty] | ​​ElecLink is a new FR - UK interconnection cable with 1000 MW capacity though the channel Tunnel between Sellindge (UK) and Mandarins (FR). Converter stations will be located on Eurotunnel concession at Folkestone and Coquelles. This HVDC interconnection is a PCI project (Project of Common Interest) no. 1.7.3. | 320 | DC |  |  | Design & permitting | Sellindge (UK) | Mandarins (FR) | [9 empty] | 2018
173 | FR-BE Phase 2 (study): Aubange-Moulaine |  |  |  | ELIA;RTE |  |  |  | France - Belgium | Future Project | [12 empty] | 20 |  | 10 |  |  | 2020
173 | FR-BE Phase 2 (study): Aubange-Moulaine |  | 1281 | Aubange-Moulaine: PSTs (under study) |  | ELIA | RTE | - | Cross-border |  | The reference solution consists of the installation of two phase shifting transformers, one on each of the 225kV circuits of the Aubange-Moulaine cross-border overhead line. | 225 |  | No EC Regional Group linked | Phase Shift Transformer | Under Consideration | Aubange (BE) | Moulaine (FR) |  | Upgrade | [7 empty] | 01/01/2020 | Project introduced in TYNDP16 related to congestion signals picked up vibilateral studies and confirmed in RG NS Common Planning Study. | New Investment
174 | Greenconnector |  |  |  | Worldenergy SA |  |  |  | Italy - Switzerland | Mid-term project | [12 empty] | 600 |  | 60 |  |  | 2021
174 | Greenconnector |  | 1014 | Greenconnector | [6 empty] | ​Greenconnector is an HVDC interconnector project between Italy and Switzerland for power transport using DC cables rather than overhead lines. The route length is about 150 km. The design power is 1000 MW (1200 MW in overload condition), while the DC voltage is +/- 400 kV DC. Two cables will be installed, working with a bipolar scheme. Great part of the cables route will exploit a section of an existing oil pipeline, no longer in service since January 1997. This pipeline crosses the Italian and Switzerland border at Splügenpass and is running close by the two end stations of the Greenconnector project (Sils in Graubunden Canton and Verderio Inferiore, Lecco). The cables will be pulled inside the pipeline itself, reducing the amount of civil works required before and after cable laying and therefore limiting even temporary environmental impact. For about 47 km the cables will run across the Como lake.​ | 400 | DC |  |  | Design & permitting | Verderio | Sils i.D. |  |  |  | 150 | [5 empty] | 2021
175 | Great Belt II |  |  |  | Energinet.dk |  |  |  | Denmark-West - Denmark-East | Future Project | [12 empty] | 250 |  | 50 |  |  | 2030
175 | Great Belt II |  | 1000 | Great Belt II |  | ENERGINET | - | - | Internal |  | 600 MW HVDC subsea link between both DK systems (2 synchr. areas, 2 market areas) | 450 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Malling (DKW) | Kyndby (DKE) | 600 | New | Single Circuit | 200 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2030 | optional candidate project from TYNDP14 | Investment on time
176 | Hansa PowerBridge 1 |  |  |  | 50HERTZ;SVK |  |  |  | Germany - Sweden | Long-term Project | [12 empty] | 660 |  | 70 |  |  | 2025
176 | Hansa PowerBridge 1 |  | 995 | Hansa PowerBridge |  | SVK | 50HERTZ | - | Cross-border |  | New HVDC interconnector between Sweden (SE4) and Germany (50 Hertz) aiming to enhance the integration of the Nordic and the continental power market. Moreover the interconnector facilitates RES integration and increases the system adequacy in both systems. | 300 | DC | No EC Regional Group linked | Subsea Cable | Planning | Station SE4 | Güstrow (DE) | 700 | New | Single Circuit | 250 |  |  |  | 01/01/2025 | Under Consideration | 2025 | RGBS common investigations for TYNDP 2014 | Investment on time
177 | PST Hradec | N/A - the project is not in the PCI list |  |  | CEPS |  |  |  | Czech - Germany | Mid-term Project | [12 empty] | 52 |  | 10 |  |  | 2016
177 | PST Hradec |  | 889 | PST Hradec |  | CEPS | - | - | Cross-border |  | Construction of new PST in substation Hradec with target capacity 2x1700MVA | 400 |  | North-South (EAST) | Phase Shift Transformer | Under Construction | Hradec |  | 500 | New |  |  |  | New project |  | 01/01/2016 | Design & Permitting | 1/ 1/ 2016 | Progress as planned | Investment on time
179 | DKE - DE |  |  |  | 50HERTZ;Energinet.dk |  |  |  | Denmark-East - Germany | Future Project | [12 empty] | 360 |  | 100 |  |  | 2030
179 | DKE - DE |  | 1016 | Kontek 2 |  | ENERGINET | 50HERTZ | - | Cross-border |  | new 600 MW HVDC subsea cable connecting DK2 and DE | 400 | DC | Baltic Energy Market Interconnection Plan | Subsea Cable | Under Consideration | Bjæverskov (DK2) | Bentwisch (DE) | 600 | New | Single Circuit | 170 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2030 | optional candidate project from TYNDP14 | Investment on time
183 | DKW-DE, Westcoast | 1.3.1 |  |  | Energinet.dk;TENNET-DE |  |  |  | Denmark-West - Germany | Mid-term Project | [12 empty] | 210 |  | 42 |  |  | 2022
183 | DKW-DE, Westcoast |  | 1018 | WestCoast Line, North v2 |  | ENERGINET | TENNET-DE | - | Cross-border |  | new 380 kV Overhead line DK1-DE for integration of RES and increase of NTC | 380 | AC | North Seas Countries Offshore Grid Initiative | Underground Cable | Planning | Niebüll (DE) | Endrup (DKW) | 500 | New | Double Circuit | 92 |  |  |  | 01/01/2022 | Planning | 31/ 12/ 2022 | project planning and technical design is progressing | Investment on time
184 | PST Arkale | 2.8 |  |  | REE |  |  |  | Spain - France | Mid-term Project | [12 empty] | 23 |  | 3 |  |  | 2017
184 | PST Arkale |  | 594 | PST Arkale |  | REE | - | - | Cross-border |  | New PST in Arkale-Argia 220 kV interconnection line | 220 |  | North-South (WEST) | Phase Shift Transformer | Permitting | Arkale (ES) |  | 500 | New |  |  |  | design & permitting |  | 01/01/2016 | Planning | 1/ 1/ 2017 | Delays because of closure on budget and financing | Delayed
186 | east of Austria |  |  |  | APG |  |  |  | outside-inside | Mid-term Project | [12 empty] | 200 |  | 50 |  |  | 2021
186 | east of Austria |  | 886 | 886 |  | APG | - | - | Internal |  | To allow the grid integration of the planned renewable energy generation (mainly wind power) in the north-eastern part of Austria ("Weinviertel") and to cover the foreseen load growth in that region the transmission grid infrastructure has to be enforced and new substations for the connection need to be erected | 380 | AC | No EC Regional Group linked | Overhead Line | Design | Seyring | Neusiedl/Zaya | 0 | New | Double Circuit | 60 |  | New project |  | 01/01/2021 | Planning | 1/ 1/ 2021 | Start of the authorisation process (EIA) in mid 2016. | Investment on time
187 | St. Peter - Pleinting |  |  |  | APG;TENNET-DE |  |  |  | Austria - Germany | Long-term Project | [12 empty] | 180 |  | 30 |  |  | 2022
187 | St. Peter - Pleinting |  | 997 | 997 Pleinting - St. Peter |  | TENNET-DE | APG | - | Cross-border |  | new 380-kV-line Pleinting (DE) - St. Peter (AT) on exting OHL corridor | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Pleinting (DE) | St. Peter (AT) | 1500 | New | Double Circuit | 60 |  |  |  | 01/01/2022 | Under Consideration | 1/ 1/ 2022 | Investment on time relative to TYNDP14 | Investment on time
189 | Irish Scottish Links on Energy Study (ISLES) |  |  |  | the Department of Enterprise, Trade and Investment in Northern Ireland, the Department of Communications, Energy and Natural Resources in Ireland, and the Scottish Government |  |  |  | UK - Ireland | Future Project | [12 empty] | 7840 |  |  |  |  | 2020-2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1389 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | HVDC Platform​ |  |  |  |  | Under consideration | Argyll Hub | N/A | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1390 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​HVDC Platform |  |  |  |  | Under Consideration | Coleraine Hub | N/A | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1391 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​HVDC Platform |  |  |  |  | Under Consideration | coolkeeragh hub | N/A | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1392 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​101km, 1GW subsea cable from Argyll hub to Coleraine. |  |  |  |  | Under Consideration | Argyll hub | Coleraine | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1393 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​43 km subsea cable from Coolkeeragh hub to nshore landing point, 10 km onshore cable to Coolkeeragh substation. |  |  |  |  | Under Consideration | Coolkeeragh | Coolkeeragh hub | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1394 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​41km, 1GW subsea DC cable from Coleraine substation to Coolkeeragh hub |  |  |  |  | Under Consideration | Coleraine substation | Coolkeeragh hub | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1395 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​HVDC Platform |  |  |  |  | Under Consideration | Southern Hub | n/a | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1396 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | 53km, 500MW subsea​ DC cable from Coleraine hub to Coolkeeragh hub |  |  |  |  | Under Consideration | Coleraine hub | Coolkeeragh hub | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1397 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Subsea cable |  |  |  |  | Under Consideration | Southern Hub UK | Trawsfynydd | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1398 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​348km, 1GW subseaDC cable from Hunterston to Coleraine |  |  |  |  | Under Consideration | Hunterston | Coleraine | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1399 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​DC Cable |  |  |  |  | Under Consideration | Southern Hub | Trawsfynydd | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1400 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Substation |  | DC |  |  | Under Consideration | Trawsfynydd | n/a | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1401 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​subsea cable |  |  |  |  | Under Consideration | Southern Hub | Pembroke | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1402 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Onshore cable |  |  |  |  | Under Consideration | Southern Hub | Pembroke | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1403 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​offshore cable |  |  |  |  | Under Consideration | Southern Hub | Lodgewood | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1404 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Onshore cable |  |  |  |  | Under Consideration | Southern Hub | Lodgewood | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1406 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Substation |  |  |  |  | Under Consideration | Pembroke | n/a | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1408 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Substation |  |  |  |  | Under Consideration | Lodgewood | n/a | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1411 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | DC cable |  |  |  |  | Under Consideration | Central Hub | Southern Hub | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1412 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Platform Hub |  |  |  |  | Under Consideration | Central Hub | n/a | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1413 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​cable |  |  |  |  | Under Consideration | Central Hub | Dunstown | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1414 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Onshore DC cable | [5 empty] | Central Hub | Dunstown | [9 empty] | 9999
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1415 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​offshore cable | [5 empty] | Central hub | Trawsfynydd | [9 empty] | 9999
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1416 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Onshore cable | [5 empty] | Central Hub | Trawsfynydd | [9 empty] | 9999
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1417 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | Hub | [5 empty] | Trawsfynydd | n/a | [9 empty] | 9999
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1418 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Hub | [5 empty] | Dunstown | n/a | [9 empty] | 9999
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1419 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Offshore DC Cable | [5 empty] | Central Hub | Woodland | [9 empty] | 9999
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1420 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Onshore Cable | [5 empty] | Central Hub | Woodland | [9 empty] | 9999
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1421 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Subsea cable | [5 empty] | Northern Hub | Central Hub | [9 empty] | 9999
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1422 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | Platform Hub | [5 empty] | Northern Hub | n/a | [9 empty] | 9999
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1423 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Offshore DC Cable |  |  |  |  | Under Consideration | Northern Hub | Louth | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1424 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Offshore DC Cable |  |  |  |  | Under Consideration | Northern Hub | Louth | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1425 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Onshore DC cable |  |  |  |  | Under Consideration | Northern Hub | Louth | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1426 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​Platform Hub |  |  |  |  | Under Consideration | Louth | n/a | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1427 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | Substation |  |  |  |  | Under Consideration | Woodland | n/a | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1428 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | ​offshore cable |  |  |  |  | Under Consideration | Northern Hub | Louth | [9 empty] | 1/1/2030
189 | Irish Scottish Links on Energy Study (ISLES) |  | 1429 | Irish Scottish Links on Energy Study (ISLES) | [6 empty] | Offshore Cable | 300 | DC |  |  | Under Consideration | Northern Hub | Louth | [9 empty] | 1/1/2030
190 | NorthConnect | PCI 1.10 |  |  | NorthConnect |  |  |  | Great Britain - Norway | Mid-term project | [12 empty] | 1613 |  |  |  |  | 2022
190 | NorthConnect |  | 1382 | NorthConnect | [6 empty] | ​​​​A 650 km long subsea interconnector between Norway and Scotland is planned to be realized in 2022. The main driver for the project is to integrate the hydro-based Norwegian system with the thermal/nuclear/wind-based British system. The interconnector will improve security of supply both in Norway in dry years and in Great Britain in periods with negative power balance (low wind, low solar, high demand etc.). Additionally the interconnector will be positive both for the European market integration, for facilitating renewable energy and also for preparing for a power system with lower CO2-emissions. The interconnector is planned to be a 500 kV 1400 MW HVDC subsea interconnector between western Norway and eastern Scotland.​ | 500 | DC |  |  | Design | Sima | Peterhead | [9 empty] | 2022 |  | Delayed
191 | OWP TenneT Northsea Part 2 |  |  |  | TENNET-DE |  |  |  | inside-DE | Long-term Project | [12 empty] | 4000 |  | 1000 |  |  | 2022
191 | OWP TenneT Northsea Part 2 |  | 656 | BorWin3 |  | TENNET-DE | - | - | Internal |  | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 160 km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Construction | Cluster BorWin3 | Emden/Ost (DE) | 900 | New | Single Circuit | 160 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 1/ 1/ 2019 | due to the project | Delayed
191 | OWP TenneT Northsea Part 2 |  | 952 | Cluster DolWin 5 (NOR 1-1) |  | TENNET-DE | - | - | Internal |  | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 250 km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Cluster DolWin 5 (NOR-1-1) | Halbemond | 900 | New | Single Circuit | 135 |  |  |  | 01/01/2021 | Under Consideration | 1/ 1/ 2024 |  | Rescheduled
191 | OWP TenneT Northsea Part 2 |  | 953 | Cluster DolWin6 |  | TENNET-DE | - | - | Internal |  | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 60km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Cluster DolWin 6 (NOR-3-3) | Emden/East | 900 | New | Single Circuit | 60 |  |  |  | 01/01/2021 | Under Consideration | 1/ 1/ 2023 | due to the project | Delayed
192 | OWP Northsea TenneT Part 3 |  |  |  | TENNET-DE |  |  |  | inside-DE | Future Project | [12 empty] | 6000 |  | 1000 |  |  | 2027
192 | OWP Northsea TenneT Part 3 |  | 211 | DolWin 4 (NOR-3-2) |  | TENNET-DE | - | - | Internal |  | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 190km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Cluster DolWin 4 (NOR 3-2) | area of Cloppenburg | 900 | New | Single Circuit | 190 |  | under consideration |  | 01/01/2020 | Under Consideration | 1/ 1/ 2028 | delayed due to the project | Delayed
192 | OWP Northsea TenneT Part 3 |  | 659 | SylWin2 |  | TENNET-DE | - | - | Internal |  | New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 205 km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Cluster SylWin2 (DE) | Büttel (DE) | 900 | New | Single Circuit | 205 |  | under consideration |  | 01/01/2023 | Under Consideration | 1/ 1/ 2026 | due to the project | Delayed
192 | OWP Northsea TenneT Part 3 |  | 954 | Cluster BorWin 5 (NOR-7-1) |  | TENNET-DE | - | - | Internal |  | Connecton of new offshore wind parks. New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 260km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Underground Cable | Under Consideration | Cluster BorWin 5 (NOR-7-1) | area of Cloppenburg/East | 900 | New | Single Circuit | 250 |  |  |  | 01/01/2022 | Under Consideration | 1/ 1/ 2025 |  | Rescheduled
192 | OWP Northsea TenneT Part 3 |  | 955 | BorWin6 (NOR-7-2) |  | TENNET-DE | - | - | Internal |  | Connection of new offshore wind parks.New HVDC transmission system consisting of offshore platform, cable and converters with a total length of 255km. Line capacity&#58; 900 MW | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Cluster BorWin6 (NOR-7-2) | area of Wilhelmshafen | 900 | New | Single Circuit | 255 |  |  |  | 01/01/2023 | Under Consideration | 1/ 1/ 2030 |  | Rescheduled
193 | Godelleta-Morella/La Plana | 2.26 |  |  | REE |  |  |  | Internal boundary in the east of Spain | Future Project | [12 empty] | 69 |  | 6.9 |  |  | 2023
193 | Godelleta-Morella/La Plana |  | 927 | La Plana/Morella-Godelleta |  | REE | - | - | Internal |  | New 400 kV axis Godelleta-Morella/La Plana (Spain) | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | La Plana/Morella | Godelleta | 1415 | New | Double Circuit | 310 |  |  |  | 01/01/2023 | Under Consideration | 1/ 1/ 2023 | The investment progressed as previously planned | Investment on time
194 | Cartuja |  |  |  | REE |  |  |  | Internal boundary in the south of Spain | Future Project | [12 empty] | 39.6 |  | 4 |  |  | 2029
194 | Cartuja |  | 561 | New substation Cartuja |  | REE | - | - | Internal |  | New 400kV substation Cartuja with a 400/220kV transformer. | 400 |  | No EC Regional Group linked | Substation | Under Consideration | Cartuja (ES) |  | 1320 | New |  |  |  | partly commissioned, design & permitting |  | 01/01/2022 | Under Consideration | 1/ 1/ 2029 | Rescheduled due to changes in the Spanish Master Plan that consider a delay in the commissioning of the renewable generation link to this project | Rescheduled
194 | Cartuja |  | 929 | Cartuja-Arcos 400 kV |  | REE | - | - | Internal |  | New double circuit Cartuja-Arcos 400 kV | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Cartuja | Arcos | 1320 | New | Double Circuit | 60 |  |  |  | 01/01/2022 | Under Consideration | 1/ 1/ 2029 | Rescheduled due to changes in the Spanish Master Plan that consider a delay in the commissioning of the renewable generation link to this project | Rescheduled
197 | N-S Finland P1 stage 2 |  |  |  | FINGRID |  |  |  | Finland North-South | Long-term Project | [12 empty] | 90 |  | 10 |  |  | 2023
197 | N-S Finland P1 stage 2 |  | 742 | Pyhänselkä-Petäjävesi |  | FINGRID | - | - | Internal |  | New single circuit 400 kV OHLs will be built from middle Finland to Oulujoki Area to increase the capacity between North and South Finland. Will replace existing 220 kV lines. | 400 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Pyhänselkä (FI) | Petäjävesi (FI) | 1000 | New | Single Circuit | 320 |  | design & permitting |  | 01/01/2023 | Design & Permitting | 1/ 1/ 2023 | Progresses as planned | Investment on time
198 | Area of Lake Constance | 2.11 |  |  | AMPRION; TRANSNET-BW; VUEN |  |  |  | Germany - Austria | Long-term Project | [12 empty] | 460 |  | 70 |  |  | 2023
198 | Area of Lake Constance |  | 136 | DE-AT-CH connection |  | VUEN | TRANSNET-BW | AMPRION | Cross-border |  | 380 kV Rüthi – Meiningen and 380 kV Meiningen - Border Area AT-DE | 380 | AC | North-South (WEST) | Overhead Line | Under Consideration | Border area (DE-AT) | Rüthi (CH) | 1200 | New | Double Circuit | 45 |  | planned |  | 01/01/2022 | Planning | 1/ 1/ 2023 | Due to the changed market and grid situation in this area, there is a need for an update of the current study and its findings. | Delayed
198 | Area of Lake Constance |  | 984 | Herbertingen - Tiengen |  | AMPRION | - | - | Cross-border |  | Herbertingen – Tiengen; Between the two substations Herbertingen and Tiengen a new line will be constructed in an existing corridor. Enhancement of the grid, which will increase transmission capacity noticeably, is needed at the substation Herbertingen. | 380 | AC | North-South (WEST) | Overhead Line | Planning | Herbertingen (DE) | Tiengen (DE) | 400 | Upgrade | Double Circuit | 115 |  |  |  | 01/01/2020 | Planning | 1/ 1/ 2020 |  | Investment on time
198 | Area of Lake Constance |  | 985 | Rommelsb. - Herbertingen |  | AMPRION | - | - | Cross-border |  | Rommelsbach – Herbertingen; Between point Rommelsbach and substation Herbertingen a new line will be constructed in an existing corridor.This will significantly increase transmission capacity (grid enhancement). | 380 | AC | North-South (WEST) | Overhead Line | Permitting | Rommelsbach (DE) | Herbertingen (DE) | 400 | Upgrade | Double Circuit | 62 |  |  |  | 01/01/2018 | Planning | 1/ 1/ 2019 | Delay due to long permitting process | Delayed
198 | Area of Lake Constance |  | 986 | Wullenstetten - border area (DE-AT) |  | AMPRION | TRANSNET-BW | - | Cross-border |  | Between point Wullenstetten and point border area (DE-AT) an upgrade of an existing 380-kV-line is necessary (grid enhancement). Thereby, a significantly higher transmission capacity is realized. The 380 kV substation station Dellmensingen is due to be extended (grid enhancement). Between switching point Neuravensburg and Austrian National border (AT) a new line with a significantly higher transmission capacity will be constructed in an existing corridor (grid enhancement). | 380 | AC | North-South (WEST) | Overhead Line | Planning | Wullenstetten (DE) | Austrian National border (AT) | 2000 | Upgrade | Double Circuit | 94 |  |  |  | 01/01/2020 | Planning | 1/ 1/ 2020 |  | Investment on time
199 | Lake Geneva South |  |  |  | RTE;SWISSGRID |  |  |  | France - Switzerland | Future Project | [12 empty] | 120 |  | 30 |  |  | 2026
199 | Lake Geneva South |  | 1051 | Cornier - Chavalon 400 kV |  | RTE | SWISSGRID | - | Cross-border |  | Upgrade of the double circuit 225 kV line between Cornier (France) and Riddes and Saint Triphon (Switzerland) to a single circuit 400 kV line between Cornier and Chavalon (Switzerland). This investment will complement PST solutions around Lake Geneva. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | CORNIER (FR) | CHAVALON (CH) | 400 | Upgrade | Single Circuit | 65 |  |  |  | 01/01/2025 | Under Consideration | 1/ 1/ 2026 | In-depth feasibility studies are needed to find the most suitable solution taking into account socio-environmental conditions. The commissioning date is being reassessed accordingly. | Rescheduled
200 | CZ Northwest-South corridor | 3.11.1; 3.11.2 |  |  | CEPS |  |  |  | Czech - Germany | Mid-term Project | [12 empty] | 290 |  | 58 |  |  | 2022
200 | CZ Northwest-South corridor |  | 306 | R Vitkov |  | CEPS | - | - | Internal |  | New 400/110kV substation equipped with transformers 2x350MVA. | 400 |  | North-South (EAST) | Substation | Design & Permitting | Vitkov (CZ) |  | 500 | New |  |  |  | planned |  | 01/01/2020 | Design & Permitting | 1/ 1/ 2020 | Progress as planned | Investment on time
200 | CZ Northwest-South corridor |  | 307 | R Vernerov |  | CEPS | - | - | Internal |  | New 400/110kV substation equipped with transformers 2x350MVA. | 400 |  | North-South (EAST) | Substation | Under Construction | Vernerov (CZ) |  | 500 | New |  |  |  | planned |  | 01/01/2017 | Design & Permitting | 1/ 1/ 2017 | Progress as planned | Investment on time
200 | CZ Northwest-South corridor |  | 308 | Vernerov-Vitkov |  | CEPS | - | - | Internal |  | New 400kV double circuit OHL, 1385 MVA. | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Vernerov (CZ) | Vitkov (CZ) | 500 | New | Double Circuit | 71 |  | planned |  | 01/01/2019 | Design & Permitting | 1/ 1/ 2023 | Based onCEPS request the competent authority is still in the process to changethe status of the project to "public-interest project". | Delayed
200 | CZ Northwest-South corridor |  | 309 | Vitkov-Prestice |  | CEPS | - | - | Internal |  | New 400kV double circuit OHL, 2x1730 MVA. | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Vitkov (CZ) | Prestice (CZ) | 500 | New | Double Circuit | 86 |  | under consideration |  | 01/01/2021 | Design & Permitting | 1/ 1/ 2020 | Changes due to the delay of other investment connecting substation Vitkov | Ahead of time
200 | CZ Northwest-South corridor |  | 312 | R Mirovka |  | CEPS | - | - | Internal |  | Upgrade of the existing substation 400/110kV with two transformers 2x350MVA. | 400 |  | North-South (EAST) | Substation | Design & Permitting | Mirovka (CZ) |  | 300 | New |  |  |  | planned |  | 01/01/2020 | Design & Permitting | 1/ 1/ 2020 | Progress as planned | Investment on time
200 | CZ Northwest-South corridor |  | 314 | Mirkovka-V413 |  | CEPS | - | - | Internal |  | New double circuit OHL with a capacity of 2x1385 MVA and 26.5km length. | 400 | AC | North-South (EAST) | Overhead Line | Design & Permitting | Mirovka (CZ) | V413 (CZ) | 200 | New | Double Circuit | 27 |  | planned |  | 01/01/2020 | Design & Permitting | 1/ 1/ 2018 | Project rescheduled due to changes of transmission projects to harmonize construction phases. | Ahead of time
203 | Aragón-Castellón | 2.25 (2.25.1 & 2.25.2) |  |  | REE |  |  |  | Internal boundary in the east of Spain | Mid-term Project | [12 empty] | 130 |  | 13 |  |  | 2016
203 | Aragón-Castellón |  | 537 | New substation Mudejar |  | REE | - | - | Internal |  | New 400kV substation Mudejar and connection to the axis Aragón-Teruel | 400 |  | No EC Regional Group linked | Substation | Commissioned | Mudejar (ES) |  | 1420 | New |  |  |  | design & permitting |  | 01/01/2016 | Design & Permitting |  |  | Commissioned ahead of time
203 | Aragón-Castellón |  | 538 | Morella-La Plana |  | REE | - | - | Internal |  | Southern part of the new Cantabric-Mediterranean axis. New double circuit Morella-la Plana 400kV-OHL. | 400 | AC | No EC Regional Group linked | Overhead Line | Permitting | Morella (ES) | La Plana(ES) | 1420 | New | Double Circuit | 78 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 1/ 1/ 2018 | The investment progressed as previously planned | Investment on time
203 | Aragón-Castellón |  | 1069 | Mezquita-Morella |  | REE | - | - | Internal |  | Mezquita-Morella 400 kV line | 400 | AC | No EC Regional Group linked | Overhead Line | Permitting | Mezquita | Morella | 1420 | New | Double Circuit | 68 |  |  |  | 01/01/2017 | Design & Permitting | 1/ 1/ 2017 | Final phase of permitting. Construction will start soon. | Investment on time
203 | Aragón-Castellón |  | 1070 | Mudejar-Morella |  | REE | - | - | Internal |  | OHL 400kV AC Mudejar-Morella | 400 | AC | No EC Regional Group linked | Overhead Line | Commissioned | Mudejar | Morella | 1420 | New | Double Circuit | 34 |  |  |  | 01/01/2017 | Design & Permitting |  |  | Commissioned ahead of time
204 | Grid extension between Thuringa and Bavaria |  |  |  | 50HERTZ;TENNET-DE |  |  |  | Internal Project | Long-term Project | [12 empty] | 160 |  | 24 |  |  | 2024
204 | Grid extension between Thuringa and Bavaria |  | 686 | Altenfeld-Grafenrheinfeld |  | TENNET-DE | 50HERTZ | - | Internal |  | New double circuit OHL 380-kV-line (130 km). Due to ongoing political discussions a change of the connection point Grafenrheinfeld is under consideration. | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Schalkau / area of Altenfeld (DE) | area of Grafenrheinfeld (DE) | 2408 | New | Double Circuit | 130 |  | under consideration |  | 01/01/2024 | Under Consideration | 1/ 1/ 2024 | In time relative to TYNDP14. | Investment on time
205 | South-West Interconnector | 3.13 |  |  | 50HERTZ;TENNET-DE |  |  |  | Internal Project | Mid-term Project | [12 empty] | 400 |  | 20 |  |  | 2016
205 | South-West Interconnector |  | 153 | Redwitz - Grafenrheinfeld |  | TENNET-DE | - | - | Internal |  | Upgrade of 220kV connection Redwitz - Grafenrheinfeld to 380kV, including new 380kV switchgear Eltmann. Line length -97km. | 380 | AC | No EC Regional Group linked | Overhead Line | Commissioned | Redwitz (DE) | Grafenrheinfeld (DE) | 2473 | Upgrade | Single Circuit | 97 |  | design & permitting |  | 01/01/2015 | Design & Permitting | 1/ 1/ 2015 | in time relative to TYNDP14 | Investment on time
205 | South-West Interconnector |  | 193 | Südwestkuppelleitung |  | 50HERTZ | TENNET-DE | - | Internal |  | New 380kV double-circuit OHL between the substations Vieselbach-Altenfeld-Redwitz with 215km length combined with upgrade between Redwitz and Grafenrheinfeld (see investment 153). The Sections Lauchstädt-Vieselbach and Vieselbach-Altenfeld has already been commissioned. Support of RES integration in Germany, annual redispatching cost reduction, maintaining of security of supply and support of the market development. The line crosses the former border between Eastern and Western Germany and is right downstream in the main load flow direction. The project will help to avoid loop flows through neighboring grids. | 380 | AC | North-South (EAST) | Overhead Line | Under Construction | Vieselbach (DE) | Redwitz (DE) | 3583 | New | Double Circuit | 92 |  | design & permitting |  | 01/01/2015 | Design & Permitting | 1/ 1/ 2016 | 3rd section (Altenfeld – Redwitz) is under construction now, long permitting process with strong public resistance. | Delayed
206 | Reinforcement Southern DE |  |  |  | TENNET-DE;TRANSNET-BW |  |  |  | inside-inside | Long-term Project | [12 empty] | 570 |  | 90 |  |  | 2024
206 | Reinforcement Southern DE |  | 682 | Großgartach - Endersbach |  | TRANSNET-BW | - | - | Internal |  | AC-extension of the "C corridor" at one ending point in Southern Germany towards the consumption areas allowing the existing grid to deal with the additionnal flows from DC-link | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Großgartach (DE) | Endersbach (DE) | 1340 | New | Quadruple Circuit | 32 |  | under consideration |  | 01/01/2019 | Planning | 1/ 1/ 2020 | Standard processing | Rescheduled
206 | Reinforcement Southern DE |  | 687 | Redwitz - Schwandorf |  | TENNET-DE | - | - | Internal |  | New double circuit OHL 380 kV line in existing OHL corridor Redwitz-Mechlenreuth-Etzenricht-Schwandorf (185 km) | 380 | AC | No EC Regional Group linked | Overhead Line | Permitting | Redwitz (DE) | Schwandorf (DE) | 1218 | New | Double Circuit | 185 |  | under consideration |  | 01/01/2020 | Planning | 1/ 1/ 2023 | Delay due to long permitting process | Delayed
206 | Reinforcement Southern DE |  | 688 | Altheim - Isar |  | TENNET-DE | - | - | Internal |  | New 380 kV line in existing OHL corridor Raitersaich - Ludersheim - Sittling - Altheim (160 km) | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Raitersaich (DE) | Altheim (DE) | 1902 | New | Double Circuit | 160 |  | under consideration |  | 01/01/2024 | Under Consideration | 1/ 1/ 2024 | in time relative to TYNDP 2014 | Investment on time
206 | Reinforcement Southern DE |  | 990 | Grafenrheinfeld - Großgartach |  | TRANSNET-BW | TENNET-DE | - | Internal |  | AC-extension of the "C corridor" between two of its ending points in Southern Germany allowing the existing grid to deal with the additionnal flows from DC-link. | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Grafenrheinfeld (DE) | Großgartach (DE) | 4310 | New | Double Circuit | 158 |  |  |  | 01/01/2019 | Planning | 1/ 1/ 2020 | Standard processing | Rescheduled
207 | Reinforcement Northwestern DE |  |  |  | TENNET-DE |  |  |  | inside-inside | Long-term Project | [12 empty] | 610 |  | 90 |  |  | 2024
207 | Reinforcement Northwestern DE |  | 675 | Unterweser - Conneforde |  | TENNET-DE | - | - | Internal |  | Upgrade of 220-kV-circuit Unterweser-Conneforde to 380kV , Line length; 32 km. | 380 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Conneforde (DE) | Unterweser (DE) | 4068 | Upgrade | Double Circuit | 32 |  | under consideration |  | 01/01/2024 | Under Consideration | 1/ 1/ 2024 | on time relative to TYNDP14 | Investment on time
207 | Reinforcement Northwestern DE |  | 676 | Dollern - Elsfleth/West |  | TENNET-DE | - | - | Internal |  | New 380 kV line in existing OHL corridor Dollern - Elsfleht/West Length;100 km | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Dollern (DE) | Elsfleht/West (DE) | 2849 | New | Double Circuit | 100 |  | under consideration |  | 01/01/2024 | Under Consideration | 1/ 1/ 2024 | on time relative to TYNDP14 | Investment on time
207 | Reinforcement Northwestern DE |  | 939 | Conneforde - Emden |  | TENNET-DE | - | - | Internal |  | New 380-kV-line in existing OHL corridor for integration of RES | 380 | AC | No EC Regional Group linked | Overhead Line | Permitting | Conneforde | Emden/Ost | 3336 | New | Double Circuit | 60 |  |  |  | 01/01/2019 | Planning | 1/ 1/ 2021 | Delay due to long permitting process | Delayed
207 | Reinforcement Northwestern DE |  | 940 | Emden - Halbemond |  | TENNET-DE | - | - | Internal |  | New 380-kV-line Emden - Halbemond for RES integration incl. new transformers in Halbemond | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Emden/Ost | Halbemond | 3336 | New | Double Circuit | 25 |  |  |  | 01/01/2021 | Under Consideration | 1/ 1/ 2022 | Delay due to long permitting process | Delayed
208 | RES-Integration in North-West Germany 1 |  |  |  | AMPRION;TENNET-DE |  |  |  | Internal Project | Mid-term Project | [12 empty] | 810 |  | 120
208 | RES-Integration in North-West Germany 1 |  | 150 | Conneforde-Wilhelmshaven |  | TENNET-DE | - | - | Internal |  | New 380kV double circuit (OHL, partly underground) Conneforde - Wilhelmshaven (Fedderwarden, former Maade) including new 380kV switchgear Fedderwarden. Length&#58; 35 km. | 380 | AC | No EC Regional Group linked | Overhead Line | Permitting | Conneforde (DE) | Fedderwarden (DE) | 3668 | New | Double Circuit | 35 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 1/ 1/ 2020 | Delay due to long permitting process | Delayed
208 | RES-Integration in North-West Germany 1 |  | 151 | Ganderkesee - Wehrendorf |  | TENNET-DE | AMPRION | - | Internal |  | New line (length&#58; ca. 95km), extension of existing and erection of substations, erection of 380/110kV-transformers. | 380 | AC | No EC Regional Group linked | Overhead Line | Permitting | Wehrendorf (DE) | Ganderkesee (DE) | 3538 | New | Double Circuit | 95 |  | design & permitting |  | 01/01/2017 | Design & Permitting | 1/ 1/ 2021 | Long permitting process and additional longer constructing phase due to requirement of underground cable in some parts of the line. | Delayed
208 | RES-Integration in North-West Germany 1 |  | 156 | Niederrhein-Dörpen |  | AMPRION | TENNET-DE | - | Internal |  | New 380 kV double circuit overhead line Dörpen - Niederrhein including extension of existing substations. | 380 | AC | No EC Regional Group linked | Overhead Line | Permitting | Niederrhein (DE) | Dörpen/West (DE) | 988 | New | Double Circuit | 162 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 1/ 1/ 2019 | Delay due to long permitting process | Delayed
209 | Reinforcement Northeastern DE |  |  |  | TENNET-DE |  |  |  | inside-inside | Mid-term Project | [12 empty] | 160 |  | 30
209 | Reinforcement Northeastern DE |  | 935 | Kreis Segeberg - Siems |  | TENNET-DE | - | - | Internal |  | New 380-kV-lineKreis Segeberg - Lübeck - Siems - Göhl, including five new transformers | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Kreis Segeberg | Göhl | 4482 | New | Double Circuit | 110 |  |  |  | 01/01/2021 | Under Consideration | 1/ 1/ 2022 | Delay due to long permitting process | Delayed
210 | Wurmlach (AT) - Somplago (IT) Interconnection |  |  |  | Alpe Adria Energia SpA |  |  |  | Austria - Italy | Mid-term project | [12 empty] | 60 |  |  |  |  | 2018
210 | Wurmlach (AT) - Somplago (IT) Interconnection |  | 1380 | Wurmlach (AT) - Somplago (IT) Interconnection | [6 empty] | Somplago - Wurmlach interconnection is a third party cross-border electrical line promoted by Alpe Adria Energia SpA​. The project concerns a 220kV a.c. merchant line, 300 MVA from Somplago substation to Wurmlach substation, including a 300MW Phase Shift​ Transformer, located in Austria .​ | 220 | AC |  |  | Permitting | SOMPLAGO | WURMLACH | [9 empty] | 2018 |  | Delayed
214 | Interco Iceland-UK |  |  |  | LANDSNET;NGIHL |  |  |  | Iceland - Great Britain | Future Project
214 | Interco Iceland-UK |  | 1082 | Interco Iceland-UK |  | LANDSNET | - | - | Internal |  | Interco Iceland-UK | 500 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | tbd | tbd | 0 | New | Double Circuit | 1000 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2030 | Increased RES integration and market coupling<br><br> | New Investment
216 | Massif Central North |  |  |  | RTE |  |  |  | Internal boundary in France North-South | Long-term Project | [12 empty] | 500 |  | 100 |  |  | 2030
216 | Massif Central North |  | 999 | North Massif Central |  | RTE | - | - | Internal |  | Erection of a new 400-kV line substituting existing 400-kV or 225-kV lines. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Marmagne or Eguzon | Rueyres | 2700 | New | Double Circuit | 275 |  |  |  | 01/01/2030 | Under Consideration | 1/ 1/ 2030 | This long term investment is needed for scenarios with high RES development in the area, especially wind and hydro and/or with high exchanges with Spain as in all 2030 visions (8GW); additional studies are in progress for better investment definition. | Investment on time
219 | EuroAsia Interconnector |  |  |  | EuroAsia Interconnector |  |  |  | Cyprus - Greece - Israel | Mid-term project | [12 empty] | 4246.9 |  |  |  |  | PCI 3.10.1 12/2019, PCI 3.10.2 12/2022, PCI 3.10.3 12/2020
219 | EuroAsia Interconnector |  | 1407 | EuroAsia Interconnector | [6 empty] | The Euro Asia Interconnector consists of a 400 kV DC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot, Israeli and the Greek transmission networks (offshore). The Interconnector will have a capacity of 2000 MW and a total length of around 820 nautical miles/around 1518 km (approx. 329 km between CY and IL, 879 km between CY and Crete and 310 km between Crete and Athens) and allow for reverse transmission of electricity. | 500 | DC |  |  | Planning | Hadera Site | Vasilikos Site | [9 empty] | 2019
219 | EuroAsia Interconnector |  | 1409 | EuroAsia Interconnector | [6 empty] | The Euro Asia Interconnector consists of a 400 kV DC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot, Israeli and the Greek transmission networks (offshore). The Interconnector will have a capacity of 2000 MW and a total length of around 820 nautical miles/around 1518 km (approx. 329 km between CY and IL, 879 km between CY and Crete and 310 km between Crete and Athens) and allow for reverse transmission of electricity. |  | DC |  |  | Planning | Vasilikos Site | Korakia (Crete)Site | [9 empty] | 2022
219 | EuroAsia Interconnector |  | 1410 | EuroAsia Interconnector | [6 empty] | The Euro Asia Interconnector consists of a 400 kV DC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot, Israeli and the Greek transmission networks (offshore). The Interconnector will have a capacity of 2000 MW and a total length of around 820 nautical miles/around 1518 km (approx. 329 km between CY and IL, 879 km between CY and Crete and 310 km between Crete and Athens) and allow for reverse transmission of electricity. | 500 | DC |  |  |  | Korakia (Crete)Site | Athens Site | [9 empty] | 2020
225 | 2nd interconnector Belgium - Germany |  |  |  | AMPRION;ELIA |  |  |  | Belgium - Germany | Long-term Project | [12 empty] | 500 |  | 100 |  |  | 2025
225 | 2nd interconnector Belgium - Germany |  | 1107 | 2nd interconnecter between Belgium and Germany |  | ELIA | AMPRION | - | Cross-border |  | This investment item envisions the possibility of a second 1 GW HVDC interconnection between Belgium and Germany. Subject to further studies. | 320 | DC | North-South (WEST) | Underground Cable | Planning | to be defined (BE) | to be defined (DE) | 1000 | New | Single Circuit | 100 |  |  |  | 01/01/2030 | Under Consideration | 01/01/2025 | The project has been rescheduled with an indicative date of 2025 related to its potential to security-of-supply (adequacy) contribution within a context of planned nuclear phase out. The evaluation of this potential as well as interaction with reinforcements on neighboring borders are subject of further studies. | Rescheduled
227 | CSE8 Transbalkan Corridor |  |  |  | EMS |  |  |  | inside-outside | Mid-term project | [12 empty] | 131
227 | CSE8 Transbalkan Corridor |  | 627 | 400kV interconnection RS-BA |  | EMS | - | - | Cross-border |  | Description of broader context - New double circuit 400kV OHL connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS) and new double circuit 400kV OHL connecting existing substation Visegrad (BA) and substation Bajina Basta (RS). In the first phase one 400 kV circuit would be equiped. In the second phase New SS Bistrica (RS) would be connected to the exisitng double circuit 400 kV OHL between SS Bajina Basta (RS), SS Visegrad (BA) and SS Pljevlja (ME). Part of regional transmission corridor northeast-southwest. | 400 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Bajina Basta (RS) | Visegrad (BA) | 500 | New | Double Circuit | 45 |  | planned |  | 01/01/2020 | Planning | 2022 | Del_ Financing issues | Delayed
227 | CSE8 Transbalkan Corridor |  | 628 | 400kV OHL B.Basta-Obrenovac |  | EMS | - | - | Internal |  | Double circuit 400 kV OHL between upgraded substation Bajina Basta and substation Obrenovac. Part of larger regional transmission corridor northeast-southwest. | 400 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | SS Bajina Basta (RS) | SS Obrenovac (RS) | 500 | New | Double Circuit | 115 |  | design & permitting |  | 01/01/2019 | Design & Permitting | 2021 | Del_ Financing issues | Delayed
227 | CSE8 Transbalkan Corridor |  | 630 | 400kV interconnection RS-ME |  | EMS | - | - | Cross-border |  | Description of broader context - New double circuit 400kV OHL (105km RS + 16km ME) connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS) and new double circuit 400kV OHL connecting existing substation Visegrad (BA) and substation Bajina Basta (RS). In the first phase one 400 kV circuit would be equiped. In the second phase New SS Bistrica (RS) would be connected to the exisitng double circuit 400 kV OHL between SS Bajina Basta (RS), SS Visegrad (BA) and SS Pljevlja (ME). Part of regional transmission corridor northeast-southwest. | 400 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Bajina Basta (RS) | Pljevlja (ME) | 500 | New | Double Circuit | 121 |  | planned |  | 01/01/2020 | Planning | 2022 | Del_ Financing issues | Delayed
227 | CSE8 Transbalkan Corridor |  | 631 | 400kV SS B.Basta upgrade |  | EMS | - | - | Internal |  | Upgrade of existing 220/110 kV substation in Bajina Basta to 400/220/110 kV substation as part of overall western Serbia system upgrade to 400 kV voltage level. Part of larger regional transmission corridor northeast-southwest. | 400 |  | No EC Regional Group linked | Substation | Design & Permitting | Bajina Basta (RS) |  | 500 | Upgrade |  |  |  | planned |  | 01/01/2019 | Design & Permitting | 2021 | Del_ Financing issues | Delayed
228 | Muhlbach - Eichstetten |  |  |  | RTE;TransnetBW |  |  |  | France - Germany | Long-term Project | [12 empty] | 42 |  | 8 |  |  | 2025
228 | Muhlbach - Eichstetten |  | 1231 | Muhlbach Eichstetten |  | RTE | TRANSNET-BW | - | Cross-border |  | Operation of a second circuit at 400kV OHL Muhlbach - Eichstetten, instead of the currently operated circuit Eichstetten - Vogelgrun at 225kV and reinforcement of the existing circuit 400kV OHL Muhlbach - Eichstetten. Some restructurations on the existing grid may be necessary in the area. Reinforcement of the existing circuit at 400kV OHL Muhlbach - Eichstetten in order to increase the thermal capacity of the line. | 400 | AC | No EC Regional Group linked | Overhead Line | Planning | Muhlbach | Eichstetten | 300 | Upgrade | Double Circuit | 32 | [5 empty] | 2025 | The detailed timeline of the investment is under definition but it is expected works should be completed slightly before initially thought. | Rescheduled
229 | GerPol Power Bridge II | 3.14 |  |  | 50Hertz; PSE |  |  |  | Poland - Germany | Future Project | [12 empty] | 200 |  | 50 |  |  | >2030
229 | GerPol Power Bridge II |  | 1270 | Baczyna-Zielona Góra |  | PSE | - | - | Internal |  | Indentation to the 2x400 kV line Baczyna - Plewiska (construction 40 km new 2x400 kV line from new substation Zielona Góra to the point of indentation). Creating new route 2x 400 kV Baczyna - Zielona Góra. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Baczyna-Plewiska Indentation | Zielona Góra | 750 | New | Double Circuit | 40 | [5 empty] | >2030 |  | Investment on time
229 | GerPol Power Bridge II |  | 1271 | Zielona Góra - Plewiska |  | PSE | - | - | Internal |  | Indentation to the 2x400 kV line Baczyna - Plewiska (construction 40 km new 2x400 kV line from new substation Zielona Góra to the point of indentation). Creating new 2x400 kV route Zielona Góra - Plewiska. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Zielona Góra | Plewiska | 750 | New | Double Circuit | 40 | [5 empty] | >2030 |  | Investment on time
229 | GerPol Power Bridge II |  | 1272 | Zielona Góra |  | PSE | - | - | Internal |  | Construction of new substation 400/110 kV Zielona Góra to connect 400 kV lines : Baczyna - Zielona Góra, Zielona Góra - Plewiska, Zielona Góra - Gubin | 400 |  | No EC Regional Group linked | Substation | Under Consideration | Zielona Góra |  | 1500 | New | Single Circuit | [6 empty] | >2030 |  | Investment on time
229 | GerPol Power Bridge II |  | 1273 | Zielona Góra-Gubin |  | PSE | - | - | Internal |  | Construction of new 2x400 kV line from new substation Zielona Góra to new substation Gubin | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Zielona Góra | Gubin | 1500 | New | Double Circuit | 60 | [5 empty] | >2030 |  | Investment on time
229 | GerPol Power Bridge II |  | 1274 | Gubin |  | PSE | - | - | Internal |  | Construction of new 400 kV substation Gubin to connect new 400 kV lines: 2x400 kV Zielona Góra - Gubin and crossborder 2x400 kV line Gubin - Eisenhuettenstadt with PST installation on crossborder line Gubin - Eisenhuettenstadt | 400 |  | No EC Regional Group linked | Substation | Under Consideration | Gubin |  | 1500 | New | [7 empty] | >2030 |  | Investment on time
229 | GerPol Power Bridge II |  | 1275 | Gubin - Eisenhuettenstadt |  | PSE | 50HERTZ | - | Cross-border |  | Construction of new crossborder 2x400 kV line between new substation Gubin (PL) end existing substation Eisenhuettenstadt (DE) | 400 |  | No EC Regional Group linked | Overhead Line | Under Consideration | Gubin | Eisenhuettenstadt | 1500 | New | Double Circuit | 20 | [5 empty] | >2030 |  | Investment on time
230 | GerPol Power Bridge I | 3.14 |  |  | 50Hertz; PSE |  |  |  | Poland - Germany | Mid-term Project | [12 empty] | 292 |  | 20 |  |  | 2022
230 | GerPol Power Bridge I |  | 353 | Krajnik-Baczyna |  | PSE Tyndp_project_promoter | - | - | Internal |  | Construction of new 400 kV double circuit line Krajnik – Baczyna. | 400 | AC | North-South (EAST) | Overhead Line | Planning | Krajnik (PL) | Baczyna (PL) | 750 | New | Double Circuit | 70 |  | planned |  | 01/01/2020 | Planning | 31/12/2021 | The investment will enter the tendering procedure in 2016 and will be realized in design and build scheme. The line is planned to be operational in 2020. | Investment on time
230 | GerPol Power Bridge I |  | 355 | Mikułowa - Świebodzice |  | PSE Tyndp_project_promoter | - | - | Internal |  | Construction of new 400 kV double circuit line Mikułowa-Świebodzice in place of existing 220 kV line. | 400 | AC | North-South (EAST) | Overhead Line | Planning | Mikułowa (PL) | Świebodzice (PL) | 750 | New | Double Circuit | 100 |  | planned |  | 01/01/2020 | Planning | 31/12/2021 | The investment will enter the tendering procedure in 2016 and will be realized in design and build scheme. The line is planned to be operational in 2020. | Investment on time
230 | GerPol Power Bridge I |  | 1035 | Baczyna |  | PSE Tyndp_project_promoter | - | - | Internal |  | Construction of new 400/110 kV Substation Baczyna to connect the new line Krajnik-Baczyna. | 400 |  | North-South (EAST) | Substation | Permitting | Baczyna |  | 750 | New | [5 empty] | 01/01/2018 | Planning | 12/06/2020 | The investment is in the tendering procedure (design and build scheme). The investment is planned to be completed in 2020. Change of commissioning date compared to previous reprting due to realization schedule of other investements (line Krajnik-Baczyna and Baczyna-Plewiska). | Delayed
230 | GerPol Power Bridge I |  | 1232 | Baczyna-Plewiska |  | PSE | - | - | Internal |  | Construction of new 400 kV double circuit line Baczyna - Plewiska | 400 | AC | North-South (EAST) | Overhead Line | Planning | Baczyna | Plewiska | 750 | New | Double Circuit | 142 | [5 empty] | 31/12/2020 |  | New Investment
231 | Concept Project DE-CH |  |  |  | swissgrid;Amprion;TransnetBW |  |  |  | Germany - Switzerland | Future Project | [17 empty] | 2030
231 | Concept Project DE-CH |  | 1282 | 380 kV Grid Reinforcement Beznau - Tiengen |  | AMPRION | SWISSGRID | TRANSNET-BW | Cross-border |  | This projects helps to increase the cross border capacity between Switzerland and Germany by upgrading an existing line from 220 kV to 380 kV including internal reinforcements. | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Beznau (CH) | Tiengen (DE) |  | Upgrade | Single Circuit | [6 empty] | 01/01/2030 |  | New Investment
231 | Concept Project DE-CH |  | 1457 | Additional measures |  | AMPRION | SWISSGRID | TRANSNET-BW | Cross-border |  |  | 380 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | [11 empty] | 2030 |  | New Investment
232 | Kontek-3 |  |  |  | 50Hertz Transmission;Energinet.dk. |  |  |  | Denmark-East - Germany | Future Project | [12 empty] | 360 |  | 100 |  |  | >2030
232 | Kontek-3 |  | 1234 | Investments to be created |  | ENERGINET | 50HERTZ | - | Cross-border |  | ​The third HVDC connector between Denmark-East and Germany, "Kontek-3" | 400 | DC | No EC Regional Group linked | Overhead Line | Under Consideration |  |  | 600 | New | Single Circuit | [6 empty] | > 2030 |  | New Investment
233 | Spanish Pumping |  |  |  | REE |  |  |  | Internal boundary in Spain (generation) | Future Project | [17 empty] | 2025
233 | Spanish Pumping |  | 1235 | Conceptual project |  | REE | - | - | Internal |  |  | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration |  |  |  |  | Single Circuit | [6 empty] | 2025 |  | New Investment
234 | DKE-PL-1 |  |  |  | Energinet.dk |  |  |  | Denmark-East - Poland | Future Project | [12 empty] | 700 |  | 100 |  |  | >2030
234 | DKE-PL-1 |  | 1236 | DKE-PL-1 |  | ENERGINET | - | - | Cross-border |  | The first HVDC connector between Denmark-East and Poland |  | DC | No EC Regional Group linked | Overhead Line | Under Consideration | Avedøre (DK) | Dunowo (PL) | 600 | New | Single Circuit | 330 | [5 empty] | >2030 |  | New Investment
235 | HVDC Brunsbüttel/Wilster to Großgartach/Grafenrheinfeld | 2.10 |  |  | TenneT TSO;TransnetBW |  |  |  | Inside Germany | Mid-term Project | [12 empty] | 6500 |  | 1300 |  |  | 2022
235 | HVDC Brunsbüttel/Wilster to Großgartach/Grafenrheinfeld |  | 664 | HVDC Line C |  | TENNET-DE | TRANSNET-BW | - | Internal |  | New DC-lines to integrate new wind generation from Northern Germany towards Southern Germany and Southern Europe for consumption and storage. | 500 | DC | North-South (WEST) | Overhead Line | Planning | Brunsbüttel, Wilster | Großgartach, Grafenrheinfeld | 3575 | New | Double Circuit | 770 |  | under consideration |  | 01/01/2022 | Planning | 1/ 1/ 2025 | The commissioning date of the investment is delayed due to new preference of underground cable instead of overhead lines by german legal requirement. | Delayed
236 | Internal Belgian Backbone West | 2.24 |  |  | Elia System Operator |  |  |  | Internal Belgium Backbone West | Mid-term Project | [12 empty] | 100 |  | 15 |  |  | 2019
236 | Internal Belgian Backbone West |  | 608 | Horta-Mercator: HTLS upgrade |  | ELIA | - | - | Internal |  | The project consists of replacing the current double circuit 380 kV overhead line between Horta and Mecator with high performance conductors. The 380kV circuit currently bypassing Mercator onwards to Doel will be integrated into the Mercator substation to obtain a better flux balance and avoid an upgrade between Mercator & Doel at this stage. | 380 | AC | North-South (WEST) | Overhead Line | Permitting | Horta (BE) | Mercator (BE) | 1500 | Upgrade | Double Circuit | 50 |  | design & permitting |  | 01/01/2020 | Design & Permitting | 01/01/2019 | The expected commissioning date of 2019 is based on the hypothesis of acquiring all necessary permits as planned. | Investment on time
237 | COBRA-2 |  |  |  | Energinet.dk.dk;TenneT TSO |  |  |  | Denmark-West - Netherlands | Future Project | [12 empty] | 620 |  | 60 |  |  | >2030
237 | COBRA-2 |  | 1239 | Investments to be created |  | - | - | - | Cross-border |  | ​The second HVDC connector between Denmark-West and The Netherlands. |  | DC | No EC Regional Group linked | Overhead Line | Under Consideration |  |  | 700 | New | Single Circuit | [6 empty] | > 2030 | potential project resulting from common planning studies analysis from ENTSO-E RGNS. | New Investment
238 | Kontiskan 2 |  |  |  | Energinet.dk.dk;Svenska Kraftnät |  |  |  | Denmark-West - Sweden (SE3) | Future Project | [17 empty] | 2030
238 | Kontiskan 2 |  | 1240 | Kontiskan 2 - Renewal |  | SVK | ENERGINET | - | Cross-border |  | Renewal of the existing Kontiskan 2 HVDC interconnector between Denmark-West (DK1) and Sweden (SE3) to maintain capacity between Sweden and Denmark. | 300 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Lindome (SE3) | Vester Hassing (DkV) | 300 | Missing Data | Single Circuit | 90 | [5 empty] | >2030 |  | New Investment
239 | Fenno-Skan 1 renewal |  |  |  | Fingrid;Svenska Kraftnät |  |  |  | Finland-Sweden (SE3) | Future Project | [12 empty] | 500 |  | 50 |  |  | 2030
239 | Fenno-Skan 1 renewal |  | 1241 | Fenno-Skan 1 renewal |  | SVK | FINGRID | - | Cross-border |  | Renewal of the existing 400 kV HVDC cable interconnection between Finland and Sweden. The projects capacity is estimated to range between 500-800 MW which could mean an updgrade compared to today. | 400 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Dannebo (SE3) | Rauma (FI) | 500 | Missing Data | Single Circuit | 200 | [5 empty] | 2030+ |  | New Investment
240 | 380-kV-grid enhancement between Area Güstrow/Bentwisch and Wolmirstedt |  |  |  | 50Hertz Transmission |  |  |  | Internal Project | Mid-term Project | [12 empty] | 370 |  | 60 |  |  | 2020
240 | 380-kV-grid enhancement between Area Güstrow/Bentwisch and Wolmirstedt |  | 200 | Güstrow - Wolmirstedt |  | 50HERTZ | - | - | Internal |  | 380-kV-grid enhancement and structuralchange Magdeburg/Wolmirstedt, incl. 380-kV-lineGustrow-Wolmirstedt (195 km). | 380 | AC | North-South (EAST) | Overhead Line | Permitting | Güstrow (DE) | Wolmirstedt (DE) | 0 | New | Double Circuit | 195 |  | planned |  | 01/01/2020 | Planning | 2020 | Investment on time | Investment on time
240 | 380-kV-grid enhancement between Area Güstrow/Bentwisch and Wolmirstedt |  | 1242 | AC Upgrade Bentwisch-Güstrow |  | 50HERTZ | - | - | Internal |  | AC Upgrade (220 kV to 380 kV) of existing line between Bentwisch and Güstrow. | 380 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Bentwisch (DE) | Güstrow (DE) |  | Upgrade | Double Circuit | 36 | [5 empty] | 2025 |  | New Investment
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines |  |  |  | HOPS;NOS BiH |  |  |  | Croatia - Bosnia and Herzegovina | Long-term Project | [12 empty] | 62 |  | 6 |  |  | 2030
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines |  | 1276 | Upgrading of existing 220 kV line between SS Đakovo (HR) and SS Tuzla (BA) to 400 kV line |  | HOPS | NOS-BIH | - | Cross-border |  | The project necessity stems for the need to increase the target transfer capacity between HR and BA in order to accommodate market integration and exploitation of RES, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4. | 400 | AC | North-South (EAST) | Overhead Line | Under Consideration | Đakovo | Tuzla | 500 | Upgrade | Single Circuit | 91 | [5 empty] | 31/12/2030 | Based on the results by the Common Planning Studies based on Vision 4.Project will increase the transfer capacity between BA and HR in order to accommodate connection of RES and improve market integration. | New Investment
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines |  | 1277 | Upgrading of existing 220 kV line between SS Đakovo (HR) and Gradačac (BA) to 400 kV line |  | HOPS | NOS-BIH | - | Cross-border |  | The project necessity stems for the need to increase the target transfer capacity between HR and BA in order to accommodate market integration and exploitation of RES, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4. | 400 | AC | North-South (EAST) | Overhead Line | Under Consideration | Đakovo | Gradačac | 500 | Upgrade | Single Circuit | 46.2 | [5 empty] | 31/12/2030 | Based on the results by the Common Planning Studies based on Vision 4.Project will increase the transfer capacity between BA and HR in order to accommodate connection of RES and improve market integration. | New Investment
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines |  | 1278 | Upgrading existing 220 kV SS Đakovo to 400 kV |  | HOPS | - | - | Internal |  | Upgrading existing 220 kV SS Đakovo to 400 kV enables connection between SS Đakovo (HR) and SS Tuzla/Gradačac (BA) by 400 kV lines. | 400 |  | North-South (EAST) | Substation | Under Consideration | Đakovo |  | 500 | Upgrade | Single Circuit | [6 empty] | 31/12/2030 | Based on the results by the Common Planning Studies based on Vision 4.Project will increase the transfer capacity between BA and HR in order to accommodate connection of RES and improve market integration. | New Investment
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines |  | 1279 | New double 400 kV line between SS Đakovo and location Razbojište |  | HOPS | - | - | Internal |  | New double 400 kV line between SS Đakovo and location Razbojište enables connection of planned 400 kV SS Đakovo to existing 400 kV line Žerjavinec - Ernestinovo | 400 | AC | North-South (EAST) | Overhead Line | Under Consideration | Đakovo | Razbojište | 500 | New | Double Circuit | 25 | [5 empty] | 31/12/2030 | Based on the results by the Common Planning Studies based on Vision 4.Project will increase the transfer capacity between BA and HR in order to accommodate connection of RES and improve market integration. | New Investment
242 | Offshore Wind Baltic Sea (I) |  |  |  | 50Hertz Transmission |  |  |  | Internal Boundary in North-East Germany | Mid-term Project | [12 empty] | 1800 |  | 200 |  |  | 2018
242 | Offshore Wind Baltic Sea (I) |  | 194 | Offshore Wind Baltic Sea (I) |  | 50HERTZ | - | - | Internal |  | ​AC grid connections connecting Offshore Wind Farms in Cluster 1 of the Baltic Sea (see German Offshore Grid Development Plan). Cluster 1 is located north east of Rügen in the German Exclusive Economic Zone. According to german law, the grid connection has to be constructed and operated by the TSO (50Hertz Transmission). | 220 | AC | No EC Regional Group linked | Subsea Cable | Under Construction | OWF Cluster Baltic Sea East (DE) | Lubmin (DE) | 750 | New | Single Circuit | 115 |  | design & permitting |  | 01/01/2031 | Design & Permitting | 2018 | The investment is split into different stages with different commissioning dates (starting in 2017) depending on the predicted installed capacity of offshore wind. For further informations see the national "Offshore Grid Development Plan" | Investment on time
243 | New 400 kV interconnection line between Serbia and Croatia |  |  |  | HOPS;JP EMS |  |  |  | Croatia - Serbia | Future Project | [12 empty] | 19 |  | 2 |  |  | 2030
243 | New 400 kV interconnection line between Serbia and Croatia |  | 1269 | New 400 kV overhead line Sombor (RS) – Ernestinovo (HR) |  | HOPS | EMS | - | Cross-border |  | The project necessity stems for the need to increase the transfer capacity between RS and HR in order to accommodate connection of RES and improve market integration, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4. | 400 | AC | North-South (EAST) | Overhead Line | Under Consideration | Ernestinovo | Sombor | 500 | New | Single Circuit | 70 | [5 empty] | 31/12/2030 | Based on the results by the Common Planning Studies based on Vision 4.Project will increase the transfer capacity between RS and HR in order to accommodate connection of RES and improve market integration. | New Investment
244 | Vigy - Uchtelfangen area |  |  |  | Amprion;RTE |  |  |  | France - Germany | Long-term Project | [12 empty] | 25 |  | 15 |  |  | 2030
244 | Vigy - Uchtelfangen area |  | 1245 | Vigy Uchtelfangen (or beyond) |  | RTE | AMPRION | - | Cross-border |  | Upgrade of existing transmission OHL between Vigy and Uchtelfangen (or beyond) to increase its capacity. Dynamic Line Rating (DLR) or High Temperature Low Sag (HTLS) conductors are the two investigated options. | 400 | AC | No EC Regional Group linked | Overhead Line | Planning | Vigy (FR) | Uchtelfangen (DE) | 1500 | Upgrade | Double Circuit | 65 | [5 empty] | 2030 |  | Investment on time
245 | 201 Upgrade Meeden - Diele |  |  |  | TenneT TSO;TenneT TSO GmbH |  |  |  | Netherlands - Germany | Mid-term project | [17 empty] | 2019
245 | 201 Upgrade Meeden - Diele |  | 1246 | Upgrade Meeden - Diele |  | - | - | - | Cross-border |  |  | 380 |  | No EC Regional Group linked | Overhead Line | Planning | Meeden [NL] | Diele [DE] |  | Upgrade | Double Circuit | 27 | [5 empty] | 01-01-2019 | Engineering completed, permits requested, construction planned. | Investment on time
247 | AQUIND Interconnector |  |  |  | Aquind Limited |  |  |  | France - Great Britain | Future project | [12 empty] | 1400 |  |  |  |  | 2020
247 | AQUIND Interconnector |  | 1381 | AQUIND Interconnector | [6 empty] | ​AQUIND Interconnector is being promoted by Aquind Limited, a UK-based company. The project is a high capacity double-circuit interconnector with the capacity of up to 2000MW between the AC transmission networks in France and the United Kingdom. To maintain the asynchronous nature of these two networks, the interconnector will use the DC technology.The interconnector will land and connect to the UK grid in the South East of England in Portsmouth area. The connection point in France will be on the Normandy Coast.​ Particular substations on both sides are to be determined. The DC transmission voltage is still to be confirmed, but is anticipated to be in the range between ±320kV and ±563kV, depending upon the final configuration of the scheme. Underground cables of 20 – 30km will link the French converter station to a transition joint on the coast at a point south-west of Le Havre. Submarine cables of 170 – 190km will run across La Manche (the English Channel) to the south coast of the United Kingdom. Underground cables of 15 – 25km will run from the transition joint at the coast landing point to the British converter station. Desktop studies of the coast landing points and the submarine route have been performed, but the final cable routing will be dependent on detailed land and marine surveys. The promoter has completed the project definition stage and has commenced the development stage of the project consisting of more detailed engineering and other studies, supply chain selection and the scope of work definition, obtaining of various permits, authorisations, licenses and connections agreements. |  | DC | No EC Regional Group linked |  | Planning | Lovedean (UK) | Le Havre (FR) | [9 empty] | 2020 | Planning status (though the project is simultaneously progressing some elements of the design and permitting activities) | New Investment
248 | Offshore Wind Baltic Sea (II) |  |  |  | 50Hertz Transmission |  |  |  | Internal Boundary in North-East Germany | Long-term Project | [12 empty] | 1200 |  | 800 |  |  | 2026
248 | Offshore Wind Baltic Sea (II) |  | 1248 | Offshore Wind Baltic (II) |  | 50HERTZ | - | - | Internal |  | AC grid connections connecting Offshore Wind Farms in Cluster 1, 2 or 4 of the Baltic Sea (see German Offshore Grid Development Plan). Clusters are located north east of Rügen mainly in the German Exclusive Economic Zone. | 220 | AC | No EC Regional Group linked | Subsea Cable | Under Consideration |  |  | 500 |  | Single Circuit | [6 empty] | 2026 |  | Investment on time
249 | Façade Atlantique |  |  |  | RTE |  |  |  | Internal boundary in south-western France | Future Project | [12 empty] | 700 |  | 200 |  |  | 2030
249 | Façade Atlantique |  | 1219 | Cubnezais - Marmagne |  | RTE | - | - | Internal |  | ​New double 400 kV line in place of existing single circuit line from Cubnezais to Marmagne. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Cubnezais | Marmagne | 3000 | New | Double Circuit | 300 | [5 empty] | 2030 | This investment is necessary to transmit the RES generation from France and Iberian peninsula | New Investment
249 | Façade Atlantique |  | 1221 | Marmagne - Tabarderie |  | RTE | - | - | Internal |  | ​Changing conductors on the existing lines. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Marmagne | Tabarderie | 3500 | Upgrade | Double Circuit | 80 | [5 empty] | 2030 | This investment is necessary to accomodate the north to south and south to north flows increased by large changes in the generation pattern. | New Investment
250 | Merchant line "Castasegna (CH) - Mese (IT)" |  |  |  | Repower |  |  |  | Italy - Switzerland | Mid-term project | [12 empty] | 90 |  |  |  |  | 2018
250 | Merchant line "Castasegna (CH) - Mese (IT)" |  | 1384 | Merchant line "Castasegna (CH) - Mese (IT)" | [6 empty] | The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Rationalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200 MW. The main Project elements are (merchant line):220 kV Connection to the Swiss HVG in Castasegna220 kV Cable line of around 14 km between Castasegna and Mese220/380 kV Substation with PST 250 MVA in Mese The Grid Rationalisation in the Region of Mese foresees the following actions:Displacement of 2 km of the 380 kV Line "Soazza – Bulciago"Realisation of a new 380/132 kV Substation in Mese (Transformation 2 x 250 MVA)Displacement of 0.8 km of 132 kV LinesRealisation of 2.6 km of 132 kV Cable connectionsDemolition of 2.45 km of 380 kV line and 2.3 km of 132 kV lines | 220 | AC |  |  | Design & permitting | Castasegna | Mese | [9 empty] | 2019
251 | Audorf-Dollern | 1.4.2, 1.4.3 |  |  | Tennet-DE |  |  |  | Inside Germany | Mid-term Project | [12 empty] | 330 |  | 50 |  |  | 2017
251 | Audorf-Dollern |  | 147 | Dollern - Hamburg/Nord |  | TENNET-DE | - | - | Internal |  | New 380kV double circuit OHL Dollern - Hamburg/Nord. Length - 43km.First circuit 2015, second cicuit 2017 | 380 | AC | North Seas Countries Offshore Grid Initiative | Overhead Line | Under Construction | Dollern (DE) | Hamburg/Nord (DE) | 2008 | New | Double Circuit | 43 |  | design & permitting |  | 01/01/2017 | Under Construction | 1/ 1/ 2018 | Delay due to long permitting process | Delayed
251 | Audorf-Dollern |  | 148 | Audorf - Hamburg/Nord |  | TENNET-DE | - | - | Internal |  | New 380kV double circuit OHL Audorf - Hamburg/Nord including two new 380/220kV transformers in substation Audorf and new 380 kV Switchgear in Kummerfeld. Length - 65km. | 380 | AC | North Seas Countries Offshore Grid Initiative | Overhead Line | Under Construction | Audorf (DE) | Hamburg/Nord (DE) | 2410 | New | Double Circuit | 65 |  | design & permitting |  | 01/01/2017 | Design & Permitting | 1/ 1/ 2018 | Delay due to long permitting process | Delayed
252 | Internal Belgian Backbone East |  |  |  | Elia System Operator |  |  |  | Internal Belgian Backbone East | Mid-term Project | [12 empty] | 150 |  | 30 |  |  | 2025
252 | Internal Belgian Backbone East |  | 1456 | Massenhoven - Van Eyck |  | ELIA | - | - | Internal |  |  | 380 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Massenhoven (BE) | Van Eyck (BE) |  | Upgrade | Single Circuit | 90 | [5 empty] | 01/01/2025 | The need for this project towards 2020-2025 horizon is to be further monitored in accordance with the evolution of transitflux/interconnection capacity on the surrounding borders, and with the perspective of evolution in the production park. | Investment on time
252 | Internal Belgian Backbone East |  | 1050 | Van Eyck - Gramme |  | ELIA | - | - | Internal |  | Further reinforcement of the 380 kV overhead line Gramme-Van Eyck by upgrading the following line sections to high-performance conductors i) 55km double circuit between Gramme-Zutendaal ii) 30 km single circuit Zutendaal Van Eyck iii) 10 km single circuit Lixhe-Herderen | 380 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Van Eyck | Gramme | 1400 | Upgrade | Double Circuit | 90 |  |  |  | 01/01/2020 | Planning | 01/01/2025 | The need for this investment towards 2020-2025 horizon is to be further monitored in accordance with the evolution of transitflux/interconnection capacity on the surrounding borders, and with the evolution in the production park i.e. planned nuclear phase out and potential of new production units that could be deployed within the area. | Investment on time
253 | Upstream reinforcement in France to increase FR-CH capacity |  |  |  | RTE |  |  |  | France - Switzerland | Future Project | [12 empty] | 50 |  | 10 |  |  | 2020
253 | Upstream reinforcement in France to increase FR-CH capacity |  | 1224 | Uprate of Creys-St Vulbas |  | RTE | - | - | Internal |  |  | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Creys(FR) | Saint Vulbas (FR) | 700 | Upgrade | Double Circuit | 21 | [5 empty] | 2020 |  | New Investment
253 | Upstream reinforcement in France to increase FR-CH capacity |  | 1225 | PST in Cornier |  | RTE | - | - | Cross-border |  | ​Phase Shifter Transformer in order to attract the flows and alleviate the congestion on the France-switzerland interconnection west of Lake Geneva. | 400 |  | No EC Regional Group linked | Phase Shift Transformer | Under Consideration | Cornier (FR) |  | 400 | New | Single Circuit | [6 empty] | 2020 |  | New Investment
254 | Ultranet | 2.9 |  |  | Amprion;TransnetBW |  |  |  | Internal Project | Mid-term Project | [12 empty] | 1070 |  | 160 |  |  | 2021
254 | Ultranet |  | 660 | HVDC Line A South - Ultranet |  | AMPRION | TRANSNET-BW | - | Internal |  | New HVDC-lines from Osterath to Philippsburg to integrate new wind generation especially from North Sea towards Central-South Germany for consumption and storage. | 400 | DC | North-South (WEST) | Overhead Line | Permitting | Osterath (DE) | Philippsburg (DE) | 3049 | New | Single Circuit | 340 |  | under consideration |  | 01/01/2019 | Design & Permitting | 01/01/2021 | Delays due to permit granting reasons. | Delayed
255 | Connection Navarra-Basque Country |  |  |  | REE |  |  |  | Internal boundary in Spain Navarra-Basque Country or ES-FR | Mid-term Project | [12 empty] | 72 |  | 7.2 |  |  | 2020
255 | Connection Navarra-Basque Country |  | 1251 | New line 400 kV Muruarte-Ichaso |  | - | - | - | Internal |  | North axis Project between Navarra and the Basque Country. New input/output in Ichaso 400 kV for RES integration. | 400 | AC | No EC Regional Group linked | Overhead Line | Planning | Muruarte | Ichaso |  | New | Single Circuit | 145 | [5 empty] | 2020 |  | New Investment
255 | Connection Navarra-Basque Country |  | 1455 | New line 400 kV Castejón-Ichaso |  | - | - | - | Internal |  | North axis Project between Navarra and the Basque Country. New input/output in Ichaso 400 kV for RES integration | 400 | AC | No EC Regional Group linked | Overhead Line | Planning | Castejón | Ichaso |  | New | Single Circuit | 169 | [5 empty] | 2020 |  | New Investment
256 | Long-term conceptual interconnector DE-NL |  |  |  | Amprion;TenneT TSO |  |  |  | Germany - Netherlands | Future Project | [17 empty] | >2030
256 | Long-term conceptual interconnector DE-NL |  | 1252 | Long-term inter-connector DE-NL |  | AMPRION | TENNET-NL | - | Cross-border |  | Upgrades of existing interconnections as well as new ones are analysed. The used technology is open – both AC and DC options are under consideration. | 400 |  | No EC Regional Group linked | Overhead Line | Under Consideration | to be defined (DE) | to be defined (NL) |  |  | Single Circuit | [6 empty] | >2030 | Concept, under investigation | New Investment
257 | Douro Spanish-Portuguese reinforcement |  |  |  | REE;REN |  |  |  | Spain - Portugal | Future Project | [17 empty] | 2030
257 | Douro Spanish-Portuguese reinforcement |  | 1253 | Reinforcement in the Douro river area |  | REN | REE | - | Cross-border |  |  | 400 | AC | North-South (WEST) | Overhead Line | Under Consideration |  |  |  |  | Single Circuit | [6 empty] | > 2030 | New investment | New Investment
258 | Westcoast line | 1.3.2 |  |  | Tennet-DE |  |  |  | Inside Germany | Mid-term Project | [12 empty] | 250 |  | 40 |  |  | 2018
258 | Westcoast line |  | 667 | Brunsbüttel - Niebüll |  | TENNET-DE | - | - | Internal |  | About 135 km new 380-kV-lines and around 10 new transformers for integration of onshore Wind in Schleswig-Holstein and increase of NTC between DE and DK | 380 | AC | North Seas Countries Offshore Grid Initiative | Overhead Line | Permitting | Brunsbüttel (DE) | Niebüll | 2014 | New | Double Circuit | 135 |  | under consideration |  | 01/01/2018 | Planning | 1/ 1/ 2018 | in time relative to TYNDP14 | Investment on time
259 | HU-RO |  |  |  | MAVIR ZRt;Transelectrica |  |  |  | Hungary-Romania | Future Project | [12 empty] | 198 |  | 51 |  |  | >2030
259 | HU-RO |  | 1205 | HU-RO |  | MAVIR | TRANSELECTRICA | - | Cross-border |  | ​400kV OHL between Hungary and Romania in order to reach the market based target capacity resulted from the Common Planning Studies based on V4; in Romania a new transformer 400/220kV in Rosiori substation is necessary as internal investment associated to this project | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Jozsa | Oradea |  | New | Single Circuit | [6 empty] | >2030 |  | New Investment
260 | New Great Britain - Netherlands Interconnector |  |  |  | National Grid;TenneT TSO BV |  |  |  | Great Britain - Netherlands | Future Project | [17 empty] | 2030
260 | New Great Britain - Netherlands Interconnector |  | 1255 | Interconnector GB-NL |  | NGT | TENNET-NL | - | Cross-border |  |  |  |  | No EC Regional Group linked | Overhead Line | Under Consideration |  |  |  |  | Single Circuit | [6 empty] | 2030 | Preliminary studies have indicated potential for further regional welfare & RES integration increase by further increasing the interconnection capacity between Netherlands & UK. | Investment on time
261 | Long-term conceptual "West-East corridor" in North Sea |  |  |  | Amprion;Creos Luxembourg;Elia System Operator;National Grid;RTE;TenneT TSO |  |  |  | Great Britain - Central Europe | Future Project | [17 empty] | >2030
261 | Long-term conceptual "West-East corridor" in North Sea |  | 1256 | Investments to be created |  | - | - | - | Cross-border |  |  |  |  | No EC Regional Group linked | Overhead Line | [5 empty] | Single Circuit | [8 empty] | Investment on time
262 | Belgium-Netherlands: further evolution |  |  |  | Elia System Operator;TenneT TSO |  |  |  | Belgium - Netherlands | Future Project | [12 empty] | 60 |  | 10 |  |  | 2025
262 | Belgium-Netherlands: further evolution |  | 1257 | Belgium-Netherlands: further evolution |  | TENNET-NL | ELIA | - | Cross-border |  | The reference solutions being further studied envisions an upgrade of the capacity of the cross-border lines by replacing the current conductors with high performance (HTLS) conductors combined with the installation of additional phase shifting transformers. | 380 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Van Eyck (BE) OR Zandvliet (BE) - TBC | Maasbracht (NL) OR Kreekrak (NL) - TBC |  | Upgrade | Double Circuit | 10 | [5 empty] | 01/01/2022 | This project is introduced in the TYNDP16 via a Common Planning Study elaborated within the Regional Group North Sea and is being studied by TenneT NL and Elia. | New Investment
263 | Swiss Roof II |  |  |  | swissgrid |  |  |  | Switzerland - Germany; and Switzerland - Austria | Future Project | [12 empty] | 34 |  | 7 |  |  | 2022
263 | Swiss Roof II |  | 1258 | Rüthi - Bonaduz/Grynau |  | SWISSGRID | - | - | Internal |  | Integration of the new 380 kV tie-line Rüthi (CH) - Meiningen (AT) through optimisations between Rüthi and Grynau, Rüthi and Bonaduz and the construction of a new 380 kV substation and a new 380/220 kV transformer in Rüthi. | 380 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Rüthi | Grynau & Bonaduz |  |  | Triple Circuit | [6 empty] | 01/01/2023 |  | Investment on time
264 | Swiss Roof I |  |  |  | swissgrid |  |  |  | Switzerland - Germany; and Switzerland - Austria | Mid-term Project | [12 empty] | 591 |  | 118 |  |  | 2022
264 | Swiss Roof I |  | 1259 | Beznau - Mettlen |  | SWISSGRID | - | - | Internal |  | Optimization of the existing route by voltage conversion to 380 kV, partial reinforcement including a new 380/220 kV transformer in Beznau. | 380 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Beznau | Mettlen |  |  | Double Circuit | [6 empty] | 01/01/2025 |  | Investment on time
264 | Swiss Roof I |  | 1284 | Pradella - La Punt |  | SWISSGRID | - | - | Internal |  | Reinforcement of the existing route | 380 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Pradella | La Punt |  |  | Double Circuit | [6 empty] | 01/01/2020 |  | Investment on time
264 | Swiss Roof I |  | 1287 | Bassecourt - Mühleberg |  | SWISSGRID | - | - | Internal |  | Optimization of the existing route by voltage conversion to 380 kV including a new 380/220 kV transformer in Mühleberg. | 380 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Bassecourt | Mühleberg |  |  | Single Circuit | [6 empty] | 01/01/2025 |  | Investment on time
264 | Swiss Roof I |  | 1288 | Mettlen - Ulrichen |  | SWISSGRID | - | - | Internal |  | Reinforcement of the existing 220 kV line to 380 kV | 220 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Mettlen | Ulrichen |  |  | Double Circuit | [6 empty] | 01/01/2025 |  | Investment on time
265 | Swiss Ellipse II |  |  |  | swissgrid |  |  |  | Switzerland | Long-term Project | [12 empty] | 194 |  | 39 |  |  | 2029
265 | Swiss Ellipse II |  | 1260 | Grimsel connection |  | SWISSGRID | - | - | Internal |  | Voltage increase to 380 kV of line Innertkirchen – Ulrichen and construction of a new 380 kV substation and a new 380/220 kV transformer in Innertkirchen in order to connect the new pump storage power plant. | 380 | AC | No EC Regional Group linked | Overhead Line | Planning | Innertkirchen | Ulrichen |  |  | Double Circuit | [6 empty] | 01/01/2029 |  | Investment on time
265 | Swiss Ellipse II |  | 1289 | Lago Bianco connection |  | SWISSGRID | - | - | Internal |  | new 380 kV substation in Golbia | 380 | AC | No EC Regional Group linked | Overhead Line | Planning |  |  |  |  | Double Circuit | [6 empty] | 01/01/2029 |  | Investment on time
265 | Swiss Ellipse II |  | 1290 | Magadino - Ulrichen |  | SWISSGRID | - | - | Internal |  | reinforcement of the infrastructure in canton Tessin | 380 | AC | No EC Regional Group linked | Overhead Line | Planning |  |  |  |  | Single Circuit | [6 empty] | 01/01/2029 |  | Investment on time
266 | Swiss Ellipse I |  |  |  | swissgrid |  |  |  | Switzerland | Mid-term Project | [12 empty] | 553 |  | 111 |  |  | 2022
266 | Swiss Ellipse I |  | 1261 | Bickigen - Chippis - Chamoson |  | SWISSGRID | - | - | Internal |  | Chippis - Bickigen: Optimisation of the existing route by voltage conversion to 380 kV Chamoson - Chippis: Reinforcement by new construction of a 380 kV route New 380/220 kV transformer in Chippis | 380 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Bickigen | Chamoson |  |  | Double Circuit | [6 empty] | 01/01/2019 |  | Investment on time
266 | Swiss Ellipse I |  | 1285 | Magadino |  | SWISSGRID | - | - | Internal |  | New construction to connect the Avegno - Gorduno line to the Magadino substation |  | AC | No EC Regional Group linked | Overhead Line | Design & Permitting |  |  |  |  | Single Circuit | [6 empty] | 01/01/2019 |  | Investment on time
266 | Swiss Ellipse I |  | 1286 | Chippis - Lavorgo |  | SWISSGRID | - | - | Internal |  | Reinforcement by new construction of a 380 kV route including a new 380/220 kV transformer in Mörel | 380 | AC | No EC Regional Group linked | Overhead Line | Design & Permitting | Chippis | Lavorgo |  |  | Single Circuit | [6 empty] | 01/01/2024 |  | Investment on time
267 | Hansa PowerBridge 2 |  |  |  | 50Hertz Transmission;Svenska Kraftnät |  |  |  | Sweden (SE4)-Germany | Future Project | [12 empty] | 660 |  | 70 |  |  | 2025-2030
267 | Hansa PowerBridge 2 |  | 1262 | Hansa Power Bridge 2 |  | SVK | 50HERTZ | - | Cross-border |  | Possible second HVDC cable interconnector between southern Sweden (Bidding area SE4) and Germany (50Hertz). This project candidate is driven by market based target capacities found in the Common Planning Studies by Regional Group Baltic Sea. |  | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Substation SE4 | Güstrow (DE) |  | New | Single Circuit | [6 empty] | 2030 |  | New Investment
268 | Upgrading existing single 400 kV interconnection line between Romania and Serbia to double 400 kV line |  |  |  | JP EMS;Transelectrica |  |  |  | Romania - Serbia | Future Project | [12 empty] | 4 |  | 1 |  |  | >2030
268 | Upgrading existing single 400 kV interconnection line between Romania and Serbia to double 400 kV line |  | 1263 | Portile de Fier (RO) - Djerdap (RS) 2nd |  | TRANSELECTRICA | EMS | - | Cross-border |  | The project stems from the need to increase the transfer capacity between Romania and Serbia in order to accomodate connection of RES and improve market. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Portile de Fier | Djerdap | 500 | Upgrade | Double Circuit | [6 empty] | 01/01/2035 |  | Investment on time
269 | Uprate the western 220kV Sevilla Ring |  |  |  | REE |  |  |  | Spain - Portugal | Mid-term Project | [12 empty] | 1 |  | 0.1 |  |  | 2019
269 | Uprate the western 220kV Sevilla Ring |  | 1228 | Uprate D.Rodrigo-Aljarafe |  | REE | - | - | Internal |  | Uprate OHL 220kV line D.Rodrigo-Aljarafe​ | 220 |  | No EC Regional Group linked | Overhead Line | Planning | D.Rodrigo | Aljarafe |  |  | Single Circuit | 34 | [5 empty] | 2017 |  | New Investment
269 | Uprate the western 220kV Sevilla Ring |  | 1229 | Uprate Aljarafe-Santiponce |  | REE | - | - | Cross-border |  | Uprate OHL 220kV line Aljarafe-Santiponce​ | 220 |  | No EC Regional Group linked | Overhead Line | Planning | Aljarafe | Santiponce |  |  | Single Circuit | 13 | [5 empty] | 2019 |  | New Investment
270 | FR-ES project -Aragón-Atlantic Pyrenees | part of PCI 2.27. Capacity increase between Spain and France (generic project) |  |  | REE;RTE |  |  |  | Spain - France | Long-term Project | [12 empty] | 1200 |  | 120 |  |  | 2023
270 | FR-ES project -Aragón-Atlantic Pyrenees |  | 1211 | Aragón region -Marsillón |  | REE | RTE | - | Cross-border |  | New axis Aragón region -Marsillon (AC or DC)​ | 320 | DC | North-South (WEST) | Underground Cable | Planning | Aragón region | Marsillon | 1500 | New | Double Circuit | [6 empty] | 01/01/2025 |  | New Investment
270 | FR-ES project -Aragón-Atlantic Pyrenees |  | 1212 | New axis Ejea-Aragón region 400 kV |  | REE | RTE | - | Internal |  |  | 400 |  | No EC Regional Group linked | Overhead Line | Planning | Ejea de los Caballeros | Aragón region |  |  | Double Circuit | 110 | [5 empty] | 01/01/2025 |  | New Investment
270 | FR-ES project -Aragón-Atlantic Pyrenees |  | 1214 | Ejea de los Caballeros subestation |  | REE | RTE | - | Internal |  | new 400kV Ejea de los Caballeros subestation and connection to the lines La Serna-Magallón and Magallón Peñalba​ |  |  | No EC Regional Group linked | Substation | Planning | Ejea de los Caballeros |  |  | New | Double Circuit | 6 | [5 empty] | 01/01/2025 |  | New Investment
270 | FR-ES project -Aragón-Atlantic Pyrenees |  | 1215 | Aragón region subestation |  | REE | - | - | Internal |  | New 400 kV Aragón region subestation and connection to existing network and future cross border project​ | 400 |  | No EC Regional Group linked | Substation | Planning | Aragón region |  |  | New | Double Circuit | 5 | [5 empty] | 01/01/2025 |  | New Investment
271 | Long term conceptual project "Northern Seas offshore grid infrastructure" |  |  |  | EirGrid;Elia System Operator;Energinet.dk.dk;Creos Luxembourg;National Grid;RTE;TenneT TSO GmbH;SONI;Statnett;TenneT TSO |  |  |  | Countries around the Northern Seas | Future Project | [12 empty] | 18000 |  | 6000 |  |  | ~2020 ...>2030
271 | Long term conceptual project "Northern Seas offshore grid infrastructure" |  | 1264 | Investments to be created |  | - | - | - | Cross-border |  |  |  |  | No EC Regional Group linked | Overhead Line | [5 empty] | Single Circuit | [8 empty] | Investment on time
272 | Network upgrade in Central Serbia from 220 kV to 400 kV voltage level |  |  |  | JP EMS |  |  |  |  | Future Project | [12 empty] | 110 |  | 11 |  |  | 2030
272 | Network upgrade in Central Serbia from 220 kV to 400 kV voltage level |  | 1218 | Upgrade of exsisting OHL 220 kV to 400 kV between SS Nis 2 and SS Kruševac 1 |  | EMS | - | - | Cross-border |  | "​This investment is a part of East - West corridor." | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | SS 400/110 kV Nis 2 | SS 400/220/110 kV Krusevac 1 |  | New | Single Circuit | 72 | [5 empty] | 01/01/2034 |  | New Investment
272 | Network upgrade in Central Serbia from 220 kV to 400 kV voltage level |  | 1220 | Upgrading SS 220/110 kV Krusevac 1 to 400 kV voltage level |  | EMS | - | - | Internal |  | "​This investment is part on the East - West corridor." | 400 |  | No EC Regional Group linked | Substation | Under Consideration | SS 220/110 kV Krusevac 1 |  |  | Upgrade | Single Circuit | [6 empty] | 01/01/2034 |  | New Investment
272 | Network upgrade in Central Serbia from 220 kV to 400 kV voltage level |  | 1222 | Upgrading of exsisting OHL 220 kV to 400 kV between SS Krusevac 1 and SS Kraljevo 3 |  | EMS | - | - | Internal |  | "​This investment is a part of East - West corridor." | 400 |  | No EC Regional Group linked | Overhead Line | Under Consideration | SS 400/220/110 kV Krusevac 1 | SS 400/220/110 kV Kraljevo 3 |  | Upgrade | Single Circuit | 48 | [5 empty] | 01/01/2034 |  | New Investment
272 | Network upgrade in Central Serbia from 220 kV to 400 kV voltage level |  | 1223 | Uprading exsisting OHL 220 kV to 400 kV between SS Kraljevo 3 and SS Bajina Basta |  | EMS | - | - | Internal |  | "​This investment is a part of East - West corridor." | 400 |  | No EC Regional Group linked | Overhead Line | Under Consideration | SS 400/220/110 kV Kraljevo 3 | SS 400/220 kV Bajina Basta |  | Upgrade | Single Circuit | 80 | [5 empty] | 01/01/2030 |  | New Investment
273 | Closing of 400 kV ring around Belgrade region |  |  |  | JP EMS |  |  |  |  | Future Project | [12 empty] | 35 |  | 4 |  |  | 2030
273 | Closing of 400 kV ring around Belgrade region |  | 1209 | New SS 400/110 kV Belgrade West |  | EMS | - | - | Internal |  | "​New SS 400/110 Belgrade West will increase realiability of supplying of consumpution of Belgrade city. It is precondition for closing 400 kVloop around Belgrade region." | 400 |  | No EC Regional Group linked | Substation | Under Consideration | SS 400/110 kV Belgrade |  |  | New | Single Circuit | [6 empty] | 01/01/2035 |  | New Investment
273 | Closing of 400 kV ring around Belgrade region |  | 1217 | New OHL 400 kV SS Pancevo 2 - SS Belgrade West |  | EMS | - | - | Cross-border |  | "​This line will close 400 kV loop around Belgrade city. By closing of this loop, transmission capacity in direction East - West will be increased." | 400 |  | No EC Regional Group linked | Substation | Under Consideration | SS 400/220/110 kV Pancevo 2 | SS 400/110 kV Belgrade West |  |  | Double Circuit | 60 | [5 empty] | 01/01/2035 |  | New Investment
274 | Concept project France-Switzerland 400kV AC |  |  |  | RTE;swissgrid |  |  |  | France - Switzerland | Future Project | [17 empty] | >2030
274 | Concept project France-Switzerland 400kV AC |  | 1226 | new 400-kV France-Switzerland interconnection |  | RTE | SWISSGRID | - | Cross-border |  | Concept investment that could allow to increase the cross-border capacity between France and Switzerland. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration |  |  | 1000 | New | Single Circuit | 25 | [5 empty] | 2030 |  | New Investment
275 | Concept project France-Switzerland HVDC |  |  |  | RTE;swissgrid |  |  |  | France - Switzerland | Future Project | [17 empty] | >2030
275 | Concept project France-Switzerland HVDC |  | 1227 | New HVDC cross-border link between France and Switzerland |  | RTE | SWISSGRID | - | Cross-border |  | ​The project consists of a new cross-border HVDC between France and Switzerland. | 320 | DC | No EC Regional Group linked | Underground Cable | Under Consideration |  |  | 1000 | New | Single Circuit | 200 | [5 empty] | 2030 |  | New Investment
276 | FR-ES project -Navarra-Landes | part of PCI 2.27. Cpacity increase between Spain and France (generfic project) |  |  | REE;RTE |  |  |  | Spain - France | Long-term Project | [12 empty] | 1470 |  | 150 |  |  | 2023
276 | FR-ES project -Navarra-Landes |  | 1206 | HVDC Pamplona area -Cantegrit |  | REE | RTE | - | Cross-border |  | HVDC Pamplona area (Spain) -Cantegrit (France)​ | 320 | DC | North-South (WEST) | Underground Cable | Planning | Pamplona area | Cantegrit | 1500 | New | Double Circuit | 180 | [5 empty] | 01/01/2025 |  | New Investment
276 | FR-ES project -Navarra-Landes |  | 1207 | Upgrade Cantegrit-Saucats |  | RTE | - | - | Internal |  | Upgrade of 2* 400 kV lines Cantegrit-Saucats​ | 400 | AC | North-South (WEST) | Overhead Line | Planning | Cantegrit | Saucats |  | Upgrade | Single Circuit | 70 | [5 empty] | 01/01/2025 |  | New Investment
276 | FR-ES project -Navarra-Landes |  | 1208 | Upgrade Cantegrit-Marsillon |  | RTE | - | - | Internal |  | Upgrade of existing 2*225kV line Cantegrit-Marsillon to 1* 400kV​ | 400 | AC | North-South (WEST) | Overhead Line | Planning | Cantegrit | Marsillon |  | Upgrade | Single Circuit | 80 | [5 empty] | 01/01/2025 |  | New Investment
276 | FR-ES project -Navarra-Landes |  | 1210 | New substation Pamplona area |  | REE | - | - | Internal |  | New substation Pamplona area 400 kV and connection to the 400 kV line Ichaso-Castejón/Muruarte​ | 400 |  | No EC Regional Group linked | Substation | Planning | Pamplona area |  |  | New | Single Circuit | [6 empty] | 01/01/2025 |  | New Investment
277 | New double 400 kV interconnection line between Bulgaria and Serbia |  |  |  | ESO EAD;JP EMS |  |  |  | Bulgaria - Serbia | Future Project | [12 empty] | 52 |  | 5 |  |  | >2030
277 | New double 400 kV interconnection line between Bulgaria and Serbia |  | 1266 | Sofia West (BG) - Nis 2 (RS) 2nd |  | ESO | EMS | - | Cross-border |  | The project stems from the need to increase the transfer capacity between Bulgaria and Serbia in order to accomodate connection of RES and improve electricity market. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Sofia West (BG) | Nis 2 (RS) | 800 | New | Double Circuit | [6 empty] | 01/01/2034 |  | Investment on time
278 | Additional project France - Spain |  |  |  | RTE;REE |  |  |  | Spain - France | Future Project | [17 empty] | 2030
278 | Additional project France - Spain |  | 1267 | Investments to be created |  | - | - | - | Cross-border |  |  |  |  | No EC Regional Group linked | Overhead Line | Under Consideration |  |  |  |  | Single Circuit | [6 empty] | 2030 |  | Investment on time
279 | Third interconnector between Bulgaria and Greece |  |  |  | IPTO;ESO EAD |  |  |  | Bulgaria - Greece | Future Project | [17 empty] | 2030
279 | Third interconnector between Bulgaria and Greece |  | 1452 | Maritsa East 1 (BG)- Nea Santa (GR) 2nd line |  | IPTO-SA | ESO | - | Cross-border |  | The project concerns the construction of a new 400kV AC line between Bulgaria and Greece. The project necessity stems from the need to increase the transfer capacity between Greece and Bulgaria in order to accomodate connection of RES and improve market integration, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Maritsa East 1 (BG) | Nea Santa (GR) | 500 | New | Single Circuit | 130 | [5 empty] | 20/10/2030 |  | Investment on time
280 | FR-BE Phase 3 (study) |  |  |  | ELIA; RTE |  |  |  | France - Belgium | Future Project | [12 empty] | 100 |  | 25 |  |  | 2025
280 | FR-BE Phase 3 (study) |  | 1008 | Lonny-Achène-Gramme: HTLS upgrade (under study) |  | RTE | ELIA | - | Cross-border |  | The option that will be evaluated envisions the replacement of the current conductors on the axis Lonny-Achène-Gramme with high performance conductors. Hereby not excluding that the bilateral study could lead to complementary / alternative solutions such as a new HVDC corridor (onshore or offshore) or installation of a PST. | 400 | AC | No EC Regional Group linked | Overhead Line | Under Consideration | Lonny (FR) | Gramme (BE) | 1000 | Upgrade | Single Circuit | 75 |  |  |  | 01/01/2030 | Under Consideration | 01/01/2025 | Related to the long-term perspective of the energy transition. Subject to further studies to determine techno-economic most optimum solution taking into account the feasability of different solutions. | Investment on time
281 | ANAI: Abengoa Northern Atlantic Interconnection |  |  |  | Abengoa |  |  |  | Spain - France - United Kingdom | Future Project | [12 empty] | 3700 |  |  |  |  | 2024/2026
281 | ANAI: Abengoa Northern Atlantic Interconnection |  | 1379 | ANAI: Abengoa Northern Atlantic Interconnection |  | - | - | - |  |  | ANAI project consists on a subsea multiterminal (with Voltage Source Converters) High Voltage Direct Current cable with 2,000 Megawatt of power grid transfer capability. |  | DC |  |  | Under Consideration | Soto de Ribera | Exeter | [9 empty] | 2026 | Under evaluation by ENTSO-E
282 | ASEI: Abengoa Southern Europe Interconnection |  |  |  | Abengoa |  |  |  | Spain - France - Italy | Future Project | [12 empty] | 2600 |  |  |  |  | 2023/2025
282 | ASEI: Abengoa Southern Europe Interconnection |  | 1297 | ASEI: Abengoa Southern Europe Interconnection |  | - | - | - |  |  | ASEI Projct consists on a subsea multiterminal (with Voltage Source Converters) High Voltage Direct Current cable with 2,000 Megawatt of power grid transfer capability |  | DC |  |  | Under Consideration | Vandellos | La Spezia | [9 empty] | 2025 |  | New Investment
283 | TuNur |  |  |  | TuNur Ltd |  |  |  | Tunisia, Italia | Future Project | [12 empty] | 2700 |  | 200 |  |  | 30/12/2020
283 | TuNur |  | 1378 | TuNur | [6 empty] | ​TuNur is aimed to connect to the European network a Concentrated Solar Power plant with storage to be located in Rejim Maatoug, Kebili, Tunisia. The connection point to the ENTSO-E network is located in Montalto di Castro, Lazio, Italy. The transmission project will comprise +/- 500kV DC submarine cables from the Tunisian Northern coast to Montalto di Castro, DC overhead lines in Tunisia from the power plant to the shoring point, and HVDC converter stations at the terminal points.​ |  | DC |  |  | Permitting | Rejim Maatoug 400kV | Montalto 400kV | [9 empty] | 2020
283 | TuNur |  | 1430 | TuNur | [6 empty] | ​TuNur is aimed to connect to the European network a Concentrated Solar Power plant with storage to be located in Rejim Maatoug, Kebili, Tunisia. The connection point to the ENTSO-E network is located in Montalto di Castro, Lazio, Italy. The transmission project will comprise +/- 500kV DC submarine cables from the Tunisian Northern coast to Montalto di Castro, DC overhead lines in Tunisia from the power plant to the shoring point, and HVDC converter stations at the terminal points.​ This section covers the AC part of the link. |  |  |  |  | Permitting | Rejim Maatoug 400 kV | Montalto 400 kV | [9 empty] | 2020
284 | LEG1 |  |  |  | GreenPower 2020 |  |  |  | Greece, Egypt, Libya | Future Project | [12 empty] | 1015 |  |  |  |  | 2021
284 | LEG1 |  | 1405 | LEG1 | [6 empty] | 3000 MW HVDC Submarine cable not deeper than 2500 m​ |  | DC |  |  | Under consideration | SALOUM (EG), TOBRUK (LIBYA) | MIRES (GR Crete) | [9 empty] | 2019
285 | GridLink |  |  |  | Elan Energy Ltd |  |  |  | UK, France | Future Project | [12 empty] | 600 |  |  |  |  | Q4 2020/ Q1 2021
285 | GridLink |  | 1383 | GridLink |  | - | - | - |  |  | ​UK-France, 1.5GW HVDC Interconnector |  | DC |  |  | Planning | Kemsley (Sittingbourne, UK) | Warande (Gravelines, France) | [9 empty] | 2021 |  | New Investment
286 | Greenlink |  |  |  | Element Power |  |  |  | Ireland - Wales UK | Future Project | [12 empty] | 400 |  |  |  |  | 2020
286 | Greenlink |  | 1385 | Greenlink | [6 empty] | ​A subsea HVDC interconnector between Wales and Ireland​ |  | DC |  |  | Design | Great Island (to be confirmed) | Pembroke (to be confirmed) | [9 empty] | 2022 | A pure interconnector with Ofgem IPA approval. | Delayed
287 | Greenwire South |  |  |  | Element Power |  |  |  | Ireland and Great Britain | Future Project | [12 empty] | 850 |  |  |  |  | 2021
287 | Greenwire South |  | 1439 | Greenwire South | [6 empty] | ​An HVDC link between Wales and Ireland |  | DC |  |  | Planning | Grenwire South Hub | Pembroke (to be confirmed) | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
287 | Greenwire South |  | 1441 | Greenwire South | [6 empty] | ​HVDC link between Greenwire South HVDC backbone and EirGrid​ |  |  |  |  | Planning | Grenwire South Hub | Dunstown, Laois or other tbc | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
287 | Greenwire South |  | 1442 | Greenwire South | [6 empty] | ​HVAC link 1 from windfarm collector substation to HVDC hub​ |  |  |  |  | Planning | Grenwire South Hub | Greenwire South substation AC1 | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
287 | Greenwire South |  | 1443 | Greenwire South | [6 empty] | ​HVAC link 2 from windfarm collector substation to HVDC hub​ |  |  |  |  | Planning | Grenwire South Hub | Greenwire South substation AC2 | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
287 | Greenwire South |  | 1444 | Greenwire South | [6 empty] | ​HVAC link 3 from windfarm collector substation to HVDC hub​ |  |  |  |  | Planning | Grenwire South Hub | Greenwire South substation AC3 | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
287 | Greenwire South |  | 1445 | Greenwire South | [6 empty] | ​HVAC link 4 from windfarm collector substation to HVDC hub​ |  |  |  |  | Planning | Grenwire South Hub | Greenwire South substation AC4 | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
287 | Greenwire South |  | 1446 | Greenwire South | [6 empty] | ​HVAC link 5 from windfarm collector substation to HVDC hub​ |  |  |  |  | Planning | Grenwire South Hub | Greenwire South substation AC5 | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
289 | MAREX UK-Ireland Intrconnector |  |  |  | Organic Power Ltd. |  |  |  | UK-Ireland | Future Project | [12 empty] | 1300 |  | 200 |  |  | 2020
289 | MAREX UK-Ireland Intrconnector |  | 1386 | MAREX UK-Ireland Intrconnector |  | - | - | - |  |  | ​1500MW VSC HVDC bipole inetrconnector drom 400kV AC Connah's Quay UK-Finglas Dublin 400kV AC-Bellacorick Mayo 400kV AC |  | DC | No EC Regional Group linked |  | Under Consideration | Connah's Quay | Finglas Dublin | [9 empty] | 2020
289 | MAREX UK-Ireland Intrconnector |  | 1387 | MAREX UK-Ireland Intrconnector |  | - | - | - |  |  | ​​This describes the underground cable-OHL-subsea cable combination transmission from Mayo to Dublin |  |  |  |  | Under Consideration | Finglas Dublin | Bellacorick Mayo | [9 empty] | 2020
290 | Greenwire North |  |  |  | Element Power |  |  |  | Ireland and Great Britain | Future Project | [12 empty] | 800 |  |  |  |  | 2021
290 | Greenwire North |  | 1369 | Greenwire North | [6 empty] | ​HVAC link 1 from windfarm collector substation to HVDC hub​ |  |  |  |  | Planning | Greenwire North Hub | Woodlands or new Midlands 400/220V substations tba | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
290 | Greenwire North |  | 1440 | Greenwire North | [6 empty] | An HVDC link between Wales and Ireland​ |  | DC |  |  | Planning | Greenwire North Hub | Pentir (to be confirmed) | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
290 | Greenwire North |  | 1447 | Greenwire North | [6 empty] | ​HVDC link between Greenwire North HVDC backbone and EirGrid​ |  |  |  |  | Planning | Greenwire North Hub | Woodlands or new Midlands 400/220V substation tba | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
290 | Greenwire North |  | 1448 | Greenwire North | [6 empty] | ​HVAC link 2 from windfarm collector substation to HVDC hub​ |  |  |  |  | Planning | Greenwire North Hub | Greenwire North substation AC2 | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
290 | Greenwire North |  | 1449 | Greenwire North | [6 empty] | ​HVAC link 3 from windfarm collector substation to HVDC hub​ |  |  |  |  | Planning | Greenwire North Hub | Greenwire North substation AC3 | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
290 | Greenwire North |  | 1450 | Greenwire North | [6 empty] | ​HVAC link 4 from windfarm collector substation to HVDC hub​ |  |  |  |  | Planning | Greenwire North Hub | Greenwire North substation AC4 | [9 empty] | 2023 | Awaiting international contracts for renewable energy | Delayed
291 | Greenwire Loop |  |  |  | Element Power |  |  |  | North and South Wales | Future Project | [12 empty] | 50 |  |  |  |  | 2022
291 | Greenwire Loop |  | 1454 | Greenwire Loop Cable |  | - | - | - | Cross-border |  | An onshore underground link in Ireland between Greenwire North and Greenwire South to create loop flow potential between North Wales (e.g. Pentir) and South Wales (e.g. Pembroke)​ |  | DC | No EC Regional Group linked | Overhead Line | Under Consideration | Greenwire North Hub | Grenwire South Hub |  |  | Single Circuit | [6 empty] | 2022 |  | New Investment
292 | Greenconnect |  |  |  | Element Power |  |  |  | Ireland - North Wales UK | Future Project | [12 empty] | 400 |  |  |  |  | 2022
292 | Greenconnect |  | 1453 | interconnection |  | - | - | - | Cross-border |  | A subsea HVDC interconnector between Wales and Ireland |  | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Dublin Area ( to be agreed) | Pentir (to be agreed) |  |  | Single Circuit | [6 empty] | 2023 |  | New Investment
293 | Southern Aegean Interconnector |  |  |  | Kykladika Meltemia SA |  |  |  | Greece | Future Project | [12 empty] | 1800 |  |  |  |  | 2020
293 | Southern Aegean Interconnector |  | 1431 | Southern Aegean Interconnector | [6 empty] | ​New DC link (2 converter SS + 270 km DC subm. cable) to connect 582MW of offshore WF generation to the mainland (Area of Athens)​ | 220 | DC |  |  | Design & permitting | LAVRIO | LEVITHA | [9 empty] | 2020 |  | Investment on time
293 | Southern Aegean Interconnector |  | 1432 | Southern Aegean Interconnector | [6 empty] | ​​Facilitates future connection of the Crete to the Greek Mainland via Levitha substation. | 320 | DC |  |  | Design | LEVITHA | KORAKIA CRETE | [9 empty] | 2021 |  | Investment on time
293 | Southern Aegean Interconnector |  | 1433 | Southern Aegean Interconnector | [6 empty] | ​Connection Wind Farms with AC Substations at Levitha and Syrna | 500 | AC |  |  | Design | Levitha | Syrna | [9 empty] | 2020 |  | Investment on time
293 | Southern Aegean Interconnector |  | 1434 | Southern Aegean Interconnector | [6 empty] | ​​AC Submarine cable to connect Kinaros Offshore Wind Farm HiV sub station to the AC side of Levitha Converter SS | 220 | AC |  |  | Design | KINAROS | LEVITHA | [9 empty] | 2021 |  | Investment on time
293 | Southern Aegean Interconnector |  | 1435 | Southern Aegean Interconnector | [6 empty] | ​AC Submarine cable to connect Kandeliousa OffsHore Wind Farm HV substation to Syrna SS | 220 | AC |  |  | Design | Kandeliousa | Syrna | [9 empty] | 2021 |  | Investment on time
293 | Southern Aegean Interconnector |  | 1436 | Southern Aegean Interconnector | [6 empty] | ​AC Submarine cable connect Kandeliousa offshore Wind Farm HV substation to Pergousa SS | 220 | AC |  |  | Design | Kandeliousa | Pergousa | [9 empty] | 2021 |  | Investment on time
294 | Maali |  |  |  | Element Power |  |  |  | GB - NO | Future Project | [12 empty] | 500 |  |  |  |  | 2023
294 | Maali |  | 1356 | Maali | [6 empty] | ​A subsea HVDC interconnector between Shetland and Norway |  | DC |  |  | Under consideration | Kergord Shetland tba | tba near Bergen-Mongstad or Karsto- Blafalli | [9 empty] | 2023 | Viking Windfarm Shetland and HVDC to Scotland
295 | Gallant |  |  |  | Element Power |  |  |  | Northern Ireland – Scotland | Future Project | [12 empty] | 250 |  |  |  |  | 2021
295 | Gallant |  | 1438 | Gallant | [6 empty] | ​A subsea HVDC interconnector between South West Scotland and Northern Ireland​ |  | DC |  |  | Under consideration | Glenluce | Kilroot | [9 empty] | 2023 | Dumfries and Galloway strategic reinforcement
296 | Britib |  |  |  | ACS Cobra |  |  |  | Spain, France, United Kingdom | Future Project | [12 empty] | 2450 |  |  |  |  | 2020
296 | Britib |  | 1437 | Britib | [6 empty] | Interconnection project between South-West England (United Kingdom), Cordemais (France) and Basque Country (Spain) in a multiterminal VSC HVDC bipole configuration of +/- 525-600 kV with 3 inputs/outputs of 1800 MW each, and a mostly subsea route from Spain to Great Britain along the French coast of about 1330 km in total. | 320 | DC |  |  | Under Consideration | Gatica/Hernani, Cordemais and Langage/Indian Queens | Gatica/Hernani, Cordemais and Langage/Indian Queens | [9 empty] | 2020 | Information provided from TSO
297 | Belgian North Border: BRABO II + III | 2.23 |  |  | ELIA |  |  |  | Zandvliet-Mercator | Mid-term Project | [12 empty] | 120 |  | 30 |  |  | 2020
297 | Belgian North Border: BRABO II + III |  | 445 | BRABO II: Zandvliet - Lillo - Liefkenshoek |  | ELIA | - | - | Internal |  | The second phase of the BRABO project consists of the construction of a new double circuit 380kV overhead line from Zandvliet via Lillo to Liefkenshoek where the new line will be the temporarily connected to the existing 380kV line Doel-Mercator. This new line will be constructed making use of the corridor of the existing 150kV overhead line Zandvliet-Oorderen-Lillo, which will be undergrounded. | 380 | AC | North-South (WEST) | Overhead Line | Design & Permitting | Zandvliet | Lillo - Liefkenshoek | 1000 | New | Double Circuit | 18 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 01/01/2020 | Progress made in permitting procedures brought clarification to preferential trajectory. Planning has been reviewed accordingly with 2020 based upon the hypothesis of acquiring all necessary permits as currently planned. | Delayed
297 | Belgian North Border: BRABO II + III |  | 604 | BRABO III: Liefkenshoek - Mercator |  | ELIA | - | - | Internal |  | The existing 150kV overhead will be upgraded to a single 380kV overhead line between the site Liefkenshoek and the substation Mercator. To facilitate this upgrade, the adjacent 150kV grid will be adapted. This investment would be needed in an earlier stage (before 2023, 2020 earliest possible) to secure the intended interconnection capacity increase, if a production scenario would occur where all four nuclear units at Doel are present. | 380 | AC | North-South (WEST) | Overhead Line | Design & Permitting | Liefkenshoek (BE) | Mercator (BE) | 1000 | New | Single Circuit | 18 |  | design & permitting |  | 01/01/2018 | Design & Permitting | 01/01/2023 | BRABO III will be realized sequentially after BRABO II in anticipation of potential future integration of production unit / interconnectors in the Antwerp area, hereby safeguarding the long-term character of the increase of interconnection capacity of the North Border. | Rescheduled
297 | Belgian North Border: BRABO II + III |  | 605 | BRABO II: Lillo 380 |  | ELIA | - | - | Internal |  | This concerns the construction of the 380kV substation Lillo, including a 380/150 kV transformer, as part of the second phase of the BRABO-project. | 380 |  | North-South (WEST) | Substation | Design & Permitting | Lillo (BE) |  | 1000 | New |  |  |  | design & permitting |  | 01/01/2018 | Design & Permitting | 01/01/2019 | Progress made in permitting procedures brought clarification to preferential trajectory. Planning has been reviewed accordingly with 2019 based upon the hypothesis of acquiring all necessary permits as currently planned. | Delayed
298 | Anglo-Scottish Cluster -2 |  |  |  | NGT;SHETL |  |  |  | GB Internal North-South | Long-term Project | [12 empty] | 1460 |  |  |  |  | 2023
298 | Anglo-Scottish Cluster -2 |  | 453 | Eastern HVDC Link |  | NGT | - | - | Internal |  | A new ~2GW submarine HVDC cable route from Peterhead to Hawthorn Pit with associated AC network reinforcement works at both ends with possible offshore HVDC integration in the Firth of Forth area. | 500 | DC | No EC Regional Group linked | Subsea Cable | Under Consideration | Peterhead (GB) | Hawthorn Pit (GB) | 2000 | New | Quadruple Circuit | 365 |  | Planned |  | 01/01/2020 | Under Consideration | 1/ 1/ 2023 | Changes in the generation background | Rescheduled
299 | SACOI3 |  |  |  | Terna |  |  |  | Italy-Corsica | Long-term Project | [12 empty] | 700 |  | 50 |  |  | 2023
299 | SACOI3 |  | 1458 | SACOI3 |  | - | - | - | Internal |  | New HVDC line between Italy mainland, Corsica and Sardinia replacing existing link SACOI2 |  | DC | No EC Regional Group linked | Subsea Cable | Design | Codrongianos | Suvereto |  | Upgrade | Single Circuit | [6 empty] | 2023 | Project rescheduled to meet the target commissioning date 2023 | Investment on time

## CBA results
TYNDP 2016 Project Index | Attribute | EP2020 | Vision 1 | Vision 2 | Vision 3 | Vision 4
1 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±10 | 30 ±10 | 40 ±10 | 130 ±20 | 180 ±30
| B3 RES integration (GWh/yr) | 410 ±80 | 410 ±80 | 410 ±80 | 1580 ±320 | 2090 ±420
| B4 Losses (GWh/yr) | 25 ±25 | 0 ±25 | 0 ±25 | 75 ±25 | 75 ±25
| B4 Losses (Meuros/yr) | 1 ±1 | 0 ±1 | 0 ±1 | 4 ±2 | 5 ±2
| B5 CO2 Emissions (kT/year) | -200 ±30 | -200 ±100 | -200 ±100 | -600 ±100 | -700 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | 15-25km
| B6 Technical resilience | +
| B7 Robustness | +
2 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 30 ±10 | 30 ±10 | 40 ±10 | 130 ±20 | 240 ±40
| B3 RES integration (GWh/yr) | 440 ±80 | 450 ±90 | 450 ±90 | 1680 ±340 | 2740 ±550
| B4 Losses (GWh/yr) | -25 ±25 | 0 ±25 | 0 ±25 | 0 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | -2 ±2 | 0 ±1 | 0 ±1 | 0 ±1 | 0 ±2
| B5 CO2 Emissions (kT/year) | -300 ±50 | -200 ±100 | -200 ±100 | -700 ±100 | -1000 ±200
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
4 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | 40 ±10 | 60 ±10 | 10 ±10 | 70 ±10
| B3 RES integration (GWh/yr) | <10 | 10 ±10 | 150 ±20 | 50 ±20 | 430 ±140
| B4 Losses (GWh/yr) | 25 ±25 | 75 ±25 | 100 ±25 | 75 ±25 | 100 ±25
| B4 Losses (Meuros/yr) | 1 ±1 | 4 ±1 | 4 ±2 | 4 ±2 | 6 ±2
| B5 CO2 Emissions (kT/year) | 300 ±60 | 500 ±100 | 300 ±100 | ±100 | -300 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
13 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 60 ±10 | 80 ±10 | 90 ±10 | 110 ±20
| B3 RES integration (GWh/yr) | - | 1090 ±220 | 1300 ±260 | 1460 ±290 | 1580 ±320
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | -500 ±100 | -500 ±100 | -600 ±100 | -600 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
16 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 200 ±30 | 120 ±20 | 150 ±20 | 120 ±30 | 240 ±30
| B3 RES integration (GWh/yr) | 40 ±40 | 460 ±200 | 960 ±190 | 700 ±250 | 1000 ±140
| B4 Losses (GWh/yr) | 700 ±100 | 800 ±100 | 1200 ±400 | 750 ±100 | 1200 ±200
| B4 Losses (Meuros/yr) | 30 ±5 | 40 ±10 | 55 ±20 | 35 ±10 | 55±20
| B5 CO2 Emissions (kT/year) | 2400 ±500 | 800 ±400 | ±100 | -1000 ±200 | -2300 ±200
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
| B6 Technical resilience | +
| B7 Robustness | ++
21 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 90 ±10 | 40 ±20 | 90 ±30 | 30 ±10 | 40 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 50 ±40 | 90 ±80
| B4 Losses (GWh/yr) | 225 ±25 | 225 ±25 | 375 ±37 | 250 ±25 | 125 ±25
| B4 Losses (Meuros/yr) | 9 ±1 | 12 ±1 | 17 ±2 | 14 ±2 | 8 ±2
| B5 CO2 Emissions (kT/year) | 1600 ±120 | 800 ±400 | 1100 ±300 | -300 ±100 | -400 ±200
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
22 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | <10 | 20 ±10
| B4 Losses (GWh/yr) | 0 ±25 | 50 ±25 | 100 ±25 | 25 ±25 | 100 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | 2 ±2 | 4 ±2 | 1 ±2 | 6 ±2
| B5 CO2 Emissions (kT/year) | ±100 | ±100 | ±100 | ±100 | -100 ±0
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
23 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±10 | 20 ±10 | 20 ±10 | 30 ±10 | 20 ±10
| B3 RES integration (GWh/yr) | <10 | 10 ±20 | <10 | 500 ±140 | 190 ±20
| B4 Losses (GWh/yr) | 200 ±50 | 200 ±50 | 200 ±50 | 150 ±50 | 150 ±50
| B4 Losses (Meuros/yr) | 8 ±2 | 10 ±3 | 9 ±3 | 9 ±3 | 10 ±3
| B5 CO2 Emissions (kT/year) | 100 ±30 | 200 ±200 | 100 ±300 | -100 ±100 | -200 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
24 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 10 ±10 | 10 ±10 | <10 | 20 ±10 | 20 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | 10 ±20 | 200 ±60 | 120 ±50
| B4 Losses (GWh/yr) | 0 ±25 | 0 ±25 | 0 ±25 | 0 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | 0 ±1 | 0 ±1 | 0 ±1 | 0 ±2
| B5 CO2 Emissions (kT/year) | 200 ±30 | 200 ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
25 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 90 ±20 | 60 ±10 | 100 ±10 | 90 ±20 | 80 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | 740 ±200 | 910 ±280 | 520 ±150
| B4 Losses (GWh/yr) | -300 ±30 | 0 ±25 | 350 ±35 | 650 ±65 | 650 ±65
| B4 Losses (Meuros/yr) | -14 ±2 | 0 ±1 | 16 ±2 | 39 ±4 | 43 ±5
| B5 CO2 Emissions (kT/year) | 1600 ±230 | 1000 ±200 | 400 ±300 | -600 ±200 | -600 ±200
| S1 - Environmental impact | 15-50km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
26 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 30 ±10 | 30 ±20 | 20 ±20 | 10 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | 70 ±60 | 30 ±20
| B4 Losses (GWh/yr) | - | 75 ±25 | 75 ±25 | -425 ±42 | -150 ±25
| B4 Losses (Meuros/yr) | - | 4 ±1 | 3 ±2 | -26 ±3 | -10 ±2
| B5 CO2 Emissions (kT/year) | - | 600 ±200 | 400 ±200 | -100 ±100 | -300 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
28 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 130 ±20 | 140 ±50 | 150 ±50 | 140 ±40 | 60 ±40
| B3 RES integration (GWh/yr) | 50 ±10 | <10 | <10 | 1650 ±400 | 350 ±190
| B4 Losses (GWh/yr) | 325 ±25 | 400 ±40 | 400 ±40 | 125 ±25 | -50 ±25
| B4 Losses (Meuros/yr) | 14 ±1 | 21 ±3 | 18 ±2 | 7 ±2 | -4 ±2
| B5 CO2 Emissions (kT/year) | 1400 ±170 | 2800 ±1600 | 1400 ±500 | -600 ±500 | -600 ±200
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
29 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 190 ±30 | 100 ±20 | 120 ±20 | 170 ±30 | 130 ±20
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 890 ±180 | 260 ±50
| B4 Losses (GWh/yr) | 175 ±25 | 200 ±25 | 175 ±25 | 175 ±25 | 175 ±25
| B4 Losses (Meuros/yr) | 7 ±1 | 10 ±2 | 8 ±1 | 10 ±2 | 11 ±2
| B5 CO2 Emissions (kT/year) | 700 ±100 | ±100 | 300 ±100 | -800 ±100 | -700 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
31 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 40 ±< 10 | 10 ±10 | 30 ±20 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | <10 | 30 ±20
| B4 Losses (GWh/yr) | 50 ±25 | -25 ±25 | -25 ±25 | 25 ±25 | 25 ±25
| B4 Losses (Meuros/yr) | 2 ±1 | -2 ±2 | -1 ±1 | 1 ±2 | 1 ±2
| B5 CO2 Emissions (kT/year) | 1000 ±70 | 300 ±100 | 400 ±300 | ±100 | -300 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
33 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 110 ±20 | 90 ±10 | 120 ±20 | 220 ±30 | 190 ±30
| B3 RES integration (GWh/yr) | 1280 ±260 | 1270 ±250 | 1270 ±250 | 1960 ±390 | 1440 ±290
| B4 Losses (GWh/yr) | -75 ±25 | -100 ±25 | -100 ±25 | -100 ±25 | -100 ±25
| B4 Losses (Meuros/yr) | -4 ±1 | -6 ±2 | -5 ±2 | -6 ±2 | -7 ±2
| B5 CO2 Emissions (kT/year) | -2200 ±300 | -700 ±100 | -400 ±100 | -1100 ±200 | -900 ±100
| S1 - Environmental impact | 15-50km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
35 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 0 ±0 | 20 ±10 | 20 ±0 | 40 ±0 | 50 ±10
| B3 RES integration (GWh/yr) | 0 ±0 | 240 ±10 | 230 ±10 | 540 ±40 | 390 ±80
| B4 Losses (GWh/yr) | - | -625 ±62 | -125 ±25 | -25 ±25 | -50 ±25
| B4 Losses (Meuros/yr) | - | -34 ±4 | -6 ±1 | -2 ±2 | -4 ±2
| B5 CO2 Emissions (kT/year) | 0 ±0 | -100 ±100 | -100 ±100 | -200 ±0 | -500 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
36 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 10 ±10 | 40 ±10
| B4 Losses (GWh/yr) | 50 ±25 | 0 ±25 | 25 ±25 | 25 ±25 | 25 ±25
| B4 Losses (Meuros/yr) | 2 ±1 | 0 ±1 | 1 ±1 | 1 ±2 | 1 ±2
| B5 CO2 Emissions (kT/year) | -200 ±50 | -200 ±100 | -200 ±100 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
37 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 110 ±20 | 100 ±10 | 100 ±20 | 120 ±10 | 70 ±10
| B3 RES integration (GWh/yr) | 100 ±20 | 220 ±170 | <10 | 890 ±180 | 350 ±70
| B4 Losses (GWh/yr) | 350 ±35 | 350 ±35 | 350 ±35 | 350 ±35 | 350 ±35
| B4 Losses (Meuros/yr) | 15 ±1 | 19 ±2 | 16 ±2 | 21 ±2 | 23 ±3
| B5 CO2 Emissions (kT/year) | -400 ±80 | ±100 | -500 ±500 | -700 ±100 | -100 ±800
| S1 - Environmental impact | 50-100km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
39 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±10 | <10 | 20 ±10 | 10 ±10 | 20 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | 20 ±30 | 120 ±70 | 130 ±50
| B4 Losses (GWh/yr) | 50 ±25 | 50 ±25 | 25 ±25 | 25 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | 2 ±1 | 2 ±2 | 1 ±1 | 1 ±2 | 0 ±2
| B5 CO2 Emissions (kT/year) | ±100 | ±100 | -200 ±100 | -200 ±100 | ±100
| S1 - Environmental impact | 15-50km
| S2 - social impact | 15-25km
| B6 Technical resilience | +
| B7 Robustness | +
40 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 10 ±10 | 20 ±10 | 10 ±10 | 10 ±10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 170 ±60 | 100 ±30
| B4 Losses (GWh/yr) | -25 ±25 | 0 ±25 | 0 ±25 | 0 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | -2 ±2 | 0 ±1 | 0 ±1 | 0 ±1 | 0 ±2
| B5 CO2 Emissions (kT/year) | 300 ±50 | 400 ±100 | 200 ±100 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
42 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 670 ±140 | 1220 ±90 | 1060 ±80 | 1350 ±70 | 1520 ±90
| B3 RES integration (GWh/yr) | 15550 ±3110 | 20640 ±10 | 20650 ±20 | 19200 ±150 | 20180 ±70
| B4 Losses (GWh/yr) | 550 ±55 | 925 ±92 | 1000 ±100 | 1300 ±130 | 1825 ±182
| B4 Losses (Meuros/yr) | 23 ±3 | 50 ±5 | 46 ±5 | 77 ±8 | 122 ±13
| B5 CO2 Emissions (kT/year) | -12200 ±1830 | -11700 ±200 | -15800 ±2000 | -7300 ±1000 | -8400 ±1300
| S1 - Environmental impact | More than 100km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
47 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 80 ±10 | 80 ±20 | 90 ±70 | 210 ±60 | 180 ±70
| B3 RES integration (GWh/yr) | 10 ±< 10 | 60 ±10 | 20 ±10 | 2030 ±260 | 1210 ±220
| B4 Losses (GWh/yr) | -25 ±25 | 320 ±100 | 75 ±25 | 350 ±35 | 515 ±35
| B4 Losses (Meuros/yr) | -2 ±2 | 17 ±6 | 3 ±2 | 21 ±2 | 34 ±3
| B5 CO2 Emissions (kT/year) | 1100 ±160 | 1100 ±100 | 600 ±300 | -900 ±700 | -1200 ±200
| S1 - Environmental impact | 15-50km
| S2 - social impact | 15-25km
| B6 Technical resilience | +
| B7 Robustness | ++
48 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 10 ±10 | 10 ±10
| B4 Losses (GWh/yr) | -25 ±25 | 50 ±25 | -725 ±315 | -105 ±25 | -125 ±25
| B4 Losses (Meuros/yr) | -2 ±2 | 2 ±2 | -34 ±15 | -7 ±2 | -9 ±2
| B5 CO2 Emissions (kT/year) | -200 ±50 | ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
| B6 Technical resilience | +
| B7 Robustness | +
54 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
55 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | 0 ±25 | -25 ±25 | -25 ±25 | -50 ±25 | -50 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | -2 ±2 | -1 ±1 | -3 ±2 | -4 ±2
| B5 CO2 Emissions (kT/year) | ±100 | ±100 | ±100 | ±100 | -100 ±100
| S1 - Environmental impact | 15-50km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
62 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | 20 ±10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 10 ±10 | <10
| B4 Losses (GWh/yr) | -25 ±25 | 150 ±25 | 175 ±25 | 25 ±25 | 25 ±25
| B4 Losses (Meuros/yr) | -2 ±2 | 8 ±1 | 8 ±1 | 1 ±2 | 1 ±2
| B5 CO2 Emissions (kT/year) | ±100 | 200 ±100 | 200 ±100 | ±100 | ±100
| S1 - Environmental impact | More than 100km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | ++
| B7 Robustness | ++
69 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
71 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±10 | 10 ±10 | 20 ±10 | 10 ±10 | 20 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 160 ±100 | 150 ±50
| B4 Losses (GWh/yr) | 200 ±25 | 200 ±25 | 250 ±25 | 225 ±25 | 225 ±25
| B4 Losses (Meuros/yr) | 8 ±1 | 10 ±2 | 11 ±2 | 13 ±2 | 15 ±2
| B5 CO2 Emissions (kT/year) | 300 ±30 | 300 ±100 | ±100 | -200 ±100 | ±100
| S1 - Environmental impact | 50-100km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | ++
| B7 Robustness | +
74 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 90 ±20 | 40 ±10 | 90 ±10 | 80 ±10 | 80 ±20
| B3 RES integration (GWh/yr) | <10 | <10 | 740 ±210 | 720 ±210 | 530 ±170
| B4 Losses (GWh/yr) | 0 ±25 | -300 ±30 | -320 ±30 | -100 ±25 | 120 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | -17 ±2 | -15 ±2 | -6 ±2 | 8 ±2
| B5 CO2 Emissions (kT/year) | 1600 ±250 | 800 ±100 | 200 ±300 | -500 ±100 | -600 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
75 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 320 ±50 | 430 ±40 | 360 ±20 | 420 ±20 | 480 ±40
| B3 RES integration (GWh/yr) | 7070 ±1420 | 7100 ±40 | 7080 ±10 | 6260 ±190 | 6920 ±80
| B4 Losses (GWh/yr) | 120 ±25 | 570 ±50 | 570 ±50 | 250 ±25 | 250 ±25
| B4 Losses (Meuros/yr) | 5 ±1 | 30 ±3 | 26 ±3 | 14 ±2 | 16 ±2
| B5 CO2 Emissions (kT/year) | -800 ±5130 | -3800 ±200 | -4800 ±200 | -2200 ±100 | -2300 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
77 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 40 ±10 | 70 ±10 | 40 ±10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 100 ±100 | 400 ±100 | ±100 | 200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
78 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 1380 ±210 | 1040 ±160 | 750 ±110 | 1370 ±210
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 3600 ±500 | 3000 ±500 | 2400 ±400 | 4900 ±700
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
79 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 630 ±90 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 20000 ±3000 | -300 ±100 | -100 ±100 | 53700 ±8100
| S1 - Environmental impact | 50-100km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
81 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±10 | 20 ±10 | 20 ±10 | 30 ±10 | 30 ±10
| B3 RES integration (GWh/yr) | 120 ±30 | 90 ±30 | 50 ±10 | 260 ±60 | 200 ±40
| B4 Losses (GWh/yr) | -25 ±25 | -25 ±25 | -25 ±25 | 0 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | -2 ±2 | -2 ±2 | -1 ±1 | 0 ±1 | 0 ±2
| B5 CO2 Emissions (kT/year) | -200 ±30 | ±100 | ±100 | -200 ±100 | -300 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
82 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 40 ±10 | 30 ±10 | 20 ±10 | 30 ±10
| B3 RES integration (GWh/yr) | - | 570 ±40 | 510 ±30 | 200 ±100 | 480 ±50
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | -200 ±100 | -300 ±100 | -200 ±100 | -400 ±300
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
85 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 20 ±10 | 120 ±20 | 40 ±10 | 240 ±40
| B3 RES integration (GWh/yr) | - | 290 ±60 | 1340 ±270 | 490 ±100 | 2750 ±550
| B4 Losses (GWh/yr) | - | 0 ±25 | 0 ±25 | 0 ±25 | 75 ±25
| B4 Losses (Meuros/yr) | - | 0 ±1 | 0 ±1 | 0 ±1 | 5 ±2
| B5 CO2 Emissions (kT/year) | - | -100 ±100 | -500 ±100 | -200 ±100 | -1000 ±200
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
86 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | 50 ±10 | 70 ±10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
92 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 30 ±20 | 30 ±10 | 20 ±10 | 20 ±10 | 10 ±10
| B3 RES integration (GWh/yr) | <10 | 10 ±10 | <10 | 270 ±150 | 150 ±40
| B4 Losses (GWh/yr) | -40 ±25 | 250 ±50 | 350 ±50 | 100 ±50 | 75 ±25
| B4 Losses (Meuros/yr) | -2 ±1 | 13 ±3 | 16 ±2 | 6 ±3 | 5 ±2
| B5 CO2 Emissions (kT/year) | 600 ±100 | 600 ±100 | 300 ±200 | -100 ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
94 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 130 ±20 | 190 ±10 | 140 ±20 | 70 ±10 | 70 ±10
| B3 RES integration (GWh/yr) | 10 ±< 10 | 10 ±10 | 10 ±10 | 350 ±70 | 170 ±10
| B4 Losses (GWh/yr) | 475 ±47 | 1025 ±102 | -75 ±25 | -150 ±25 | 350 ±35
| B4 Losses (Meuros/yr) | 20 ±2 | 55 ±6 | -4 ±2 | -9 ±2 | 23 ±3
| B5 CO2 Emissions (kT/year) | -400 ±50 | 2000 ±100 | 500 ±100 | -1700 ±300 | -1400 ±200
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
96 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | - | - | - | -
| B3 RES integration (GWh/yr) | - | - | - | - | -
| B4 Losses (GWh/yr) | -25 ±25 | -25 ±25 | -50 ±25 | -75 ±25 | -75 ±25
| B4 Losses (Meuros/yr) | -2 ±2 | -2 ±2 | -2 ±1 | -5 ±2 | -5 ±2
| B5 CO2 Emissions (kT/year) | - | - | - | - | -
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
103 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 10 ±10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | 10 ±20 | 80 ±90 | 40 ±20
| B4 Losses (GWh/yr) | - | -350 ±35 | -350 ±35 | -400 ±40 | -375 ±37
| B4 Losses (Meuros/yr) | - | -19 ±2 | -17 ±2 | -24 ±3 | -26 ±3
| B5 CO2 Emissions (kT/year) | 300 ±50 | 300 ±100 | 200 ±100 | ±100 | ±100
| S1 - Environmental impact | More than 100km
| S2 - social impact | More than 50km
| B6 Technical resilience | +
| B7 Robustness | ++
107 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 80 ±20 | 70 ±10 | 80 ±10 | 100 ±20 | 90 ±10
| B3 RES integration (GWh/yr) | 490 ±100 | 580 ±140 | 610 ±150 | 1340 ±180 | 950 ±200
| B4 Losses (GWh/yr) | - | 550 ±55 | 625 ±62 | 700 ±70 | 700 ±70
| B4 Losses (Meuros/yr) | - | 30 ±3 | 29 ±3 | 42 ±4 | 47 ±5
| B5 CO2 Emissions (kT/year) | 800 ±100 | 300 ±200 | 400 ±400 | -600 ±100 | -500 ±200
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
110 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 190 ±30 | 140 ±10 | 190 ±10 | 170 ±30 | 140 ±10
| B3 RES integration (GWh/yr) | 90 ±20 | 150 ±150 | 850 ±60 | 840 ±170 | 870 ±390
| B4 Losses (GWh/yr) | 875 ±87 | 475 ±47 | 275 ±27 | 275 ±27 | 475 ±105
| B4 Losses (Meuros/yr) | 37 ±4 | 25 ±3 | 12 ±2 | 16 ±2 | 32 ±7
| B5 CO2 Emissions (kT/year) | 2200 ±350 | 1500 ±400 | 700 ±300 | -900 ±300 | -900 ±600
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
111 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | 20 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | 50 ±25 | -25 ±25 | -50 ±25 | -85 ±45 | -120 ±70
| B4 Losses (Meuros/yr) | 2 ±1 | -2 ±2 | -2 ±1 | -5 ±3 | -8 ±5
| B5 CO2 Emissions (kT/year) | ±100 | -100 ±100 | ±100 | ±100 | -200 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | ++
| B7 Robustness | ++
113 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 50 ±40 | 30 ±10 | 20 ±10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | 30 ±20 | <10 | 40 ±40 | 100 ±40
| B4 Losses (GWh/yr) | -125 ±25 | -275 ±175 | 30 ±130 | 0 ±25 | -25 ±25
| B4 Losses (Meuros/yr) | -6 ±1 | -15 ±10 | 1 ±6 | 0 ±1 | -2 ±2
| B5 CO2 Emissions (kT/year) | 1100 ±180 | 800 ±200 | 500 ±100 | ±100 | 100 ±200
| S1 - Environmental impact | 15-50km
| S2 - social impact | 25-50km
| B6 Technical resilience | +
| B7 Robustness | +
120 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | - | - | 400 ±40 | 420 ±40
| B3 RES integration (GWh/yr) | - | - | - | 6410 ±200 | 6650 ±200
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | - | - | -2100 ±100 | -2100 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
121 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 40 ±10 | 70 ±10 | 60 ±10 | 70 ±10
| B3 RES integration (GWh/yr) | - | <10 | 640 ±150 | 640 ±120 | 360 ±130
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 700 ±200 | ±100 | -400 ±100 | -600 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
123 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 70 ±10 | 80 ±10 | 30 ±10 | 30 ±10 | 30 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 60 ±10 | 20 ±10
| B4 Losses (GWh/yr) | 825 ±82 | 650 ±65 | 300 ±30 | 225 ±25 | 525 ±52
| B4 Losses (Meuros/yr) | 35 ±4 | 35 ±4 | 13 ±2 | 13 ±2 | 35 ±4
| B5 CO2 Emissions (kT/year) | -400 ±50 | 1400 ±200 | 600 ±100 | -1500 ±200 | -1100 ±200
| S1 - Environmental impact | 15-50km
| S2 - social impact | 25-50km
| B6 Technical resilience | 0
| B7 Robustness | ++
124 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | - | - | - | -
| B3 RES integration (GWh/yr) | - | - | - | - | -
| B4 Losses (GWh/yr) | -150 ±25 | -150 ±25 | -125 ±25 | -100 ±25 | -75 ±25
| B4 Losses (Meuros/yr) | -7 ±1 | -8 ±1 | -6 ±1 | -6 ±2 | -5 ±2
| B5 CO2 Emissions (kT/year) | - | - | - | - | -
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | ++
| B7 Robustness | ++
126 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | 100 ±25 | 0 ±25 | 0 ±25 | 0 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | 4 ±1 | 0 ±1 | 0 ±1 | 0 ±1 | 0 ±2
| B5 CO2 Emissions (kT/year) | 300 ±50 | -200 ±100 | ±100 | ±100 | 200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | ++
| B7 Robustness | ++
127 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 240 ±40 | 260 ±40 | 260 ±40 | 420 ±60 | 420 ±60
| B3 RES integration (GWh/yr) | 3950 ±790 | 3910 ±780 | 3910 ±780 | 4340 ±870 | 4270 ±850
| B4 Losses (GWh/yr) | -225 ±25 | -200 ±25 | -175 ±25 | -325 ±32 | -300 ±30
| B4 Losses (Meuros/yr) | -10 ±1 | -11 ±2 | -8 ±1 | -19 ±2 | -20 ±2
| B5 CO2 Emissions (kT/year) | -2200 ±300 | -2200 ±300 | -2200 ±300 | -2400 ±400 | -2400 ±400
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
129 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | - | - | 870 ±40 | 1110 ±70
| B3 RES integration (GWh/yr) | - | - | - | 12560 ±290 | 15140 ±50
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | - | - | -4700 ±100 | -6000 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
130 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 50 ±10 | 160 ±20 | 80 ±10 | 90 ±10 | 80 ±10
| B3 RES integration (GWh/yr) | 30 ±10 | 250 ±50 | 110 ±20 | 850 ±170 | 660 ±130
| B4 Losses (GWh/yr) | 0 ±25 | 225 ±25 | 75 ±25 | -50 ±25 | 25 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | 12 ±1 | 3 ±2 | -3 ±2 | 1 ±2
| B5 CO2 Emissions (kT/year) | -100 ±20 | 900 ±100 | 400 ±100 | -700 ±100 | -1000 ±200
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | ++
| B7 Robustness | ++
132 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±< 10 | 150 ±20 | 70 ±10 | 510 ±80 | 310 ±50
| B3 RES integration (GWh/yr) | 30 ±10 | 600 ±120 | 220 ±40 | 5720 ±1140 | 3560 ±710
| B4 Losses (GWh/yr) | 0 ±25 | -375 ±37 | -275 ±27 | -325 ±32 | -300 ±30
| B4 Losses (Meuros/yr) | 0 ±1 | -20 ±2 | -13 ±2 | -19 ±2 | -20 ±2
| B5 CO2 Emissions (kT/year) | ±100 | 300 ±100 | 200 ±100 | -2900 ±400 | -2100 ±300
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | ++
| B7 Robustness | ++
133 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 90 ±10 | 40 ±10 | 530 ±80 | 900 ±130
| B3 RES integration (GWh/yr) | - | 250 ±50 | 170 ±30 | 5780 ±1160 | 9950 ±1990
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 300 ±100 | ±100 | -2800 ±400 | -5100 ±800
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | ++
| B7 Robustness | ++
134 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 240 ±40 | 360 ±50 | 260 ±40 | 330 ±50 | 270 ±40
| B3 RES integration (GWh/yr) | 1440 ±290 | 1680 ±340 | 1030 ±210 | 3430 ±690 | 2350 ±470
| B4 Losses (GWh/yr) | -75 ±25 | -275 ±27 | -175 ±25 | 100 ±25 | 75 ±25
| B4 Losses (Meuros/yr) | -4 ±1 | -15 ±2 | -8 ±1 | 5 ±2 | 5 ±2
| B5 CO2 Emissions (kT/year) | 800 ±130 | 600 ±100 | 600 ±100 | -1500 ±200 | -1000 ±200
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
135 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±< 10 | 120 ±20 | 60 ±10 | 30 ±10 | 20 ±10
| B3 RES integration (GWh/yr) | <10 | 370 ±70 | 110 ±20 | 200 ±20 | <10
| B4 Losses (GWh/yr) | -225 ±25 | -175 ±25 | -225 ±25 | -350 ±35 | -225 ±25
| B4 Losses (Meuros/yr) | -10 ±1 | -10 ±2 | -11 ±2 | -21 ±2 | -15 ±2
| B5 CO2 Emissions (kT/year) | ±100 | 300 ±100 | 200 ±100 | 200 ±100 | 200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
136 | B1 SoS (MWh/yr) | 0 | 0 | 0 | 0 | 0
| B2 SEW (MEuros/yr) | 30 ±< 10 | 20 ±10 | 10 ±10 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | 25 ±25 | -75 ±25 | -25 ±25 | 25 ±25 | -75 ±25
| B4 Losses (Meuros/yr) | 1 ±1 | -4 ±1 | -1 ±1 | 1 ±2 | -5 ±2
| B5 CO2 Emissions (kT/year) | 500 ±50 | 300 ±100 | 300 ±100 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | 15-25km
| B6 Technical resilience | +
| B7 Robustness | ++
138 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 60 ±10 | 80 ±10 | 50 ±10 | 40 ±10 | 270 ±40
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 30 ±10 | 140 ±30
| B4 Losses (GWh/yr) | 50 ±25 | 25 ±25 | 125 ±25 | -125 ±25 | -150 ±25
| B4 Losses (Meuros/yr) | 2 ±1 | 1 ±2 | 6 ±1 | -8 ±2 | -10 ±2
| B5 CO2 Emissions (kT/year) | 700 ±100 | 1100 ±200 | 700 ±100 | -900 ±100 | -900 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
141 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 10 ±< 10 | 80 ±10 | 80 ±10 | 10 ±10 | 30 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | 25 ±25 | -125 ±25 | -125 ±25 | -100 ±25 | -50 ±25
| B4 Losses (Meuros/yr) | 1 ±1 | -7 ±2 | -6 ±1 | -6 ±2 | -4 ±2
| B5 CO2 Emissions (kT/year) | 200 ±80 | 900 ±100 | 800 ±100 | -200 ±100 | -300 ±100
| S1 - Environmental impact | More than 100km
| S2 - social impact | 15-25km
| B6 Technical resilience | 0
| B7 Robustness | ++
142 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 30 ±10 | 20 ±10 | 30 ±10 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 30 ±10 | 80 ±20
| B4 Losses (GWh/yr) | 0 ±25 | 0 ±25 | -75 ±25 | -175 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | 0 ±1 | -4 ±2 | -11 ±2 | 0 ±2
| B5 CO2 Emissions (kT/year) | 500 ±80 | 400 ±100 | 400 ±100 | ±100 | ±100
| S1 - Environmental impact | 15-50km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
144 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 50 ±10 | 90 ±10 | 60 ±10 | <10 | 60 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 30 ±10 | 120 ±20
| B4 Losses (GWh/yr) | 25 ±25 | 325 ±32 | 125 ±25 | 75 ±25 | 75 ±25
| B4 Losses (Meuros/yr) | 1 ±1 | 17 ±2 | 6 ±1 | 4 ±2 | 5 ±2
| B5 CO2 Emissions (kT/year) | 900 ±50 | 1700 ±300 | 1100 ±200 | ±100 | -400 ±100
| S1 - Environmental impact | 15-50km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
146 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 30 ±10 | 30 ±10 | 20 ±10 | 20 ±10 | 30 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 140 ±30 | <10
| B4 Losses (GWh/yr) | -150 ±25 | -50 ±25 | 75 ±25 | -250 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | -7 ±1 | -3 ±2 | 3 ±2 | -15 ±2 | 0 ±2
| B5 CO2 Emissions (kT/year) | 400 ±80 | 400 ±100 | 400 ±100 | ±100 | -100 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
147 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 250 ±20 | 60 ±10 | 130 ±20 | 30 ±10 | 170 ±30
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 250 ±50 | 650 ±130
| B4 Losses (GWh/yr) | -150 ±25 | 25 ±25 | 0 ±25 | -125 ±25 | 100 ±25
| B4 Losses (Meuros/yr) | -7 ±1 | 1 ±2 | 0 ±1 | -8 ±2 | 6 ±2
| B5 CO2 Emissions (kT/year) | 700 ±100 | 700 ±100 | 700 ±100 | ±100 | -400 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
150 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 70 ±10 | 90 ±30 | 110 ±30 | 20 ±10 | 20 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 20 ±20 | 40 ±40
| B4 Losses (GWh/yr) | 75 ±25 | -200 ±25 | 225 ±25 | 75 ±25 | 125 ±25
| B4 Losses (Meuros/yr) | 3 ±1 | -11 ±2 | 10 ±2 | 4 ±2 | 8 ±2
| B5 CO2 Emissions (kT/year) | 1700 ±130 | 1600 ±500 | 1100 ±200 | ±100 | -200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
151 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
153 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 120 ±20 | 80 ±10 | 140 ±10 | 120 ±30 | 120 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | 980 ±190 | 1160 ±230 | 690 ±220
| B4 Losses (GWh/yr) | -125 ±25 | -200 ±25 | 375 ±37 | 850 ±85 | 850 ±85
| B4 Losses (Meuros/yr) | -6 ±1 | -11 ±2 | 17 ±2 | 51 ±5 | 57 ±6
| B5 CO2 Emissions (kT/year) | 2300 ±330 | 1400 ±400 | 500 ±400 | -800 ±200 | -800 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
157 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 30 ±10 | 30 ±10 | 60 ±10 | 80 ±10
| B3 RES integration (GWh/yr) | - | 680 ±140 | 690 ±140 | 720 ±140 | 830 ±170
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | -200 ±100 | -200 ±100 | -200 ±100 | -300 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
158 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | 200 ±30 | 200 ±30
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | -100 ±25 | -150 ±25 | -225 ±25 | -125 ±25
| B4 Losses (Meuros/yr) | - | -6 ±2 | -7 ±1 | -14 ±2 | -9 ±2
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | -700 ±140 | -700 ±140
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
164 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 140 ±20 | 290 ±40 | 360 ±50 | 540 ±80 | 20 ±10
| B3 RES integration (GWh/yr) | 680 ±140 | 2060 ±410 | 3580 ±720 | 6170 ±1230 | 420 ±80
| B4 Losses (GWh/yr) | -250 ±25 | 25 ±25 | 250 ±25 | -25 ±25 | -275 ±27
| B4 Losses (Meuros/yr) | -11 ±1 | 1 ±2 | 11 ±2 | -2 ±2 | -19 ±2
| B5 CO2 Emissions (kT/year) | -800 ±120 | -400 ±100 | -1600 ±200 | -3900 ±600 | -300 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
167 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 150 ±40 | 90 ±10 | 140 ±10 | 110 ±10 | 110 ±10
| B3 RES integration (GWh/yr) | 20 ±10 | 60 ±50 | 990 ±170 | 770 ±100 | 720 ±200
| B4 Losses (GWh/yr) | 0 ±25 | 325 ±32 | 325 ±32 | 700 ±70 | 725 ±72
| B4 Losses (Meuros/yr) | 0 ±1 | 17 ±2 | 14 ±2 | 42 ±4 | 48 ±5
| B5 CO2 Emissions (kT/year) | 2900 ±430 | 1700 ±100 | 600 ±300 | -700 ±100 | -700 ±200
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
168 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | 30 ±10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 200 ±100 | 200 ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
170 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | - | - | - | -
| B3 RES integration (GWh/yr) | - | - | - | - | -
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | - | - | - | -
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
172 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 90 ±20 | 60 ±10 | 100 ±10 | 90 ±20 | 80 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | 740 ±200 | 910 ±280 | 520 ±150
| B4 Losses (GWh/yr) | -325 ±32 | 475 ±47 | 725 ±72 | 950 ±95 | 975 ±97
| B4 Losses (Meuros/yr) | -15 ±2 | 25 ±3 | 33 ±4 | 56 ±6 | 65 ±7
| B5 CO2 Emissions (kT/year) | 1600 ±230 | 1000 ±200 | 400 ±400 | -600 ±200 | -600 ±200
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
173 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | <10 | 20 ±10 | 20 ±10 | 20 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 780 ±160 | 180 ±60
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | ±100 | 200 ±200 | -100 ±100 | ±100 | -200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
174 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 70 ±10 | 20 ±10 | 40 ±20 | 10 ±10 | 20 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 30 ±30 | 60 ±50
| B4 Losses (GWh/yr) | -250 ±25 | -50 ±25 | -50 ±25 | 0 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | -11 ±1 | -3 ±2 | -2 ±1 | 0 ±1 | 0 ±2
| B5 CO2 Emissions (kT/year) | 1400 ±110 | 400 ±200 | 600 ±200 | -100 ±100 | -300 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
175 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | 10 ±10 | 40 ±10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | -100 ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
176 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 30 ±10 | 40 ±10 | 40 ±10 | 20 ±10 | 40 ±10
| B3 RES integration (GWh/yr) | <10 | 10 ±10 | <10 | 280 ±60 | 190 ±40
| B4 Losses (GWh/yr) | 250 ±25 | 275 ±27 | 275 ±27 | 325 ±32 | 225 ±25
| B4 Losses (Meuros/yr) | 10 ±1 | 14 ±2 | 12 ±2 | 19 ±2 | 15 ±2
| B5 CO2 Emissions (kT/year) | -600 ±100 | -300 ±100 | -900 ± | 300 ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | ++
| B7 Robustness | ++
177 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | <10 | <10 | 20 ±0 | 40 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 310 ±30 | 160 ±30
| B4 Losses (GWh/yr) | 0 ±25 | 0 ±25 | 0 ±25 | 0 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | 0 ±1 | 0 ±1 | 0 ±1 | 0 ±2
| B5 CO2 Emissions (kT/year) | ±100 | ±100 | ±100 | -200 ±100 | -700 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
179 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | 40 ±10 | 130 ±30
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 400 ±100 | -300 ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
183 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 10 ±10 | <10 | <10 | 10 ±10 | 10 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 60 ±10 | 170 ±150
| B4 Losses (GWh/yr) | 0 ±25 | 25 ±25 | 25 ±25 | 0 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | 1 ±2 | 1 ±1 | 0 ±1 | 0 ±2
| B5 CO2 Emissions (kT/year) | ±100 | ±100 | -200 ±100 | -200 ±100 | 100 ±200
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
184 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±10 | 20 ±10 | 30 ±0 | 30 ±0 | 50 ±10
| B3 RES integration (GWh/yr) | 20 ±10 | 160 ±80 | 330 ±120 | 220 ±40 | 270 ±40
| B4 Losses (GWh/yr) | 100 ±25 | 100 ±25 | 75 ±25 | 75 ±25 | 100 ±25
| B4 Losses (Meuros/yr) | 4 ±1 | 5 ±2 | 3 ±2 | 4 ±2 | 6 ±2
| B5 CO2 Emissions (kT/year) | 300 ±80 | ±100 | ±100 | -200 ±0 | -500 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
186 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 80 ±20 | 110 ±10 | 100 ±10 | 190 ±10 | 190 ±0
| B3 RES integration (GWh/yr) | 1940 | 1940 ±0 | 1940 ±0 | 2620 ±20 | 2650 ±0
| B4 Losses (GWh/yr) | -150 ±25 | 25 ±25 | 50 ±25 | -25 ±25 | -100 ±25
| B4 Losses (Meuros/yr) | -7 ±1 | 1 ±2 | 2 ±1 | -2 ±2 | -7 ±2
| B5 CO2 Emissions (kT/year) | -1600 ±80 | -6100 ±5000 | -1400 ±0 | -1100 ±100 | -1100 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
187 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 40 ±30 | 30 ±30 | 90 ±30 | 60 ±10
| B3 RES integration (GWh/yr) | - | 20 ±10 | <10 | 860 ±70 | 600 ±240
| B4 Losses (GWh/yr) | - | 175 ±25 | 250 ±25 | 500 ±50 | 300 ±30
| B4 Losses (Meuros/yr) | - | 9 ±2 | 11 ±2 | 30 ±3 | 20 ±2
| B5 CO2 Emissions (kT/year) | - | 800 ±900 | 300 ±300 | -400 ±400 | -300 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
189 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 40 ±10 | 10 ±10 | 50 ±10 | 40 ±10
| B3 RES integration (GWh/yr) | - | 440 ±90 | 100 ±20 | 720 ±190 | 680 ±130
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 200 ±100 | -100 ±100 | -200 ±100 | -300 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | ++
| B7 Robustness | ++
190 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 190 ±30 | 140 ±10 | 190 ±10 | 170 ±30 | 140 ±10
| B3 RES integration (GWh/yr) | 70 ±10 | 150 ±10 | 950 ±210 | 1440 ±230 | 560 ±190
| B4 Losses (GWh/yr) | 2900 ±290 | 370 ±30 | 200 ±25 | 175 ±25 | 795 ±105
| B4 Losses (Meuros/yr) | 125 ±13 | 20 ±2 | 9 ±1 | 10 ±2 | 53 ±7
| B5 CO2 Emissions (kT/year) | 1900 ±280 | 1800 ±200 | 800 ±100 | -1100 ±200 | -500 ±500
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
191 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 560 ±40 | 480 ±30 | 610 ±30 | 700 ±40
| B3 RES integration (GWh/yr) | - | 9690 ±10 | 9710 ±10 | 8860 ±90 | 9370 ±30
| B4 Losses (GWh/yr) | - | 625 ±62 | 700 ±70 | 750 ±75 | 1250 ±125
| B4 Losses (Meuros/yr) | - | 33 ±4 | 32 ±4 | 44 ±5 | 83 ±9
| B5 CO2 Emissions (kT/year) | - | -5700 ±100 | -6800 ±300 | -3300 ±100 | -3800 ±100
| S1 - Environmental impact | More than 100km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
192 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | - | - | 800 ±40 | 910 ±60
| B3 RES integration (GWh/yr) | - | - | - | 11510 ±180 | 12320 ±10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | - | - | -4400 ±500 | -5200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
193 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 150 ±20 | 110 ±20 | 60 ±10 | 70 ±10
| B3 RES integration (GWh/yr) | - | 50 ±10 | 80 ±20 | 150 ±30 | 330 ±70
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | -300 ±100 | -300 ±100 | -200 ±100 | -300 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
194 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 90 ±10 | <10 | 110 ±20 | 130 ±20
| B3 RES integration (GWh/yr) | - | 710 ±140 | <10 | 1730 ±350 | 1830 ±370
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | -300 ±100 | ±100 | -400 ±100 | -400 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
197 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | - | - | - | -
| B3 RES integration (GWh/yr) | - | - | - | - | -
| B4 Losses (GWh/yr) | -25 ±25 | -50 ±25 | -50 ±25 | -75 ±25 | -75 ±25
| B4 Losses (Meuros/yr) | -2 ±2 | -3 ±2 | -2 ±1 | -5 ±2 | -5 ±2
| B5 CO2 Emissions (kT/year) | - | - | - | - | -
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | -
| B7 Robustness | -
198 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | 20 ±20 | <10 | 50 ±0 | 40 ±10
| B3 RES integration (GWh/yr) | <10 | 20 ±10 | <10 | 540 ±40 | 300 ±20
| B4 Losses (GWh/yr) | - | 170 ±30 | 125 ±25 | -75 ±25 | 80 ±160
| B4 Losses (Meuros/yr) | - | 9 ±2 | 6 ±1 | -5 ±2 | 5 ±11
| B5 CO2 Emissions (kT/year) | ±100 | 200 ±300 | ±100 | -200 ±200 | -300 ±100
| S1 - Environmental impact | 50-100km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
199 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 0 ±0 | <10 | <10 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | 0 ±0 | <10 | <10 | <10 | 20 ±20
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | 0 ±0 | ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | 0
| B7 Robustness | +
200 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 0 ±0 | 20 ±10 | 20 ±0 | 40 ±0 | 50 ±10
| B3 RES integration (GWh/yr) | 0 ±0 | 240 ±10 | 230 ±10 | 540 ±40 | 390 ±80
| B4 Losses (GWh/yr) | 0 ±25 | -625 ±62 | -125 ±25 | -25 ±25 | -50 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | -34 ±4 | -6 ±1 | -2 ±2 | -4 ±2
| B5 CO2 Emissions (kT/year) | 0 ±0 | -100 ±100 | -100 ±100 | -200 ±0 | -500 ±100
| S1 - Environmental impact | 15-50km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
203 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 70 ±10 | 140 ±20 | 110 ±20 | 120 ±20 | 190 ±30
| B3 RES integration (GWh/yr) | 10 ±< 10 | 40 ±10 | 50 ±10 | 390 ±80 | 550 ±110
| B4 Losses (GWh/yr) | -100 ±25 | 50 ±25 | 25 ±25 | -50 ±25 | -75 ±25
| B4 Losses (Meuros/yr) | -5 ±1 | 2 ±2 | 1 ±1 | -3 ±2 | -5 ±2
| B5 CO2 Emissions (kT/year) | -200 ±40 | ±100 | ±100 | ±100 | -100 ±100
| S1 - Environmental impact | 15-50km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
204 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | 30 ±10 | 20 ±10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | 10 ±10 | <10 | 50 ±10 | 30 ±10
| B4 Losses (GWh/yr) | -200 ±25 | -175 ±25 | -200 ±25 | -25 ±25 | -25 ±25
| B4 Losses (Meuros/yr) | -9 ±1 | -10 ±2 | -9 ±1 | -2 ±2 | -2 ±2
| B5 CO2 Emissions (kT/year) | ±100 | 200 ±100 | 100 ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
205 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 150 ±20 | 460 ±70 | 300 ±50 | 140 ±20 | 110 ±20
| B3 RES integration (GWh/yr) | <10 | 1350 ±270 | 730 ±150 | 1170 ±230 | 1180 ±240
| B4 Losses (GWh/yr) | 575 ±57 | 750 ±75 | 600 ±60 | 300 ±30 | 275 ±27
| B4 Losses (Meuros/yr) | 24 ±3 | 40 ±5 | 27 ±3 | 18 ±2 | 18 ±2
| B5 CO2 Emissions (kT/year) | 1100 ±170 | 1400 ±200 | 1000 ±200 | -300 ±100 | -400 ±100
| S1 - Environmental impact | 50-100km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
206 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | 70 ±10 | 160 ±20 | 60 ±10 | 70 ±10
| B3 RES integration (GWh/yr) | <10 | 130 ±30 | 270 ±50 | 700 ±140 | 700 ±140
| B4 Losses (GWh/yr) | -250 ±25 | -75 ±25 | 0 ±25 | -75 ±25 | -25 ±25
| B4 Losses (Meuros/yr) | -11 ±1 | -4 ±1 | 0 ±1 | -5 ±2 | -2 ±2
| B5 CO2 Emissions (kT/year) | ±100 | 300 ±100 | 700 ±100 | -200 ±100 | -200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
207 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | 230 ±30 | 200 ±30 | 400 ±60 | 220 ±30
| B3 RES integration (GWh/yr) | <10 | 4880 ±980 | 4350 ±870 | 5200 ±1040 | 2810 ±560
| B4 Losses (GWh/yr) | -25 ±25 | 25 ±25 | 100 ±25 | -75 ±25 | -75 ±25
| B4 Losses (Meuros/yr) | -2 ±2 | 1 ±2 | 4 ±2 | -5 ±2 | -5 ±2
| B5 CO2 Emissions (kT/year) | ±100 | -3300 ±500 | -3700 ±500 | -4100 ±600 | -2000 ±300
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
208 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 120 ±20 | 410 ±60 | 310 ±50 | 600 ±90 | 670 ±100
| B3 RES integration (GWh/yr) | 250 ±50 | 2540 ±510 | 1800 ±360 | 1150 ±230 | 7170 ±1430
| B4 Losses (GWh/yr) | -200 ±25 | -175 ±25 | -175 ±25 | -100 ±25 | 175 ±25
| B4 Losses (Meuros/yr) | -9 ±1 | -10 ±2 | -8 ±1 | -6 ±2 | 11 ±2
| B5 CO2 Emissions (kT/year) | -100 ±20 | ±100 | 200 ±100 | -6800 ±1000 | -3900 ±600
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
209 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 70 ±10 | 20 ±10 | <10 | 80 ±10 | <10
| B3 RES integration (GWh/yr) | 40 ±10 | 410 ±80 | 180 ±40 | 970 ±190 | 60 ±10
| B4 Losses (GWh/yr) | -150 ±25 | -125 ±25 | -125 ±25 | -125 ±25 | -150 ±25
| B4 Losses (Meuros/yr) | -7 ±1 | -7 ±2 | -6 ±1 | -8 ±2 | -10 ±2
| B5 CO2 Emissions (kT/year) | 400 ±60 | -300 ±100 | -200 ±100 | -800 ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
210 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 30 ±< 10 | <10 | 10 ±10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 20 ±30 | 10 ±30
| B4 Losses (GWh/yr) | 0 ±25 | -200 ±25 | 0 ±25 | 25 ±25 | -25 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | -11 ±2 | 0 ±1 | 1 ±2 | -2 ±2
| B5 CO2 Emissions (kT/year) | 600 ±40 | 200 ±0 | 200 ±0 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
214 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 370 ±10 | 320 ±20 | 330 ±50 | 380 ±10
| B3 RES integration (GWh/yr) | - | 5710 ±10 | 5430 ±160 | 4750 ±810 | 5470 ±10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | -2300 ±100 | -3000 ±200 | -1500 ±300 | -2100 ±100
S1 - Environmental impact
S2 - social impact
| B6 Technical resilience | +
| B7 Robustness | +
216 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 50 ±10 | 200 ±30 | 250 ±40 | 200 ±30
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | -100 ±25 | -175 ±25 | -175 ±25 | -150 ±25
| B4 Losses (Meuros/yr) | - | -6 ±2 | -8 ±1 | -11 ±2 | -10 ±2
| B5 CO2 Emissions (kT/year) | - | -200 ±100 | -700 ±100 | -900 ±100 | -700 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
219 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 360 ±40 | 660 ±100 | 580 ±90 | 1010 ±150 | 1120 ±170
| B3 RES integration (GWh/yr) | 750 ±50 | 4080 ±820 | 4070 ±810 | 3260 ±650 | 3010 ±600
| B4 Losses (GWh/yr) | 1250 ±125 | 1100 ±110 | 1100 ±110 | 1225 ±122 | 2050 ±205
| B4 Losses (Meuros/yr) | 54 ±5 | 59 ±6 | 51 ±5 | 73 ±7 | 137 ±14
| B5 CO2 Emissions (kT/year) | ±100 | -5600 ±800 | -6800 ± | -2300 ±300 | -1300 ±200
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
225 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 20 ±10 | <10 | 10 ±10 | 10 ±10
| B3 RES integration (GWh/yr) | - | 10 ±10 | 10 ±10 | 170 ±70 | 80 ±20
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 400 ±100 | ±100 | ±100 | -100 ±200
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
227 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 30 ±10 | 30 ±10 | 20 ±10 | 20 ±10 | 30 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 140 ±30 | <10
| B4 Losses (GWh/yr) | -150 ±25 | -50 ±25 | 75 ±25 | -250 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | -7 ±1 | -3 ±2 | 3 ±2 | -15 ±2 | 0 ±2
| B5 CO2 Emissions (kT/year) | 400 ±80 | 400 ±100 | 400 ±100 | ±100 | -100 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
228 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | 10 ±0 | <10 | 10 ±0 | 10 ±0
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 160 ±0 | 90 ±10
| B4 Losses (GWh/yr) | - | 100 ±50 | 100 ±25 | 125 ±25 | 95 ±35
| B4 Losses (Meuros/yr) | - | 5 ±3 | 4 ±2 | 7 ±2 | 6 ±3
| B5 CO2 Emissions (kT/year) | 100 ±20 | 100 ±0 | ±100 | ±100 | -100 ±0
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
229 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | 80 ±10 | 110 ±20
| B3 RES integration (GWh/yr) | - | 10 ±10 | <10 | <10 | 410 ±10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | -4300 ±600 | -3300 ±800
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | 0
| B7 Robustness | 0
230 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 40 ±10 | 60 ±10 | 50 ±10 | 140 ±10 | 140 ±20
| B3 RES integration (GWh/yr) | 10 ±< 10 | 20 ±10 | 10 ±10 | 770 ±70 | 460 ±10
| B4 Losses (GWh/yr) | -275 ±27 | 75 ±25 | -125 ±25 | -225 ±25 | 800 ±80
| B4 Losses (Meuros/yr) | -12 ±1 | 4 ±1 | -6 ±1 | -14 ±2 | 53 ±6
| B5 CO2 Emissions (kT/year) | -100 ±100 | 600 ±100 | ±100 | -3900 ±1500 | -4200 ±400
| S1 - Environmental impact | More than 100km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | -
| B7 Robustness | -
231 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 10 ±10 | <10 | 30 ±10 | 20 ±0
| B3 RES integration (GWh/yr) | - | <10 | <10 | 450 ±30 | 240 ±0
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 200 ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
232 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | 60 ±10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | -300 ±100 | -200 ±100 | -100 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | -
233 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 30 ±10 | 30 ±10 | 10 ±10 | 120 ±20
| B3 RES integration (GWh/yr) | - | <10 | 210 ±40 | 30 ±10 | 410 ±80
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 1400 ±200 | ±100 | ±100 | -600 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
234 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 50 ±10 | 30 ±10 | 40 ±10 | 50 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | 130 ±30 | 250 ±50
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 900 ±100 | 200 ±100 | -1900 ±300 | -1500 ±200
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | -
235 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 200 ±30 | 300 ±40 | 330 ±50 | 770 ±120 | 910 ±140
| B3 RES integration (GWh/yr) | 870 ±170 | 1220 ±240 | 2860 ±570 | 8090 ±1620 | 9680 ±1940
| B4 Losses (GWh/yr) | -150 ±25 | -50 ±25 | -100 ±25 | 175 ±25 | 375 ±37
| B4 Losses (Meuros/yr) | -7 ±1 | -3 ±2 | -5 ±2 | 10 ±2 | 25 ±3
| B5 CO2 Emissions (kT/year) | -2100 ±320 | 200 ±100 | -2600 ±400 | -4600 ±700 | -5400 ±800
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | ++
| B7 Robustness | ++
236 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±10 | 10 ±10 | 80 ±10 | 80 ±10 | 130 ±20
| B3 RES integration (GWh/yr) | <10 | <10 | 590 ±120 | 950 ±190 | 760 ±150
| B4 Losses (GWh/yr) | -70 ±25 | -80 ±25 | -150 ±25 | 80 ±25 | 250 ±25
| B4 Losses (Meuros/yr) | -4 ±2 | -5 ±2 | -7 ±1 | 4 ±2 | 16 ±2
| B5 CO2 Emissions (kT/year) | 400 ±100 | 200 ±100 | 200 ±100 | -400 ±100 | -800 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | 15-25km
| B6 Technical resilience | +
| B7 Robustness | +
237 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | 10 ±10 | 10 ±10 | 10 ±10
| B3 RES integration (GWh/yr) | - | <10 | 20 ±20 | 40 ±40 | 70 ±40
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 200 ±100 | -100 ±100 | -100 ±100 | -200 ±200
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | ++
| B7 Robustness | +
238 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 20 ±10 | 20 ±10 | 10 ±10 | 20 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | 180 ±40 | 160 ±30
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | -400 ±100 | -600 ± | ±100 | -300 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | ++
| B7 Robustness | ++
239 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | 10 ±10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | -200 ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | ++
| B7 Robustness | ++
240 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 30 ±10 | 190 ±30 | 150 ±20 | 410 ±60 | 390 ±60
| B3 RES integration (GWh/yr) | 130 ±30 | 2020 ±400 | 1750 ±350 | 4890 ±980 | 4610 ±920
| B4 Losses (GWh/yr) | -25 ±25 | 250 ±25 | 225 ±25 | 175 ±25 | 150 ±25
| B4 Losses (Meuros/yr) | -2 ±2 | 13 ±2 | 10 ±2 | 10 ±2 | 10 ±2
| B5 CO2 Emissions (kT/year) | -100 ±20 | -1000 ±200 | -1000 ±200 | -2400 ±400 | -2200 ±300
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
241 | B1 SoS (MWh/yr) | 0 | 0 | 0 | 0 | 0
| B2 SEW (MEuros/yr) | 20 ±10 | 10 ±10 | <10 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | 25 ±25 | 150 ±25 | 25 ±25 | -75 ±25
| B4 Losses (Meuros/yr) | - | 1 ±2 | 7 ±1 | 1 ±2 | -5 ±2
| B5 CO2 Emissions (kT/year) | 200 ±30 | 300 ±100 | 200 ±100 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
242 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 160 ±30 | 230 ±20 | 200 ±10 | 230 ±10 | 270 ±20
| B3 RES integration (GWh/yr) | 3940 ±790 | 3940 ±10 | 3950 ±10 | 3420 ±90 | 3690 ±20
| B4 Losses (GWh/yr) | 250 ±25 | 375 ±37 | 450 ±45 | 250 ±25 | 225 ±25
| B4 Losses (Meuros/yr) | 10 ±1 | 20 ±2 | 21 ±2 | 14 ±2 | 15 ±2
| B5 CO2 Emissions (kT/year) | -3100 ±460 | -2400 ±400 | -2800 ±100 | -1300 ±0 | -1400 ±200
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | 0
| B7 Robustness | +
243 | B1 SoS (MWh/yr) | 0 | 0 | 0 | 0 | 0
| B2 SEW (MEuros/yr) | 230 ±20 | 10 ±10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | 3940 ±10 | <10 | <10 | 10 ±10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | -2400 ±400 | 200 ±100 | 100 ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
244 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 30 ±10 | 40 ±10 | 30 ±10 | 70 ±20 | 60 ±10
| B3 RES integration (GWh/yr) | 20 ±10 | 20 ±10 | <10 | 790 ±30 | 390 ±30
| B4 Losses (GWh/yr) | - | 570 ±50 | 380 ±50 | 480 ±80 | 440 ±80
| B4 Losses (Meuros/yr) | - | 30 ±3 | 17 ±3 | 28 ±5 | 29 ±6
| B5 CO2 Emissions (kT/year) | 1500 ±820 | 800 ±500 | ±100 | -200 ±200 | -500 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
245 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 90 ±50 | 50 ±50
| B4 Losses (GWh/yr) | 0 ±25 | 25 ±25 | 25 ±25 | -75 ±25 | -75 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | 1 ±2 | 1 ±1 | -5 ±2 | -5 ±2
| B5 CO2 Emissions (kT/year) | 300 ±50 | 200 ±100 | 200 ±100 | ±100 | 100 ±200
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
247 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 80 ±10 | 140 ±10 | 120 ±20 | 130 ±10
| B3 RES integration (GWh/yr) | - | <10 | 840 ±560 | 1330 ±440 | 750 ±290
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 1600 ±300 | 400 ±400 | -700 ±100 | -900 ±400
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
248 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 30 ±10 | - | 320 ±10 | 370 ±20
| B3 RES integration (GWh/yr) | - | 460 ±90 | - | 4610 ±110 | 5020 ±1000
| B4 Losses (GWh/yr) | - | -100 ±25 | - | 200 ±25 | 200 ±25
| B4 Losses (Meuros/yr) | - | -6 ±2 | - | 11 ±2 | 13 ±2
| B5 CO2 Emissions (kT/year) | - | -300 ±100 | - | -1700 ±0 | -2000 ±300
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | 0
| B7 Robustness | +
249 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 170 ±30 | 600 ±90 | 710 ±110 | 550 ±80
| B3 RES integration (GWh/yr) | - | 2050 ±410 | 3550 ±710 | 2910 ±580 | 8570 ±1710
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | -600 ±100 | -2100 ±300 | -2400 ±400 | -1900 ±300
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
250 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±< 10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | <10 | 10 ±10
| B4 Losses (GWh/yr) | -25 ±25 | 0 ±25 | 0 ±25 | 75 ±25 | 100 ±25
| B4 Losses (Meuros/yr) | -2 ±2 | 0 ±1 | 0 ±1 | 4 ±2 | 6 ±2
| B5 CO2 Emissions (kT/year) | 400 ±30 | ±100 | 100 ±100 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | -
| B7 Robustness | +
251 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 50 ±10 | 30 ±10 | 140 ±20 | 90 ±10 | 50 ±10
| B3 RES integration (GWh/yr) | 930 ±190 | 70 ±10 | 210 ±40 | 980 ±200 | 590 ±120
| B4 Losses (GWh/yr) | -275 ±27 | -225 ±25 | -125 ±25 | -175 ±25 | -475 ±47
| B4 Losses (Meuros/yr) | -12 ±1 | -12 ±1 | -6 ±1 | -11 ±2 | -32 ±3
| B5 CO2 Emissions (kT/year) | -1000 ±150 | ±100 | -300 ±100 | -800 ±100 | -500 ±100
| S1 - Environmental impact | 15-50km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | ++
252 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 30 ±20 | 30 ±10 | <10 | 20 ±10 | <10
| B3 RES integration (GWh/yr) | <10 | 10 ±10 | 20 ±10 | 240 ±50 | 110 ±20
| B4 Losses (GWh/yr) | -25 ±25 | -25 ±25 | -25 ±25 | -25 ±25 | -25 ±25
| B4 Losses (Meuros/yr) | -2 ±2 | -2 ±2 | -1 ±1 | -2 ±2 | -2 ±2
| B5 CO2 Emissions (kT/year) | 500 ±100 | 500 ±100 | ±100 | ±100 | -300 ±100
| S1 - Environmental impact | 15-50km
| S2 - social impact | 25-50km
| B6 Technical resilience | +
| B7 Robustness | +
253 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 10 ±0 | 20 ±20
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | ±100 | ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
254 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 30 ±< 10 | 70 ±10 | 40 ±10 | 30 ±10 | 30 ±10
| B3 RES integration (GWh/yr) | <10 | 70 ±10 | 70 ±10 | 250 ±50 | 240 ±50
| B4 Losses (GWh/yr) | 0 ±25 | 125 ±25 | 100 ±25 | 0 ±25 | 25 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | 6 ±2 | 4 ±2 | 0 ±1 | 1 ±2
| B5 CO2 Emissions (kT/year) | 300 ±50 | 400 ±100 | 200 ±100 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | ++
| B7 Robustness | ++
255 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±< 10 | 30 ±10 | 40 ±10 | 70 ±10 | 90 ±10
| B3 RES integration (GWh/yr) | 50 ±10 | 20 ±10 | 30 ±10 | 140 ±30 | 270 ±50
| B4 Losses (GWh/yr) | 25 ±25 | -100 ±25 | 100 ±25 | 50 ±25 | 75 ±25
| B4 Losses (Meuros/yr) | 1 ±1 | -6 ±2 | 4 ±2 | 2 ±2 | 5 ±2
| B5 CO2 Emissions (kT/year) | ±100 | -800 ±100 | -900 ±100 | -600 ±100 | -700 ±100
| S1 - Environmental impact | 50-100km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
256 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 10 ±10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | - | 10 ±10 | 10 ±10 | <10 | 20 ±10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 300 ±100 | ±100 | ±100 | -200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
257 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | - | <10 | 10 ±<10 | <10 | 40 ±20
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
258 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 20 ±< 10 | 60 ±10 | 50 ±10 | 80 ±10 | 20 ±10
| B3 RES integration (GWh/yr) | 200 ±40 | 1230 ±250 | 850 ±170 | 780 ±160 | 280 ±60
| B4 Losses (GWh/yr) | -50 ±25 | -25 ±25 | 75 ±25 | 25 ±25 | 25 ±25
| B4 Losses (Meuros/yr) | -3 ±1 | -2 ±2 | 3 ±2 | 1 ±2 | 1 ±2
| B5 CO2 Emissions (kT/year) | -400 ±60 | -1000 ±200 | -1000 ±200 | -800 ±100 | -300 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
259 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 20 ±10 | 10 ±10 | <10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 400 ±100 | 300 ±100 | ±100 | -200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | -
| B7 Robustness | -
260 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 40 ±10 | 70 ±10 | 70 ±20 | 70 ±10
| B3 RES integration (GWh/yr) | - | <10 | 640 ±140 | 640 ±140 | 390 ±120
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 800 ±100 | ±100 | -400 ±100 | -800 ±400
| S1 - Environmental impact | More than 100km
| S2 - social impact | More than 50km
| B6 Technical resilience | +
| B7 Robustness | ++
261 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | - | - | - | -
| B3 RES integration (GWh/yr) | - | - | - | - | -
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | - | - | - | -
| B6 Technical resilience | +
| B7 Robustness | ++
262 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | 70 ±70 | 30 ±30
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 100 ±100 | ±100 | ±100 | -100 ±200
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
263 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | 30 ±10 | 10 ±10 | 50 ±10 | 30 ±10
| B3 RES integration (GWh/yr) | <10 | 10 ±10 | <10 | 750 ±150 | 350 ±30
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | ±100 | 500 ±100 | 100 ±100 | -100 ±0 | -100 ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | ++
| B7 Robustness | ++
264 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 110 ±20 | 70 ±20 | 40 ±10 | 90 ±10 | 40 ±10
| B3 RES integration (GWh/yr) | <10 | 20 ±10 | <10 | 920 ±180 | 500 ±40
| B4 Losses (GWh/yr) | 750 ±50 | -175 ±25 | -175 ±25 | -50 ±25 | -50 ±25
| B4 Losses (Meuros/yr) | 32 ±2 | -10 ±2 | -8 ±1 | -3 ±2 | -4 ±2
| B5 CO2 Emissions (kT/year) | 1900 ±290 | 1300 ±900 | 400 ±100 | -300 ±100 | -100 ±300
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | ++
| B7 Robustness | ++
265 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 40 ±0 | 40 ±10 | <10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | 70 ±10 | 10 ±0
| B4 Losses (GWh/yr) | - | 0 ±25 | 0 ±25 | -100 ±25 | -100 ±25
| B4 Losses (Meuros/yr) | - | 0 ±1 | 0 ±1 | -6 ±2 | -7 ±2
| B5 CO2 Emissions (kT/year) | - | 1600 ±0 | 1100 ±200 | -300 ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | ++
| B7 Robustness | ++
266 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 50 ±< 10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 70 ±10 | 70 ±0
| B4 Losses (GWh/yr) | 525 ±52 | -75 ±25 | -75 ±25 | -575 ±57 | -550 ±55
| B4 Losses (Meuros/yr) | 22 ±3 | -4 ±1 | -4 ±2 | -35 ±4 | -37 ±4
| B5 CO2 Emissions (kT/year) | 500 ±30 | 600 ±0 | ±100 | -300 ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | ++
| B7 Robustness | ++
267 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 30 ±10 | 40 ±10 | 20 ±10 | 30 ±10
| B3 RES integration (GWh/yr) | - | 10 ±10 | <10 | 210 ±40 | 170 ±30
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | -800 ± | ±100 | 100 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
268 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 20 ±10 | 10 ±10 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | 60 ±10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 300 ±100 | 200 ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
269 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | 50 ±25 | 0 ±25 | 0 ±25 | 0 ±25 | 0 ±25
| B4 Losses (Meuros/yr) | 2 ±1 | 0 ±1 | 0 ±1 | 0 ±1 | 0 ±2
| B5 CO2 Emissions (kT/year) | ±100 | ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
270 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 40 ±10 | 20 ±10 | 30 ±10 | 40 ±10 | 80 ±10
| B3 RES integration (GWh/yr) | <10 | 50 ±40 | 150 ±20 | 110 ±70 | 370 ±50
| B4 Losses (GWh/yr) | - | 525 ±52 | 775 ±77 | 650 ±65 | 925 ±92
| B4 Losses (Meuros/yr) | - | 28 ±3 | 35 ±4 | 39 ±4 | 62 ±6
| B5 CO2 Emissions (kT/year) | ±100 | ±100 | -100 ±100 | -300 ±100 | -900 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
271 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 1990 ±110 | 2520 ±10 | 2380 ±170 | 2540 ±80
| B3 RES integration (GWh/yr) | - | 15250 ±150 | 26280 ±2280 | 28800 ±3500 | 24290 ±2010
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 9900 ±300 | -8000 ±2000 | -12700 ±2800 | -16100 ±3400
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
272 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 20 ±10 | <10 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 300 ±100 | 200 ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
273 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 20 ±10 | 10 ±10 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | 60 ±10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 300 ±100 | 200 ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
274 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | -
| B7 Robustness | -
275 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | <10 | <10 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | -
| B7 Robustness | -
276 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 80 ±20 | 40 ±10 | 50 ±10 | 50 ±20 | 100 ±10
| B3 RES integration (GWh/yr) | <10 | 100 ±80 | 270 ±110 | 180 ±80 | 450 ±70
| B4 Losses (GWh/yr) | - | 600 ±60 | 875 ±87 | 725 ±72 | 875 ±87
| B4 Losses (Meuros/yr) | - | 32 ±4 | 40 ±4 | 43 ±5 | 59 ±6
| B5 CO2 Emissions (kT/year) | 700 ±350 | 200 ±200 | ±100 | -400 ±0 | -1100 ±100
| S1 - Environmental impact | More than 100km
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
277 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 20 ±10 | <10 | <10 | 10 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 300 ±100 | 200 ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
278 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 10 ±10 | 20 ±0 | 30 ±0 | 60 ±10
| B3 RES integration (GWh/yr) | - | 30 ±30 | 100 ±20 | 60 ±30 | 270 ±50
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | -100 ±0 | -300 ±0 | -800 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
279 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 10 ±10 | <10 | 10 ±10 | 40 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | 110 ±20 | 410 ±80
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 100 ±100 | ±100 | ±100 | -200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
280 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | <10 | <10 | 20 ±10 | 20 ±10 | 20 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 780 ±160 | 180 ±60
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | ±100 | 200 ±200 | -100 ±100 | ±100 | -200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
281 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 60 ±10 | 150 ±10 | 160 ±20 | 160 ±20
| B3 RES integration (GWh/yr) | - | 40 ±40 | 990 ±290 | 1100 ±210 | 920 ±160
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 1400 ±200 | 500 ±200 | -1100 ±100 | -1600 ±200
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
282 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 10 ±10 | <10 | 10 ±10 | 60 ±20
| B3 RES integration (GWh/yr) | - | 20 ±20 | <10 | 20 ±10 | 170 ±50
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 100 ±100 | ±100 | -100 ±100 | -600 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
283 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 80 ±10 | 30 ±0 | 100 ±20 | 50 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | 600 ±120 | 100 ±20
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 600 ±100 | ±100 | -400 ±100 | -200 ± 30
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | -
| B7 Robustness | -
284 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | - | - | - | -
| B3 RES integration (GWh/yr) | - | - | - | - | -
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | - | - | - | -
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | -
285 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 70 ±10 | 120 ±20 | 110 ±20 | 110 ±10
| B3 RES integration (GWh/yr) | - | <10 | 870 ±170 | 1190 ±240 | 580 ±200
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 1300 ±400 | 500 ±100 | -700 ±100 | -800 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
286 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 20 ±10 | <10 | 30 ±10 | 30 ±10
| B3 RES integration (GWh/yr) | - | 270 ±70 | 100 ±20 | 450 ±90 | 380 ±80
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | -100 ±100 | ±100 | -500 ±300
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
287 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 250 ±20 | 160 ±20 | 210 ±30 | 230 ±20
| B3 RES integration (GWh/yr) | - | 3830 ±20 | 3130 ±630 | 2940 ±590 | 3490 ±10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | -1600 ±100 | -1700 ±100 | -900 ±100 | -600 ±400
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
289 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 40 ±10 | 10 ±10 | 50 ±10 | 50 ±10
| B3 RES integration (GWh/yr) | - | 380 ±110 | 130 ±30 | 740 ±10 | 550 ±140
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 400 ±400 | -100 ±100 | -200 ±100 | -200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
290 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 200 ±10 | 130 ±20 | 150 ±20 | 180 ±10
| B3 RES integration (GWh/yr) | - | 2960 ±30 | 2360 ±470 | 2060 ±180 | 2740 ±30
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | -1200 ±100 | -1400 ±100 | -600 ±100 | -800 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
291 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | - | - | - | -
| B3 RES integration (GWh/yr) | - | - | - | - | -
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | - | - | - | -
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | -
| B7 Robustness | -
292 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 20 ±10 | <10 | 30 ±10 | 30 ±10
| B3 RES integration (GWh/yr) | - | 270 ±70 | 100 ±20 | 450 ±90 | 380 ±80
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | -100 ±100 | ±100 | -100 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
293 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 70 ±10 | 60 ±10 | 90 ±10 | 80 ±10
| B3 RES integration (GWh/yr) | - | 1340 ±270 | 1350 ±270 | 1200 ±240 | 990 ±200
| B4 Losses (GWh/yr) | - | 42.75 | 42.75 | 42.39 | 40.6
| B4 Losses (Meuros/yr) | - | 2.4 | 2.1 | 2.6 | 2.9
| B5 CO2 Emissions (kT/year) | - | -1000 ±200 | -1100 ± | -600 ±100 | -400 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | -
294 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 60 ±10 | 80 ±10 | 60 ±10 | 50 ±10
| B3 RES integration (GWh/yr) | - | 90 ±10 | 550 ±110 | 480 ±100 | 160 ±10
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 800 ±100 | ±100 | -400 ±100 | -300 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
295 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 20 ±10 | 10 ±10 | 30 ±10 | 30 ±10
| B3 RES integration (GWh/yr) | - | 220 ±50 | 80 ±20 | 400 ±80 | 290 ±60
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | -100 ±100 | -200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | +
296 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 50 ±10 | 140 ±10 | 140 ±20 | 100 ±20
| B3 RES integration (GWh/yr) | - | <10 | 870 ±290 | 1040 ±180 | 540 ±140
| B4 Losses (GWh/yr) | - | - | - | - | -
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | 1400 ±200 | 600 ±200 | -800 ±100 | -900 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | +
| B7 Robustness | ++
297 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | 10 ±10 | 10 ±10 | <10 | 20 ±10 | 20 ±10
| B3 RES integration (GWh/yr) | <10 | <10 | 10 ±20 | 200 ±60 | 120 ±50
| B4 Losses (GWh/yr) | 0 ±25 | 0 ±25 | 0 ±25 | -25 ±25 | -25 ±25
| B4 Losses (Meuros/yr) | 0 ±1 | 0 ±1 | 0 ±1 | -2 ±2 | -2 ±2
| B5 CO2 Emissions (kT/year) | 200 ±100 | 200 ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | Negligible or less than 15km
| S2 - social impact | Negligible or less than 15km
| B6 Technical resilience | +
| B7 Robustness | +
298 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 40 ±10 | 40 ±10 | 60 ±10 | <10
| B3 RES integration (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (GWh/yr) | 0 | - | - | - | -
| B4 Losses (Meuros/yr) | 0 | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | ±100 | 200 ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | -
| B7 Robustness | -
299 | B1 SoS (MWh/yr) | - | - | - | - | -
| B2 SEW (MEuros/yr) | - | 80 ±10 | 80 ±10 | 90 ±10 | 90 ±10
| B3 RES integration (GWh/yr) | - | <10 | <10 | 190 | 160
| B4 Losses (GWh/yr) | - | 7 | 8 | 7 | 8
| B4 Losses (Meuros/yr) | - | - | - | - | -
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
| B6 Technical resilience | ++
| B7 Robustness | ++
1000 | B2 SEW (MEuros/yr) | 10 | <10 | <10 ± 0 | <10 | <10
| B3 RES integration (GWh/yr) | -10 | <10 | <10 | -30 ± 10 | 10 ± 10
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | 200 ± 100 | 100 ± 100 | ±100 | 300 ± 100 | ±100 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1001 | B2 SEW (MEuros/yr) | 50 ± 10 | 70 ± 10 | 60 ± 10 | 70 ± 10 | 70 ± 10
| B3 RES integration (GWh/yr) | <10 ± | 910 ± 180 | 910 ± 180 | 800 ± 160 | 840 ± 170
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | 70
| B4 Losses (Meuros/yr) | 70 ± 10 | 70 | 70 ± 10 | 70 ± 10 | 70 ± 10
| B5 CO2 Emissions (kT/year) | -300 ± 10 | -200 ± 10 | -700 ± 100 | -300 ± 100 | -400 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1002 | B2 SEW (MEuros/yr) | <10 | <10 | <10 | 10 ± 10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 70 ± 70 | 60 ± 40
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | -100 ± 200 | 200 ± 200 | 300 ± 100 | ±100 | ±100 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1003 | B2 SEW (MEuros/yr) | 10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | <10 | 10 ± 10
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | 300 ± 10 | 300 ± 10 | 300 ± 100 | ±100 | ±100 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1004 | B2 SEW (MEuros/yr) | 10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | 10 | <10 | <10 | 40 ± 10 | 10 ± 10
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | -200 ± 10 | 100 ± 10 | 100 | -100 ± 100 | 300 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1005 | B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 ± | 110 ± 20 | 40 ± 20 | 30 ± 30 | 70 ± 20
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | -100 | 100 | 100 | 100 | -100 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1006 | B2 SEW (MEuros/yr) | 10 | <10 | <10 | 10 ± 10 | 40 ± 10
| B3 RES integration (GWh/yr) | <10 | <10 | <10 | 230 ± 50 | 650 ± 130
| B4 Losses (GWh/yr) | <10 | <10 | <10 | 80 | <10
| B4 Losses (Meuros/yr) | <10 ± 0 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | 100 ± 10 | 100 ± 10 | 100 ± 100 | ±100 | -200 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1007 | B2 SEW (MEuros/yr) | <10 ± | 20 ± 10 | 30 ± 10 | 40 ± 10 | 30 ± 10
| B3 RES integration (GWh/yr) | <10 ± | 320 ± 60 | 410 ± 80 | 460 ± 90 | 450 ± 90
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | 20 ± 10 | 20 | 20 ± 10 | 20 ± 10 | 20 ± 10
| B5 CO2 Emissions (kT/year) | -100 ± 100 | 400 ± 100 | 600 ± 100 | -200 ± 100 | -200 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1008 | B2 SEW (MEuros/yr) | - | <10 | <10 | 30 ± 10 | 10 ± 10
| B3 RES integration (GWh/yr) | - | <10 | <10 | 250 ± 50 | 90 ± 20
| B4 Losses (GWh/yr) | - | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | - | <10 | <10 | <10 | <10 ± 0
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | ±100 | 100 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1009 | B2 SEW (MEuros/yr) | 10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | 10 | <10 | <10 | 20 ± 10 | 10 ± 10
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 0 | <10
| B5 CO2 Emissions (kT/year) | 300 ± 10 | 100 ± 10 | 200 ± 100 | -100 ± 100 | -300 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1010 | B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | <0100M€
| B3 RES integration (GWh/yr) | <10 | 60 ± 20 | 90 ± 10 | 50 ± 50 | 140 ± 50
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | -100 ± 0 | ±100 | ±100 | ±100 | 100 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1011 | B2 SEW (MEuros/yr) | 10 ± | 20 ± 10 | 10 ± 10 | 10 ± 10 | 50 ± 10
| B3 RES integration (GWh/yr) | -10 ± | <10 | 80 ± 20 | 20 ± 10 | 190 ± 40
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | 20 ± 10 | 20 | 20 ± 10 | 20 ± 10 | 20 ± 10
| B5 CO2 Emissions (kT/year) | 200 ± 100 | 800 ± 100 | -200 ± 100 | ±100 | -200 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1012 | B2 SEW (MEuros/yr) | 10 | 10 ± 10 | 10 ± 10 | <10 | 20 ± 10
| B3 RES integration (GWh/yr) | -10 | <10 | 40 ± 10 | 10 ± 10 | 80 ± 20
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | 10 ± 10 | 10 | 10 ± 10 | 10 ± 10 | 10 ± 10
| B5 CO2 Emissions (kT/year) | 100 ± 10 | 200 ± 10 | ±100 | -100 ± 100 | -200 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1013 | B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | 40 ± 10 | <10 | 40 ± 40 | 40 ± 10
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | - | ±100 | ±100 | ±100 | -200 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1014 | B2 SEW (MEuros/yr) | <10 | <10 | 40 ± 10 | 60 ± 10 | 40 ± 10
| B3 RES integration (GWh/yr) | <10 | <10 | 380 ± 80 | 470 ± 90 | 380 ± 80
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | -100 ± 100 | 400 ± 100 | 600 ± 100 | -300 ± 100 | -200 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1015 | B2 SEW (MEuros/yr) | <10 | <10 | 40 ± 10 | 40 ± 10 | 40 ± 10
| B3 RES integration (GWh/yr) | <10 | <10 | 370 ± 70 | 460 ± 90 | 370 ± 70
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | -100 ± 100 | 400 ± 100 | 500 ± 100 | -300 ± 100 | -200 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1016 | B2 SEW (MEuros/yr) | 10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | 10 | 10 ± 10 | <10 | 90 ± 20 | 60 ± 10
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 ± 0 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | 200 ± 10 | 200 ± 10 | -100 ± 100 | ±100 | -200 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1017 | B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | 20 ± 10 | <10 | 20 ± 10
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | - | 100±100 | ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1018 | B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | <10
| B3 RES integration (GWh/yr) | <10 | <10 | 20 ± 10 | <10 | 20 ± 10
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | - | 100 ± 100 | ±100 | ±100 | ±100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1019 | B2 SEW (MEuros/yr) | <10 | 20 ± 10 | 10 ± 10 | 10 ± 10 | 60 ± 10
| B3 RES integration (GWh/yr) | <10 | <10 | 60 ± 10 | 20 ± 10 | 210 ± 40
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | 20 ± 10 | 20 | 20 ± 10 | 20 ± 10 | 20 ± 10
| B5 CO2 Emissions (kT/year) | -100 ± 100 | 600 ± 100 | -100 ± 100 | ±100 | -300 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1020 | B2 SEW (MEuros/yr) | <10 | <10 | <10 | <10 | 10 ± 10
| B3 RES integration (GWh/yr) | <10 | <10 | 30 ± 10 | 10 ± 10 | 160 ± 30
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | - | ±100 | -100 ± 100 | ±100 | -100 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1021 | B2 SEW (MEuros/yr) | <10 ± | 40 ± 10 | 70 ± 10 | 120 ± 20 | 90 ± 10
| B3 RES integration (GWh/yr) | <10 ± | 590 ± 120 | 660 ± 130 | 1390 ± 280 | 1110 ± 220
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | 40 ± 10 | 40 | 40 ± 10 | 40 ± 10 | 40 ± 10
| B5 CO2 Emissions (kT/year) | ± 100 | 600 ± 100 | 1000 ± 200 | -600 ± 100 | -400 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA
1022 | B2 SEW (MEuros/yr) | <10 | <10 | 10 ± 10 | 20 ± 10 | 20 ± 10
| B3 RES integration (GWh/yr) | <10 | <10 | 190 ± 120 | 180 ± 180 | 210 ± 100
| B4 Losses (GWh/yr) | <10 | <10 | <10 | <10 | <10
| B4 Losses (Meuros/yr) | <10 | <10 | <10 | <10 | <10
| B5 CO2 Emissions (kT/year) | -100 ± 100 | 100 ± 100 | 200 ± 100 | ±100 | -200 ± 100
| S1 - Environmental impact | NA
| S2 - social impact | NA